# Appendix B – Selected Costs of Alternative Disinfection Systems

## B.1	Technologies and Costs for Control of Disinfection By-Products

Costs were developed for modifying a “base” or “typical” treatment plant to add disinfection and other technologies.  The base plant is described as a conventional treatment plant using chlorine/chlorine disinfection consisting of rapid mixing, flocculation, sedimentation, chlorination, filtration, contact basin, chemical feed systems and finished water storage.  This appendix contains figures and tables from Technologies and Costs for Control of Disinfection By-Products (USEPA, 1998), retaining the report’s original figure and table numbers. Incremental costs are shown, determined by calculating the cost for the modified treatment plant and subtracting the base treatment plant cost.

The base treatment plant shown in Figure 7-1, is a basic alum coagulation and filtration plant, with chlorine disinfection.  This plant was modified to meet disinfection requirements.  The bases for the cost estimates are shown in Tables 7-3, 7-4, 7-5, and 7-6.  The 12 flow categories for which the costs were determined are shown in Table 7-2.

Schematics and costs to add the following schemes are shown in the attached figures and tables.

- Base treatment plant - Figure 7-1 and Table 7-7.

- Move point of chlorination.  This modification assumes no cost for moving the chlorine addition point, but costs for an added contact basin are shown in Table 7-8.

- Change to Chlorine/Chloramine - Figure 7-2 and Table 7-9.

- Change to Ozone/Chloramine - Figure 7-3 and Table 7-12.

- Change to Chlorine Dioxide – Table 7-13.

- See USEPA, 1998 for more details and information upon the costs of other technologies.

FIGURE 7-1.  ALUM COAGULATION / FILTRATION BASE PLANT

TABLE 7-2.  EPA FLOW CATEGORIES

| EPA FLOW CATEGORIES | MEDIAN POPULATION SERVED | AVERAGE FLOW (mgd) | DESIGN CAPACITY (mgd) |
| --- | --- | --- | --- |
| SMALL SYSTEMS - DESIGN FLOW < 1 MGD |  |  |  |  |  |  |
| 1 | 57 | 0.0056 | 0.024 |
| 2 | 225 | 0.024 | 0.087 |
| 3 | 750 | 0.086 | 0.27 |
| 4 | 1,910 | 0.23 | 0.65 |
| LARGE SYSTEMS - DESIGN FLOW > 1 MGD |  |  |  |  |  |  |
| 5 | 5,500 | 0.70 | 1.8 |
| 6 | 15,000 | 2.1 | 4.8 |
| 7 | 35,000 | 5.0 | 11 |
| 8 | 60,000 | 8.8 | 18 |
| 9 | 88,000 | 13 | 26 |
| 10 | 175,000 | 27 | 51 |
| 11 | 730,000 | 120 | 210 |
| 12 | 1,550,000 | 270 | 430 |
| 12a | N/A | 350 | 520 |

| TABLE 7-3. SMALL SYSTEMS BASIS FOR COST ESTIMATES FOR DBP CONTROL |  |  |  |  |
| --- | --- | --- | --- | --- |
| Process | WATER Model Assumptions | Engineering Assumption |
| Package Raw Water Pumping | Premanufactured packaged pumping station using submersible pump contained in a 20 ft deep steel pump sump. Manifold piping, sump intake valve, pump check valves, and electrical controls. Total dynamic head is 50 ft. Pump and motor efficiencies are 80 and 90%, respectively. |  |
| Package Complete Treatment Plant | Coagulation, flocculation, sedimentation, and filtration equipment provided including tube settlers rated at 1,500 gpd/sf, mixed media filters with application rates of 2 to 5 gpm/sf and media depth of 30 in. Chemical feed facilities include storage tanks and feed pumps. Filter backwash pumps and, where applicable, surface wash water pumps. Flow measurement and control devices, pneumatic air supply (for 200 gpm or larger plants), effluent pumps, and building. |  |
| Hypochlorite Solution | Solution tanks, mixers, and metering pumps | Sodium hypochlorite dose of 2.4 mg/L determined by WTP model. |
| Chlorination System | Metering pumps, PVC pipes, valves and controls are included. |  |
| Sodium Hydroxide Feed System | Storage tanks, heater, manual transfer pump, mixers, feed tanks and metering pumps are included. PVC pipes, valves and control are also included. |  |
| Alum Feed System | Solution tanks, mixers, and calibrated metering pumps are included. PVC pipes, valves and controls are also included. | Alum dose is determined by DBP control alternatives. |
| Package High Service Pump Station | Includes 2 or 3 centrifugal pumps, pressure sensing, flow control valves, instrumentation and equipment. Pumps provide a maximum output of 70 psi. |  |
| Clearwell Storage Above Ground | Above ground, steel tanks including instrumentation and control of clearwell water level and instrumentation for turbidity and residual monitoring is provided. | Clearwell size is based on storage of 25% of the daily operating flow. |
| Sludge Dewatering Lagoons | Unlined lagoon and inlet, outlet structures are provided. 2 ft freeboard, 3:1 side slopes, 5 ft depth are also provided. | Sizing of lagoons is based on solids content of 5%. Sludge is thickened to a solids concentration of 30%. |
| Dewatered Sludge Hauling | Loading facilities including sludge conveyer, hopper, and hopper enclosure are provided. Length of haul is 20 miles one-way. |  |
| Contact Basin |  | Below ground tanks without repumping are assumed. Size of basin is 60 minutes, as determined by the WTP model. The well baffled tanks are assumed to provide actual contact time of 0.7 times the theoretical according to the SWTR Guidance Manual. O&M costs were unpredictable and were assumed to be negligible. |

| TABLE 7-4. LARGE SYSTEMS BASIS FOR COST ESTIMATES FOR DBP CONTROL |  |  |  |  |
| --- | --- | --- | --- | --- |
| Process | WATER Model Assumptions | Engineering Assumption |
| Raw Water Pumping | Total dynamic head 100 ft Manifold piping velocity Standby pump, manifold piping, and instrumentation are provided |  |
| Alum Feed System | Diaphragm metering pumps, steel storage hoppers with dust collector, and mechanical weight belt feeders Commercial alum density 60 lb/cu ft Dissolving tank detention time 5 min with 2 gal of water per lb of dry alum added Maximum hopper volume 6,000 cu ft with fifteen days of storage | Alum dose is determined by DBP control alternatives |
| Rapid Mix | Vertical shaft, variable speed turbine mixers with stainless steel shafts and paddles and TEFC motors Maximum basin capacity 2,500 cu ft Water temperature 15" C Overall mechanism efficiency 70% | G = 900/sec Detention time is 1 min at design flow |
| Flocculation (Horizontal Paddle) | Rectangular-shaped, reinforced concrete basins with 12 ft depth, 4:1 length to width ratio, and 12,500 cu ft individual maximum basin size Variable speed drive units requiring 15 min/day routine O&M and an oil change every 6 months requiring 4 hrs of labor Overall mechanism efficiency 60% | G = 50/sec Detention time is 30 min at design flow |
| Rectangular Clarifiers | Chain and flight collector with drive mechanism, sludge pumps, reinforced concrete structure, and withdraw pumps are included Side wall depth = 12 ft | Overflow rate = 1,000 gpd/sq ft Maximum number of units is 2 Maximum basin area = 20,000 sq ft |
| Gravity Filtration Systems | Filter structure, underdrains, wash water troughs, pipe gallery piping and valves, instrumentation, control panel, and filter housing are provided Filter box depth = 16 ft Maximum filter size = 1,275 sq ft | Minimum 4 filters per plant Filter loading rate = 4 gpm/sq ft |
| Filtration Dual Media | 20 in of 1.0 to 1.2 mm effective size anthracite coal (UC = 1.7) 10 in of 0.42 to 0.52 mm effective size silica sand (UC = 1.6) 12 in underdrains. Media consisting of 4 sizes of silica gravel |  |
| Backwash Pumping Facilities | All required pumps and motors, flow control, sequencing control, valves and backwash headers are included Pumping head = 50 ft Overall mechanism efficiency 70% | Backwash rate = 18 gpm/sq ft One filter is backwashed at a time with each filter backwashed approximately every two days |
| Wash Water Surge Basins | Below ground, reinforced concrete basins and level control instrumentation provided | Sized to store a 20 min volume of backwash water at design flow |
| Unthickened Sludge Pumping | Variable speed, centrifugal pumps, piping and valves, electrical equipment housing, dry well, and a wet well are included Pipe velocity = 5 ft/sec Total dynamic head = 30 ft Overall pump-motor efficiency = 65% | Unthickened sludge solids concentration = 1% 12 hr/day of sludge pumping |
| Sludge Dewatering Lagoons | Unlined lagoon and inlet and outlet structures are provided 2 ft freeboard, 3:1 side slopes, and 10 ft depth are also provided | Solids production is determined by WTP model Sludge is thickened to a solids concentration of 30% Sizing of lagoons is based on a solids content of 5% |
| Dewatered Sludge Hauling | Loading facilities including sludge conveyor, hopper, and hopper enclosure are provided Length of haul is 20 miles one-way | Dewatered sludge has a solids content of 30% |
| In-plant Pumping | Constant speed, vertical turbine pumps, pump motor, wet well, and piping and valves are included Pipe velocity = 5 ft/sec | Total dynamic head = 50 ft |
| Chlorine Feed Facilities | Chlorinator, standby chlorinator, cylinder scales, evaporators, residual analyzers with flow proportioning device injector pumps, and housing to include 30 days of cylinder storage are provided Injector pumps deliver water at 25 psi to allow production of 3,500 mg/L solution | Chlorine dose is 2.4 mg/L as determined by WTP model |
| Sodium Hydroxide Feed System | Storage tanks, heater, manual transfer pump mixers, feed tanks and metering pumps are included PVC pipes, valves and controls are also included | Sodium hydroxide dose is 16 mg/L as determined by WTP model |
| Finished Water Pumping | Vertical turbine pumps powered by constant speed motors, electrical equipment instrumentation, valves, and manifolds are provided Total dynamic head is 300 ft Standby pump is also included |  |

TABLE 7-5.  COST ALLOWANCE FACTORS

| Item | Small Systems Water Model (%) | Large Systems WATERCO$T Model(%) |
| --- | --- | --- |
| Site work and Interface Piping Subsurface Considerations Standby Power General Contractors Overhead and Profit | 10 10 5 12 | 15 10 5 12 |
| Engineering Legal, Fiscal and Administration fees | 15(1) 5 to 6(1) | 15(2) 9 to 11(2) |
| Notes: (1)Percentages added to estimated construction cost plus estimated cost for other allowances factors. (2)Percentages added to estimated construction cost only. |  |  |  |  |

TABLE 7-6.  INDICES USED IN THE ESCALATION OF COSTS

| DESCRIPTION | INDEX REFERENCE | NUMERICAL VALUE | ESCALATION VALUE |
| --- | --- | --- | --- |
| Building Cost Index | ENR 1 | 3391.86 | 1.23 |
| Chemical & Allied Products | BLS 2 | 147.2 | 1.19 |
| Skilled Labor | ENR 1 | 5231.35 | 1.178 |
| Materials | ENR 1 | 2268.57 | 1.328 |
| Utility Natural Gas | BLS 055 2 | 111.3 | 1.679 |

1 Engineering News Record (July, 1997)

2 Bureau of Labor Statistics (March, 1997)

TABLE 7-7.  ESTIMATED BASE PLANT COSTS

SMALL SYSTEMS

| Design Flow (mgd) | Capital Cost1 ($M) | O & M Cost2 (4/1000 gal) | Total Cost @ 3% (4/1000 gal) | Total Cost @ 7% (4/1000 gal) | Total Cost @ 10% (4/1000 gal) |
| --- | --- | --- | --- | --- | --- |
| 0.024 | 0.63 | 600 | 2672 | 3509 | 4233 |
| 0.087 | 0.86 | 188 | 848 | 1115 | 1343 |
| 0.27 | 1.4 | 90 | 390 | 496 | 605 |
| 0.65 | 2.0 | 56 | 216 | 277 | 330 |

LARGE SYSTEMS

| Design Flow (mgd) | Capital Cost1 ($M) | O & M Cost2 (4/1000 gal) | Total Cost @ 3% (4/1000 gal) | Total Cost @ 7% (4/1000 gal) | Total Cost @ 10% (4/1000 gal) |
| --- | --- | --- | --- | --- | --- |
| 1.8 | 4.3 | 74 | 187 | 233 | 272 |
| 4.8 | 7.3 | 47 | 111 | 137 | 159 |
| 11 | 12 | 39 | 83 | 102 | 118 |
| 18 | 17 | 36 | 72 | 86 | 98 |
| 26 | 22 | 35 | 66 | 78 | 89 |
| 51 | 36 | 33 | 58 | 68 | 76 |
| 210 | 120 | 32 | 50 | 58 | 65 |
| 430 | 230 | 31 | 47 | 53 | 59 |
| 520 | 380 | 26 | 46 | 54 | 61 |

1  1991 Cost escalated based upon a factor of 1.23 derived from the ENR BCI

2 1991 Cost escalated based upon a factor of 1.19 derived from the BLS Chemical and

Allied Products Index

| TABLE 7-8. ESTIMATED UPGRADE COSTS FOR ADDITIONAL CONTACT BASIN SIZE (x $1000) 1 |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| DESIGN FLOW | Chlorine Contact Basin Time |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 30 min | 60 min | 120 min | 180 min | 240 min | 300 min | 360 min |
| 0.024 | 14 | 21 | 26 | 28 | 38 | 46 | 55 |
| 0.087 | 25 | 34 | 66 | 76 | 82 | 84 | 100 |
| 0.27 | 52 | 80 | 103 | 140 | 180 | 220 | 234 |
| 0.65 | 77 | 112 | 218 | 251 | 284 | 317 | 351 |
| 1.8 | 197 | 244 | 335 | 427 | 519 | 611 | 702 |
| 4.8 | 274 | 396 | 642 | 887 | 1,132 | 1,376 | 1622 |
| 11 | 432 | 713 | 1,274 | 1,836 | 2,399 | 2,961 | 3521 |
| 18 | 611 | 1,070 | 1,990 | 2,909 | 3,828 | 4,748 | 5667 |
| 26 | 815 | 1,478 | 2,807 | 4,135 | 5,462 | 6,791 | 8118 |
| 51 | 1,454 | 2,755 | 5,360 | 7,965 | 10,569 | 13,175 | 15,778 |
| 210 | 5514 | 10,876 | 21,600 | 32,324 | 43,050 | 53,774 | 64,499 |
| 430 | 11,132 | 22,112 | 44,071 | 66,031 | 87,991 | 109,951 | 131,910 |
| 520 | 13,374 | 26,639 | 53,224 | 79,785 | 106,352 | 132,193 | 159,456 |

1  1991 Cost escalated based upon a factor of 1.23 derived from the ENR BCI

FIGURE 7-2.  ALUM COAGULATION / FILTRATION SYSTEM UPGRADED WITH CHLORINE / CHLORAMINE DISINFECTION

TABLE 7-9.  ESTIMATED UPGRADE COSTS FOR CHLORAMINES AS SECONDARY DISINFECTANT

SMALL SYSTEMS

| Design Flow (mgd) | Capital Cost1 ($M) | O & M Cost2 (4/1000 gal) | Total Cost @ 3% (4/1000 gal) | Total Cost @ 7% (4/1000 gal) | Total Cost @ 10% (4/1000 gal) |
| --- | --- | --- | --- | --- | --- |
| 0.024 | 0.011 | 21 | 57 | 71 | 83 |
| 0.087 | 0.012 | 5.5 | 15 | 19 | 22 |
| 0.27 | 0.015 | 1.9 | 5.1 | 6.3 | 7.4 |
| 0.65 | 0.016 | 0.98 | 2.3 | 2.8 | 3.2 |

LARGE SYSTEMS

| Design Flow (mgd) | Capital Cost1 ($M) | O & M Cost2 (4/1000 gal) | Total Cost @ 3% (4/1000 gal) | Total Cost @ 7% (4/1000 gal) | Total Cost @ 10% (4/1000 gal) |
| --- | --- | --- | --- | --- | --- |
| 1.8 | 0.04 | 1.4 | 2.5 | 3.0 | 3.4 |
| 4.8 | 0.07 | 0.70 | 1.3 | 1.5 | 1.8 |
| 11 | 0.11 | 0.49 | 0.9 | 1.1 | 1.2 |
| 18 | 0.16 | 0.40 | 0.73 | 0.87 | 0.99 |
| 26 | 0.21 | 0.37 | 0.67 | 0.79 | 0.89 |
| 51 | 0.28 | 0.33 | 0.52 | 0.60 | 0.67 |
| 210 | 0.47 | 0.29 | 0.36 | 0.39 | 0.41 |
| 430 | 0.85 | 0.26 | 0.32 | 0.34 | 0.36 |
| 520 | 0.91 | 0.20 | 0.25 | 0.27 | 0.28 |

1  1991 Cost escalated based upon a factor of 1.23 derived from the ENR BCI

2 1991 Cost escalated based upon a factor of 1.19 derived from the BLS Chemical and

Allied Products Index

FIGURE 7-3.  ALUM COAGULATION / FILTRATION SYSTEMS UPGRADED WITH OZONE / CHLORAMINE DISINFECTION

TABLE 7- 12.  ESTIMATED INSTALLATION AND UPGRADE COSTS FOR OZONE AS PRIMARY DISINFECTANT - SMALL SYSTEMS

| Design Flow (mgd) | Log Inactivation = 1 |  |  |  |  | Log Inactivation = 3 |  |  |  |  | Log Inactivation = 5 |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Upgrade Capital Cost ($M) | Upgrade O&M Cost (4/1000 gal) | Total Upgrade Cost @ 3% (4/1000 gal) | Upgrade Capital Cost ($M) | Upgrade O&M Cost (4/1000 gal) | Total Upgrade Cost @ 3% (4/1000 gal) | Upgrade Capital Cost ($M) | Upgrade O&M Cost (4/1000 gal) | Total Upgrade Cost @ 3% (4/1000 gal) |
| 0.024 | 0.22 | 161 | 885 | 0.23 | 322 | 1078 | 0.24 | 644 | 1433 |
| 0.086 | 0.24 | 38 | 222 | 0.28 | 75 | 290 | 0.30 | 150 | 380 |
| 0.27 | 0.29 | 10 | 72 | 0.40 | 21 | 107 | 0.47 | 42 | 143 |
| 0.65 | 0.39 | 3.9 | 35 | 0.64 | 7.8 | 59 | 0.80 | 16 | 80 |

| Design Flow (mgd) | Log Inactivation = 1 |  |  |  |  | Log Inactivation = 3 |  |  |  |  | Log Inactivation = 5 |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Upgrade Capital Cost ($M) | Upgrade O&M Cost (4/1000 gal) | Total Upgrade Cost @ 7% (4/1000 gal) | Upgrade Capital Cost ($M) | Upgrade O&M Cost (4/1000 gal) | Total Upgrade Cost @ 7% (4/1000 gal) | Upgrade Capital Cost ($M) | Upgrade O&M Cost (4/1000 gal) | Total Upgrade Cost @ 7% (4/1000 gal) |
| 0.024 | 0.22 | 161 | 1177 | 0.23 | 322 | 1384 | 0.24 | 644 | 1752 |
| 0.086 | 0.24 | 38 | 297 | 0.28 | 75 | 377 | 0.30 | 150 | 473 |
| 0.27 | 0.29 | 10 | 97 | 0.40 | 21 | 145 | 0.47 | 42 | 183 |
| 0.65 | 0.39 | 3.9 | 48 | 0.64 | 7.8 | 81 | 0.80 | 16 | 106 |

TABLE 7- 12 (cont)

ESTIMATED INSTALLATION AND UPGRADE COSTS FOR OZONE AS PRIMARY DISINFECTANT - SMALL SYSTEMS

| Design Flow (mgd) | Log Inactivation = 1 |  |  |  |  | Log Inactivation = 3 |  |  |  |  | Log Inactivation = 5 |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Upgrade Capital Cost ($M) | Upgrade O&M Cost (4/1000 gal) | Total Upgrade Cost @ 10% (4/1000 gal) | Upgrade Capital Cost ($M) | Upgrade O&M Cost (4/1000 gal) | Total Upgrade Cost @ 10% (4/1000 gal) | Upgrade Capital Cost ($M) | Upgrade O&M Cost (4/1000 gal) | Total Upgrade Cost @ 10% (4/1000 gal) |
| 0.024 | 0.22 | 161 | 1442 | 0.23 | 322 | 1661 | 0.24 | 644 | 2023 |
| 0.086 | 0.24 | 38 | 361 | 0.28 | 75 | 445 | 0.30 | 150 | 551 |
| 0.27 | 0.29 | 10 | 119 | 0.40 | 21 | 170 | 0.47 | 42 | 217 |
| 0.65 | 0.39 | 3.9 | 59 | 0.64 | 7.8 | 98 | 0.80 | 16 | 128 |

TABLE 7- 12 (cont.)

ESTIMATED INSTALLATION AND UPGRADE COSTS FOR OZONE AS PRIMARY DISINFECTANT -

LARGE SYSTEMS

| Design Flow (mgd) | Log Inactivation = 1 |  |  |  |  | Log Inactivation = 3 |  |  |  |  | Log Inactivation = 5 |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Upgrade Capital Cost ($M) | Upgrade O&M Cost (4/1000 gal) | Total Upgrade Cost @3% (4/1000 gal) | Upgrade Capital Cost ($M) | Upgrade O&M Cost (4/1000 gal) | Total Upgrade Cost @ 3% (4/1000 gal) | Upgrade Capital Cost ($M) | Upgrade O&M Cost (4/1000 gal) | Total Upgrade Cost @ 3% (4/1000 gal) |
| 1.8 | 0.89 | 1.8 | 25 | 1.5 | 4.4 | 44 | 1.4 | 6.3 | 43 |
| 4.8 | 1.5 | 1.8 | 15 | 1.9 | 4.4 | 21 | 2.0 | 6.3 | 24 |
| 11 | 1.9 | 1.8 | 9.0 | 2.6 | 4.4 | 14 | 2.8 | 6.3 | 17 |
| 18 | 2.4 | 1.8 | 7.0 | 3.0 | 4.4 | 11 | 3.7 | 6.3 | 14 |
| 26 | 2.6 | 1.8 | 5.5 | 3.9 | 4.4 | 9.9 | 4.8 | 6.3 | 13 |
| 51 | 3.8 | 1.8 | 4.4 | 6.2 | 4.4 | 8.6 | 7.4 | 6.3 | 11 |
| 210 | 9.2 | 1.8 | 3.2 | 18 | 4.4 | 7.2 | 24 | 6.3 | 10 |
| 430 | 16.5 | 1.8 | 2.9 | 35 | 4.4 | 6.8 | 47 | 6.3 | 9.5 |
| 520 | 20 | 1.8 | 2.9 | 42 | 4.4 | 6.6 | 57 | 6.3 | 9.3 |

TABLE 7- 12 (cont.)

ESTIMATED INSTALLATION AND UPGRADE COSTS FOR OZONE AS PRIMARY DISINFECTANT -

LARGE SYSTEMS

| Design Flow (mgd) | Log Inactivation = 1 |  |  |  |  | Log Inactivation = 3 |  |  |  |  | Log Inactivation = 5 |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Upgrade Capital Cost ($M) | Upgrade O&M Cost (4/1000 gal) | Total Upgrade Cost @ 7% (4/1000 gal) | Upgrade Capital Cost ($M) | Upgrade O&M Cost (4/1000 gal) | Total Upgrade Cost @ 7% (4/1000 gal) | Upgrade Capital Cost ($M) | Upgrade O&M Cost (4/1000 gal) | Total Upgrade Cost @ 7% (4/1000 gal) |
| 1.8 | 0.89 | 1.8 | 35 | 1.5 | 4.4 | 58 | 1.4 | 6.3 | 56 |
| 4.8 | 1.5 | 1.8 | 21 | 1.9 | 4.4 | 28 | 2.0 | 6.3 | 31 |
| 11 | 1.9 | 1.8 | 12 | 2.6 | 4.4 | 17 | 2.8 | 6.3 | 21 |
| 18 | 2.4 | 1.8 | 8.9 | 3.0 | 4.4 | 13 | 3.7 | 6.3 | 17 |
| 26 | 2.6 | 1.8 | 7.2 | 3.9 | 4.4 | 12 | 4.8 | 6.3 | 15 |
| 51 | 3.8 | 1.8 | 5.6 | 6.2 | 4.4 | 10 | 7.4 | 6.3 | 13 |
| 210 | 9.2 | 1.8 | 4.0 | 18 | 4.4 | 7.8 | 24 | 6.3 | 11 |
| 430 | 16.5 | 1.8 | 3.6 | 35 | 4.4 | 7.4 | 47 | 6.3 | 11 |
| 520 | 20 | 1.8 | 3.4 | 42 | 4.4 | 6.1 | 57 | 6.3 | 10 |

TABLE 7- 12 (cont.)

ESTIMATED INSTALLATION AND UPGRADE COSTS

FOR OZONE AS PRIMARY DISINFECTANT

LARGE SYSTEMS

| Design Flow (mgd) | Log Inactivation = 1 |  |  |  |  | Log Inactivation = 3 |  |  |  |  | Log Inactivation = 5 |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Upgrade Capital Cost ($M) | Upgrade O&M Cost (4/1000 gal) | Total Upgrade Cost @ 10% (4/1000 gal) | Upgrade Capital Cost ($M) | Upgrade O&M Cost (4/1000 gal) | Total Upgrade Cost @ 10% (4/1000 gal) | Upgrade Capital Cost ($M) | Upgrade O&M Cost (4/1000 gal) | Total Upgrade Cost @ 10% (4/1000 gal) |
| 1.8 | 0.89 | 1.8 | 43 | 1.5 | 4.4 | 72 | 1.4 | 6.3 | 69 |
| 4.8 | 1.5 | 1.8 | 26 | 1.9 | 4.4 | 34 | 2.0 | 6.3 | 37 |
| 11 | 1.9 | 1.8 | 14 | 2.6 | 4.4 | 21 | 2.8 | 6.3 | 24 |
| 18 | 2.4 | 1.8 | 11 | 3.0 | 4.4 | 15 | 3.7 | 6.3 | 20 |
| 26 | 2.6 | 1.8 | 8.4 | 3.9 | 4.4 | 14 | 4.8 | 6.3 | 18 |
| 51 | 3.8 | 1.8 | 6.5 | 6.2 | 4.4 | 11 | 7.4 | 6.3 | 15 |
| 210 | 9.2 | 1.8 | 4.5 | 18 | 4.4 | 8.7 | 24 | 6.3 | 12 |
| 430 | 16 | 1.8 | 4.0 | 35 | 4.4 | 8.2 | 47 | 6.3 | 12 |
| 520 | 20 | 1.8 | 3.6 | 42 | 4.4 | 8.2 | 57 | 6.3 | 10 |

TABLE 7-13 ESTIMATED INSTALLATION AND UPGRADE COSTS

FOR CHLORINE DIOXIDE AS PRIMARY DISINFECTANT

(MANUAL GENERATOR)

SMALL SYSTEMS

|  | Log Inactivation = 1 |  |  | Log Inactivation = 3 |  |  | Log Inactivation = 5 |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Design Flow (mgd) | Upgrade Capital Cost(1) ($M) | Upgrade O&M Cost (¢/1000gal) | Total Upgrade Cost @ 3% (¢/1000gal) | Upgrade Capital Cost(1) ($M) | Upgrade O&M Cost (¢/1000gal) | Total Upgrade Cost @ 3% (¢/1000gal) | Upgrade Capital Cost(1) ($M) | Upgrade O&M Cost (¢/1000gal) | Total Upgrade Cost @ 3% (¢/1000gal) |
| 0.024 | 0.10 | 1929 | 2258 | 0.10 | 1934 | 2263 | 0.13 | 1934 | 2362 |
| 0.087 | 0.10 | 452 | 529 | 0.10 | 456 | 533 | 0.15 | 456 | 571 |
| 0.27 | 0.10 | 128 | 149 | 0.10 | 132 | 153 | 0.22 | 132 | 179 |
| 0.65 | 0.10 | 49 | 57 | 0.10 | 52 | 60 | 0.28 | 52 | 74 |
|  | Log Inactivation = 1 |  |  | Log Inactivation = 3 |  |  | Log Inactivation = 5 |  |  |
| Design Flow (mgd) | Upgrade Capital Cost(1) ($M) | Upgrade O&M Cost (¢/1000gal) | Total Upgrade Cost @ 7% (¢/1000gal) | Upgrade Capital Cost(1) ($M) | Upgrade O&M Cost (¢/1000gal) | Total Upgrade Cost @ 7% (¢/1000gal) | Upgrade Capital Cost(1) ($M) | Upgrade O&M Cost (¢/1000gal) | Total Upgrade Cost @ 7% (¢/1000gal) |
| 0.024 | 0.10 | 1929 | 2391 | 0.10 | 1934 | 2396 | 0.13 | 1934 | 2534 |
| 0.087 | 0.10 | 452 | 560 | 0.10 | 456 | 564 | 0.15 | 456 | 618 |
| 0.27 | 0.10 | 128 | 158 | 0.10 | 132 | 162 | 0.22 | 132 | 198 |
| 0.65 | 0.10 | 49 | 60 | 0.10 | 52 | 63 | 0.28 | 52 | 63 |

TABLE 7-13 (cont)

ESTIMATED INSTALLATION AND UPGRADE COSTS

FOR CHLORINE DIOXIDE AS PRIMARY DISINFECTANT

(MANUAL GENERATOR)

SMALL SYSTEMS

| Design Flow (mgd) | Upgrade Capital Cost(1) ($M) | Upgrade O&M Cost (¢/1000gal) | Total Upgrade Cost @ 10 % (¢/1000gal) | Upgrade Capital Cost(1) ($M) | Upgrade O&M Cost (¢/1000gal) | Total Upgrade Cost @ 10% (¢/1000gal) | Upgrade Capital Cost(1) ($M) | Upgrade O&M Cost (¢/1000gal) | Total Upgrade Cost @ 10% (¢/1000gal) |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 0.024 | 0.10 | 1929 | 2455 | 0.10 | 1934 | 2460 | 0.13 | 1934 | 2659 |
| 0.087 | 0.10 | 452 | 575 | 0.10 | 456 | 579 | 0.15 | 456 | 654 |
| 0.27 | 0.10 | 128 | 162 | 0.10 | 132 | 166 | 0.22 | 132 | 215 |
| 0.65 | 0.10 | 49 | 62 | 0.10 | 52 | 65 | 0.28 | 52 | 91 |

TABLE 7-13 (cont.)

ESTIMATED INSTALLATION AND UPGRADE COSTS

FOR CHLORINE DIOXIDE AS PRIMARY DISINFECTANT

(AUTOMATIC GENERATOR)

SMALL SYSTEMS

|  | Log Inactivation = 1 |  |  | Log Inactivation = 3 |  |  | Log Inactivation = 5 |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Design Flow (mgd) | Upgrade Capital Cost(1) ($M) | Upgrade O&M Cost (¢/1000gal) | Total Upgrade Cost @ 3% (¢/1000gal) | Upgrade Capital Cost(1) ($M) | Upgrade O&M Cost (¢/1000gal) | Total Upgrade Cost @ 3% (¢/1000gal) | Upgrade Capital Cost(1) ($M) | Upgrade O&M Cost (¢/1000gal) | Total Upgrade Cost @ 3% (¢/1000gal) |
| 0.024 | 0.33 | 1548 | 2633 | 0.33 | 1552 | 2637 | 0.37 | 1552 | 2769 |
| 0.087 | 0.33 | 364 | 617 | 0.33 | 367 | 620 | 0.39 | 367 | 666 |
| 0.27 | 0.33 | 104 | 175 | 0.33 | 107 | 178 | 0.47 | 107 | 208 |
| 0.65 | 0.33 | 40 | 66 | 0.33 | 43 | 69 | 0.52 | 43 | 85 |
|  | Log Inactivation = 1 |  |  | Log Inactivation = 3 |  |  | Log Inactivation = 5 |  |  |
| Design Flow (mgd) | Upgrade Capital Cost(1) ($M) | Upgrade O&M Cost (¢/1000gal) | Total Upgrade Cost @ 7% (¢/1000gal) | Upgrade Capital Cost(1) ($M) | Upgrade O&M Cost (¢/1000gal) | Total Upgrade Cost @ 7% (¢/1000gal) | Upgrade Capital Cost(1) ($M) | Upgrade O&M Cost (¢/1000gal) | Total Upgrade Cost @ 7% (¢/1000gal) |
| 0.024 | 0.33 | 1548 | 3072 | 0.33 | 1552 | 3076 | 0.37 | 1552 | 3261 |
| 0.087 | 0.33 | 364 | 720 | 0.33 | 367 | 723 | 0.39 | 367 | 787 |
| 0.27 | 0.33 | 104 | 203 | 0.33 | 107 | 206 | 0.47 | 107 | 248 |
| 0.65 | 0.33 | 40 | 77 | 0.33 | 43 | 80 | 0.52 | 43 | 101 |

TABLE 7-13 (cont.)

ESTIMATED INSTALLATION AND UPGRADE COSTS

FOR CHLORINE DIOXIDE AS PRIMARY DISINFECTANT

(AUTOMATIC GENERATOR)

SMALL SYSTEMS

| Design Flow (mgd) | Upgrade Capital Cost(1) ($M) | Upgrade O&M Cost (¢/1000gal) | Total Upgrade Cost @ 10% (¢/1000gal) | Upgrade Capital Cost(1) ($M) | Upgrade O&M Cost (¢/1000gal) | Total Upgrade Cost @ 10% (¢/1000gal) | Upgrade Capital Cost(1) ($M) | Upgrade O&M Cost (¢/1000gal) | Total Upgrade Cost @ 10% (¢/1000gal) |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 0.024 | 0.33 | 1548 | 3459 | 0.33 | 1552 | 3462 | 0.37 | 1552 | 3662 |
| 0.087 | 0.33 | 364 | 810 | 0.33 | 367 | 813 | 0.39 | 367 | 888 |
| 0.27 | 0.33 | 104 | 228 | 0.33 | 107 | 231 | 0.47 | 107 | 280 |
| 0.65 | 0.33 | 40 | 87 | 0.33 | 43 | 90 | 0.52 | 43 | 115 |

(1)  Cost were adjusted to account for an increase in basin contact time from the information reported in Table 7-10

TABLE 7-13 (cont.) ESTIMATED INSTALLATION AND UPGRADE COSTS

FOR CHLORINE DIOXIDE AS PRIMARY DISINFECTANT

(MANUAL GENERATOR)

LARGE SYSTEMS

|  | Log Inactivation = 1 |  |  |  | Log Inactivation = 3 |  |  |  | Log Inactivation = 5 |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Design Flow (mgd) | Upgrade Capital Cost(1) ($M) | Upgrade O&M Cost (¢/1000gal) | Total Upgrade Cost @ 3% (¢/1000gal) | Upgrade Capital Cost(1) ($M) |  | Upgrade O&M Cost (¢/1000gal) | Total Upgrade Cost @ 3% (¢/1000gal) | Upgrade Capital Cost(1) ($M) |  | Upgrade O&M Cost (¢/1000gal) | Total Upgrade Cost @ 3% (¢/1000gal) |
| 1.8 | 0.10 | 18 | 20.6 | 0.10 |  | 20 | 22.6 | 0.50 |  | 20 | 33 |
| 4.8 | 0.10 | 7.4 | 8.3 | 0.10 |  | 9.6 | 10.5 | 0.75 |  | 9.6 | 16 |
| 11 | 0.10 | 4.3 | 4.7 | 0.10 |  | 6.5 | 6.9 | 1.3 |  | 6.5 | 11.3 |
| 18 | 0.20 | 3.8 | 4.2 | 0.20 |  | 5.8 | 6.2 | 3.7 |  | 5.8 | 13.5 |
| 26 | 0.20 | 3.2 | 3.5 | 0.20 |  | 5.1 | 5.4 | 5.1 |  | 5.1 | 12.3 |
| 51 | 0.28 | 2.4 | 2.6 | 0.28 |  | 4.6 | 4.8 | 9.4 |  | 4.6 | 11 |
| 210 | 0.29 | 1.8 | 1.8 | 0.29 |  | 3.6 | 3.6 | 36 |  | 3.6 | 9.1 |
| 430 | 0.35 | 1.6 | 1.6 | 0.35 |  | 3.2 | 3.2 | 73 |  | 3.2 | 8.2 |
| 520 | 0.35 | 1.4 | 1.4 | 0.35 |  | 2.4 | 2.4 | 89 |  | 2. | 7.1 |

TABLE 7-13 (cont.)

ESTIMATED INSTALLATION AND UPGRADE COSTS

FOR CHLORINE DIOXIDE AS PRIMARY DISINFECTANT

(MANUAL GENERATOR)

LARGE SYSTEMS

|  |  |  | Log Inactivation = 1 |  |  |  | Log Inactivation = 3 |  |  |  | Log Inactivation = 5 |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Design Flow (mgd) |  | Upgrade Capital Cost(1) ($M) |  | Upgrade O&M Cost (¢/1000gal) | Total Upgrade Cost @ 7% (¢/1000gal) | Upgrade Capital Cost(1) ($M) |  | Upgrade O&M Cost (¢/1000gal) | Total Upgrade Cost @ 7% (¢/1000gal) | Upgrade Capital Cost(1) ($M) |  | Upgrade O&M Cost (¢/1000gal) | Total Upgrade Cost @ 7% (¢/1000gal) |  |
| 1.8 |  | 0.10 |  | 18 | 22 | 0.10 |  | 20 | 24 | 0.50 |  | 20 | 38 |  |
| 4.8 |  | 0.10 |  | 7.4 | 8.2 | 0.10 |  | 9.6 | 11 | 0.75 |  | 9.6 | 19 |  |
| 11 |  | 0.10 |  | 4.3 | 4.5 | 0.10 |  | 6.5 | 6.5 | 1.3 |  | 6.5 | 13 |  |
| 18 |  | 0.20 |  | 3.8 | 4.6 | 0.20 |  | 5.8 | 6.6 | 3.7 |  | 5.8 | 17 |  |
| 26 |  | 0.20 |  | 3.2 | 3.4 | 0.20 |  | 5.1 | 5.4 | 5.1 |  | 5.1 | 15 |  |
| 51 |  | 0.28 |  | 2.4 | 2.3 | 0.28 |  | 4.6 | 4.3 | 9.4 |  | 4.6 | 13 |  |
| 210 |  | 0.29 |  | 1.8 | 2.1 | 0.29 |  | 3.6 | 4.1 | 36 |  | 3.6 | 12 |  |
| 430 |  | 0.35 |  | 1.6 | 2.0 | 0.35 |  | 3.2 | 3.0 | 73 |  | 3.2 | 10 |  |
| 520 |  | 0.35 |  | 1.4 | 1.4 | 0.35 |  | 2.4 | 2.5 | 89 |  | 2.4 | 9.0 |  |

TABLE 7-13 (cont.)

ESTIMATED INSTALLATION AND UPGRADE COSTS

FOR CHLORINE DIOXIDE AS PRIMARY DISINFECTANT

(MANUAL GENERATOR)

LARGE SYSTEMS

|  | Log Inactivation = 1 |  |  | Log Inactivation = 3 |  |  | Log Inactivation = 5 |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Design Flow (mgd) | Upgrade Capital Cost(1) ($M) | Upgrade O&M Cost (¢/1000gal) | Total Upgrade Cost @ 10% (¢/1000gal) | Upgrade Capital Cost(1) ($M) | Upgrade O&M Cost (¢/1000gal) | Total Upgrade Cost @ 10% (¢/1000gal) | Upgrade Capital Cost(1) ($M) | Upgrade O&M Cost (¢/1000gal) | Total Upgrade Cost @ 10% (¢/1000gal) |
| 1.8 | 0.10 | 18 | 22 | 0.10 | 20 | 25 | 0.50 | 20 | 43 |
| 4.8 | 0.10 | 7.4 | 8.8 | 0.10 | 10 | 11 | 0.75 | 10 | 21 |
| 11 | 0.10 | 4.3 | 4.9 | 0.10 | 6.5 | 7.1 | 1.3 | 6.5 | 15 |
| 18 | 0.20 | 3.8 | 4.5 | 0.20 | 5.8 | 6.5 | 3.7 | 5.8 | 19 |
| 26 | 0.20 | 3.2 | 3.7 | 0.20 | 5.1 | 5.6 | 5.1 | 5.1 | 18 |
| 51 | 0.28 | 2.4 | 2.8 | 0.28 | 4.3 | 4.6 | 9.4 | 4.3 | 15 |
| 210 | 0.29 | 1.8 | 1.9 | 0.29 | 3.5 | 3.6 | 36 | 3.5 | 13 |
| 430 | 0.35 | 1.6 | 1.7 | 0.35 | 3.2 | 3.2 | 73 | 3.2 | 12 |
| 520 | 0.35 | 1.4 | 1.4 | 0.35 | 2.4 | 2.5 | 89 | 2.4 | 11 |

(1)  Cost were adjusted to account for an increase in basin contact time from the information reported in Table 7-10

TABLE 7-13 (cont.)

ESTIMATED INSTALLATION AND UPGRADE COSTS

FOR CHLORINE DIOXIDE AS PRIMARY DISINFECTANT

(AUTOMATIC GENERATOR)

LARGE SYSTEMS

|  | Log Inactivation = 1 |  |  | Log Inactivation = 3 |  |  | Log Inactivation = 5 |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Design Flow (mgd) | Upgrade Capital Cost(1) ($M) | Upgrade O&M Cost (¢/1000gal) | Total Upgrade Cost @ 3% (¢/1000gal) | Upgrade Capital Cost(1) ($M) | Upgrade O&M Cost (¢/1000gal) | Total Upgrade Cost @ 3% (¢/1000gal) | Upgrade Capital Cost(1) ($M) | Upgrade O&M Cost (¢/1000gal) | Total Upgrade Cost @ 3% (¢/1000gal) |
| 1.8 | 0.33 | 15 | 24 | 0.33 | 17 | 26 | 0.74 | 17 | 37 |
| 4.8 | 0.33 | 6.3 | 9.2 | 0.33 | 8.6 | 12 | 0.99 | 8.6 | 17 |
| 11 | 0.33 | 3.9 | 5.1 | 0.33 | 6.0 | 7.2 | 1.5 | 6.0 | 12 |
| 18 | 0.68 | 3.3 | 4.7 | 0.68 | 5.3 | 6.7 | 4.2 | 5.3 | 14 |
| 26 | 0.68 | 2.9 | 3.9 | 0.68 | 4.8 | 5.8 | 5.6 | 4.8 | 13 |
| 51 | 0.76 | 2.3 | 2.8 | 0.76 | 4.1 | 4.6 | 10 | 4.1 | 11 |
| 210 | 0.77 | 1.8 | 1.9 | 0.77 | 3.5 | 3.6 | 37 | 3.5 | 9.2 |
| 430 | 0.83 | 1.6 | 1.7 | 0.83 | 3.1 | 3.2 | 74 | 3.1 | 8.2 |
| 520 | 0.91 | 1.3 | 1.4 | 0.91 | 2.5 | 2.6 | 90 | 2.5 | 7.2 |

TABLE 7-13 (cont.)

ESTIMATED INSTALLATION AND UPGRADE COSTS

FOR CHLORINE DIOXIDE AS PRIMARY DISINFECTANT

(AUTOMATIC GENERATOR)

LARGE SYSTEMS

|  | Log Inactivation = 1 |  |  | Log Inactivation = 3 |  |  | Log Inactivation = 5 |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Design Flow (mgd) | Upgrade Capital Cost(1) ($M) | Upgrade O&M Cost (¢/1000gal) | Total Upgrade Cost @ 7% (¢/1000gal) | Upgrade Capital Cost(1) ($M) | Upgrade O&M Cost (¢/1000gal) | Total Upgrade Cost @ 7% (¢/1000gal) | Upgrade Capital Cost(1) ($M) | Upgrade O&M Cost (¢/1000gal) | Total Upgrade Cost @ 7% (¢/1000gal) |
| 1.8 | 0.33 | 15 | 27 | 0.33 | 17 | 29 | 0.74 | 17 | 44 |
| 4.8 | 0.33 | 6.3 | 10 | 0.33 | 8.6 | 13 | 0.99 | 8.6 | 21 |
| 11 | 0.33 | 3.9 | 5.7 | 0.33 | 6.0 | 7.7 | 1.5 | 6.0 | 14 |
| 18 | 0.68 | 3.3 | 5.0 | 0.68 | 5.3 | 7.0 | 4.2 | 5.3 | 17 |
| 26 | 0.68 | 2.9 | 4.4 | 0.68 | 4.8 | 6.4 | 5.6 | 4.8 | 16 |
| 51 | 0.76 | 2.3 | 2.7 | 0.76 | 4.1 | 4.7 | 10 | 4.1 | 13 |
| 210 | 0.77 | 1.8 | 2.2 | 0.77 | 3.5 | 4.2 | 37 | 3.5 | 12 |
| 430 | 0.83 | 1.6 | 2.1 | 0.83 | 3.1 | 3.1 | 74 | 3.1 | 10 |
| 520 | 0.91 | 1.3 | 1.4 | 0.91 | 2.5 | 2.6 | 90 | 2.5 | 9.1 |

(1)  Cost were adjusted to account for an increase in basin contact time from the information reported in Table 7-10

TABLE 7-13 (cont.)

ESTIMATED INSTALLATION AND UPGRADE COSTS

FOR CHLORINE DIOXIDE AS PRIMARY DISINFECTANT

(AUTOMATIC GENERATOR)

LARGE SYSTEMS

|  | Log Inactivation = 1 |  |  | Log Inactivation = 3 |  |  | Log Inactivation = 5 |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Design Flow (mgd) | Upgrade Capital Cost(1) ($M) | Upgrade O&M Cost (¢/1000gal) | Total Upgrade Cost @ 10% (¢/1000gal) | Upgrade Capital Cost(1) ($M) | Upgrade O&M Cost (¢/1000gal) | Total Upgrade Cost @ 10% (¢/1000gal) | Upgrade Capital Cost(1) ($M) | Upgrade O&M Cost (¢/1000gal) | Total Upgrade Cost @ 10% (¢/1000gal) |
| 1.8 | 0.33 | 15 | 30 | 0.33 | 17 | 32 | 0.74 | 17 | 51 |
| 4.8 | 0.33 | 6.3 | 11 | 0.33 | 8.6 | 14 | 0.99 | 8.6 | 24 |
| 11 | 0.33 | 3.9 | 6.1 | 0.33 | 6.0 | 8.1 | 1.5 | 6.0 | 16 |
| 18 | 0.68 | 3.3 | 5.5 | 0.68 | 5.3 | 7.5 | 4.2 | 5.3 | 21 |
| 26 | 0.68 | 2.9 | 4.7 | 0.68 | 4.8 | 6.7 | 5.6 | 4.8 | 19 |
| 51 | 0.76 | 2.3 | 2.9 | 0.76 | 4.1 | 4.9 | 10 | 4.1 | 16 |
| 210 | 0.77 | 1.8 | 2.2 | 0.77 | 3.5 | 4.2 | 37 | 3.5 | 13 |
| 430 | 0.83 | 1.6 | 2.1 | 0.83 | 3.1 | 3.1 | 74 | 3.1 | 12 |
| 520 | 0.91 | 1.3 | 1.4 | 0.91 | 2.5 | 2.7 | 90 | 2.5 | 11 |

(1)  Cost were adjusted to account for an increase in basin contact time from the information reported in Table 7-10

## B.2 	References

- USEPA.  1998a.   Technologies and Costs for Control of Disinfection By-Products. Washington, DC.

- USEPA.  1998b. Regulatory Impact Analysis for the Stage 1 Disinfectant/Disinfection Byproduct Rule.  Prepared by Science Applications International Corporation for the USEPA, Office of Ground Water and Drinking Water, Washington, DC.

- THIS PAGE INTENTIONALLY LEFT BLANK