RESIDENTIAL HEATING AND COOLING PRODUCTS

Air-source Heat Pumps and Central Air Conditioners*

The Vendor Must:

Provide central air-conditioning units and air-source heat pumps bearing the ENERGY STAR label that are rated below 65,000 Btuh, powered by single-phase current, and that meet the ENERGY STAR specifications for energy efficiency.  The vendor shall ensure that any ductwork installed with this product is sealed with permanent leak reduction technologies (duct tape alone is insufficient) and that any thermostats or controls installed with the equipment is designed for use with such equipment (e.g., heat pump thermostats shall be installed with heat pumps).  The vendor is encouraged to visit energystar.gov for an updated list of qualifying products.

| Product Type | Current Criteria |
| --- | --- |
|  | SEER | EER | HSPF (for heat pumps only) |
| Split Systems | ≥ 13 | ≥ 11 | ≥ 8.0 |
| Single Package Equipment (including gas/electric package units) | ≥ 12 | ≥ 10.5 | ≥ 7.6 |

Additional considerations for the procurement official:

Request that the vendor ensure:

- the unit is properly sized and installed to ensure maximum comfort and efficiency using industry accepted sizing protocols such as ACCA's Manual J.

- contractors are well trained in the proper installation of air-source heat pumps and central air-conditioners.

Room Air Conditioners

The Vendor Must:

Provide room air conditioners that bear the ENERGY STAR label and meet the ENERGY STAR criteria for energy efficiency. The vendor is encouraged to visit energystar.gov for an updated list of qualifying products.  The table below shows the qualifying levels:

| Capacity (Btu/Hr) | Federal Standard EER, with louvered sides | ENERGY STAR EER, with louvered sides | Federal Standard EER, without louvered sides | ENERGY STAR EER, without louvered sides |
| --- | --- | --- | --- | --- |
| < 6,000 | > 9.7 | > 10.7 | > 9.0 | > 9.9 |
| 6,000 to 7,999 |  |  |  |  |
| 8,000 to 13,999 | > 9.8 | > 10.8 | > 8.5 | > 9.4 |
| 14,000 to 19,999 | > 9.7 | > 10.7 |  |  |
| > 20,000 | > 8.5 | > 9.4 |  |  |
|  | Federal Standard EER | ENERGY STAR EER |
| Casement only | > 8.7 | > 9.6 |
| Casement-slider | > 9.5 | > 10.5 |

NOTE: The current ENERGY STAR criteria for room air conditioners is 10 percent above the NAECA criteria.  On October 1, 2003, the ENERGY STAR criteria for room air conditioners expanded to include units without louvered sides commonly referred to as "built in" or through-the-wall (TTW) units and the casement product classes. Units with reverse cycle are still excluded.

Boilers**

The Vendor Must:

Provide residential gas or oil fired boilers of less than 300,000 Btu per hour energy input, that bear the ENERGY STAR label and meet the ENERGY STAR specifications for energy efficiency.  The vendor is encouraged to visit energystar.gov for an updated list of qualifying products.

| Product Type | Current Criteria |
| --- | --- |
| Boiler | ≥ 85% AFUE EER |
| Combination Space Heating and Water Heating Appliance | ≥ 85% CAafue EER |

AFUE: Annual Fuel Utilization Efficiency

CAafue: Combined Appliance Annual Fuel Utilization Efficiency

Additional considerations for the procurement official:

Request that the vendor ensure:

- the unit is properly sized and installed to ensure maximum comfort and efficiency using industry accepted sizing protocols such as ACCA's Manual J.

- contractors are well trained in the proper installation of boilers.

Furnaces**

The Vendor Must:

Provide gas or oil fired furnaces that bear the ENERGY STAR label and meet the ENERGY STAR specifications for energy efficiency.  The vendor shall ensure that any ductwork installed with this product is sealed with permanent leak reduction technologies (duct tape alone is insufficient) and that any thermostats or controls installed with the equipment is designed for use with such equipment.  The vendor is encouraged to visit energystar.gov for an updated list of qualifying products.

| Product Type | Current Criteria |
| --- | --- |
| Furnace | ≥ 90% AFUE EER |

AFUE: Annual Fuel Utilization Efficiency

Additional considerations for the procurement official:

Request that the vendor ensure:

- the unit is properly sized and installed to ensure maximum comfort and efficiency using industry accepted sizing protocols such as ACCA's Manual J.

- contractors are well trained in the proper installation of furnaces.

Geothermal Heat Pumps

The Vendor Must:

Provide single or multi-speed geothermal heat pumps that bear the ENERGY STAR label and meet the ENERGY STAR specifications for energy efficiency.  The vendor is encouraged to visit energystar.gov for an updated list of qualifying products.

| Product Type | Current Criteria |
| --- | --- |
|  | EER | COP | Water Heating |
| Closed Loop System With integrated WH | 14.1 14.1 | 3.3 3.3 | YES N/A |
| Open Loop System With integrated WH | 16.2 16.2 | 3.6 3.6 | YES N/A |
| DX System With integrated WH | 15 15 | 3.5 3.5 | YES N/A |

NOTE: These specifications apply to single-speed models.  Multi-speed models may be qualified based on EER = (high speed EER+low speed EER)/2; and COP = (high speed COP+low speed COP)/2.

Additional considerations for the procurement official:

Request that the vendor ensure:

- the heat pump is properly sized for the conditioned space to ensure optimal operational cycles and comfort using industry accepted sizing protocols such as ACCA's Manual J.

- contractors are properly trained on the following issues:

- equipment installation and hookup,

- domestic water heater connection for desuperheater or integrated water heating, and

- code compliance.

Thermostats*

The Vendor Must:

Provide programmable thermostats that bear the ENERGY STAR label and meet the ENERGY STAR specifications for energy efficiency. The vendor is encouraged to visit energystar.gov for an updated list of qualifying products.

Table 1: Programmable Thermostat Setpoint Temperatures

| Setting | Setpoint Temperature (Heat) | Setpoint Temperature (Cool) |
| --- | --- | --- |
| Wake | ≤ 70°F | ≥ 78°F |
| Day | setback at least 8°F | setup at least 7°F |
| Evening | ≤ 70°F | ≥ 78°F |
| Sleep | setback at least 8°F | setup at least 4°F |

Table 2: Acceptable Setpoint Times and Temperature Settings

| Setting | Time | Setpoint Temperature(Heat) | Setpoint Temperature (Cool) |
| --- | --- | --- | --- |
| Wake | 6 a.m. | 70°F | 78°F |
| Day | 8 a.m. | 62°F | 85°F |
| Evening | 6 p.m. | 70°F | 78°F |
| Sleep | 10 p.m. | 62°F | 82°F |

Ventilating Fans**

The Vendor Must:

Provide ventilating fans that bear the ENERGY STAR label and meet the ENERGY STAR specifications for energy efficiency. The vendor is encouraged to visit energystar.gov for an updated list of qualifying products.

| Performance Characteristic | Current Criteria |
| --- | --- |
| Duty and Airflow (cfm) | Maximum Allowable Sound Level (sones) | Minimum Efficacy Level (cfm/W) |
| Range Hoods (up to 500 cfm) | 4.0 | 2.8 |
| Bathroom and Utility Room Fans (1 to 75 cfm) | 2.0 | 1.4 |
| Bathroom and Utility Room Fans (76 cfm and over) | 1.5 | 2.8 |
| Light Source | Must be an ENERGY STAR qualified light fixture. Night lights must consume no more than 4 watts. |