## Form4a-1
Form 4a |  |  |  | Project Name: |  | Page:
SYSTEMS - GENERAL
1. Applicablity (Section 1317)
Is this form required?
Form Required. Complete form if a new HVAC system is being installed, or components of an existing HVAC system are being replaced (I.e., equipment, controls, ductwork, and insulation.)
Exception. The building or part of the building qualifies for an exception from HVAC code requirements. Applicable code exception is Section 1317.1. Portions of the building that qualify:
|  | Area: |  |  | Exception
|  | Area: |  |  | Exception
|  | Area: |  |  | Exception
Form Not Required. This project does not contain work required to comply with code.
2. Simple or Complex Systems (Section 1317.9 or 1317.10)
Simple System. Building contains only Simple HVAC System(s). Complete this form (4a) and equipment efficiency worksheets as required. Form 4b is not required.
Complex System. Project includes a Complex System. Complete this form (4a), form 4b and equipment efficiency worksheets as required.
3. Equipment Performance (Section 1317.5)
No New HVAC Equipment. The building plans do not call for new electrical HVAC equipment, combustion heating equipment, or heat-operated cooling equipment.
Complies. All new HVAC equipment have efficiencies not less than those required by code.
The following equipment efficiency worksheets are attached:
4. Duct Insulation and Sealing (Sections 1317.7 & 1317.8)
No Ducts. The building plans and specifications do not call for new HVAC ducts or plenums.
Complies. The plans and specifications call for all air-handling ducts and plenums to be insulated and sealed as required by Sections 1317.7 &1317.8.
5. Distribution Transformers (Section 1316.1)
No Distribution Transformers. The plans/specs do not call for new distribution transformers.
Complies. All new distribution transformers comply with efficiency, testing, and labeling requirements of Section 1316.1.1.
Exception. The project qualifies for an exception per Section 1316.1.1, Exceptiion:
Attach relevant documentation for appropriate exception. The plans/specs show compliance in the following locations:
4-1
Not Required Until 10/1/04
Applicability Discussion of qualifying exceptions on page 4-25
Exceptions Discussion of qualifying exceptions on page 3-11
Exceptions Discussion of qualifying exceptions on page 3-11
Exceptions Discussion of qualifying exceptions on page 4-18
Exceptions Discussion of qualifying exceptions on page 3-11
Exceptions Discussion of qualifying exceptions on page 4-14
Exceptions Discussion of qualifying exceptions on page 4-16
Exceptions Discussion of qualifying exceptions on page 4-18
Exceptions Discussion of qualifying exceptions on page 3-11
Exceptions Discussion of qualifying exceptions on page 4-14
Exceptions Discussion of qualifying exceptions on page 3-11
Exceptions Discussion of qualifying exceptions on page 3-11
Exceptions Discussion of qualifying exceptions on page 3-11
Controls
Exceptions Discussion of qualifying exceptions on page 4-18
Exceptions Discussion of qualifying exceptions on page 3-11
Exceptions Discussion of qualifying exceptions on page 3-11
Exceptions Discussion of qualifying exceptions on page 3-11
Exceptions Discussion of qualifying exceptions on page 4-18
Exceptions Discussion of qualifying exceptions on page 3-11
Plans/Specs Show compliance by including a drawing sheet, detail number, specification section and subparagraph.

## Form4a-2
Form 4a |  |  |  | Project Name: |  | Page:
SYSTEMS - GENERAL
6. HVAC Controls (Section 1317.4)
6.1 System Thermostat/Zone Controls (Section 1317.4.1)
Complies. All new HVAC systems include at least one temperature control device responding to temperatures within the zones.
Exception. HVAC system qualifies for an exception from zone control requirements.
|  | The applicable code exception is Section 1317.4.2, |  |  | Exception
Portions of the building that qualify:
The plans/specs show compliance in the following locations:
6.2 Off-hour Controls - Auto Setback or Shutdown (Section 1317.4.3)
Complies. Systems must have at least one of the following features:
Control Setback Complies. Each system is equipped with automatic control capable of reducing energy through control setback during periods of non-use or alternate use of spaces served.
Equipment Shutdown Complies. Each system is equipped with controls capable of reducing energy use through automatic shutdown during periods of non-use or alternate use of spaces.
HVAC systems with equipment shutdown are equipped with at least one of the following:
Programmable controls (1317.4.3.1 (1))
Occupant sensor (1317.4.3.1 (2))
Interlocked to a security system (1317.4.3.1 (3))
Manually activated timers with 2-hour operation max (1317.4.3.1 (4))
Exception. The building qualifies for an exception to the requirement for automatic setback or shutdown controls. The applicable code exception is Section 1317.4.3
Exception
The plans/specs show compliance in the following locations:
6.3 Control Capabilities (Sec. 1317.4.2.1)
Complies. Zone thermostats are capable of being set to the temperatures described in Sec. 1317.4.2.1. Where used to control both heating and cooling, zone controls shall be capable of providing a temperature range or deadband of at least 5 degrees F within which the supply of heating and cooling energy to the zone is shut off or reduced to a minimum.
Exception. The building qualifies for an exception to the deadband requirements.
|  | The applicable code exception is Section 1317.4.2.1 |  |  | Exception
Portions of the building that qualify:
The plans/specs show compliance in the following locations:
6.4 Optimum Start Controls (Section 1317.4.3.2)
Complies. Separate HVAC systems have controls capable of varying start-up time of system to just meet temperature set point at time of occupancy.
Exception. HVAC systems have a design supply air capacity not exceeding 10,000 cfm.
The plans/specs show compliance in the following locations:
6.5 Heat Pump Controls (Section 1317.4.4)
No Heat Pump. The plans/specs do not call for a new heat pump
Complies. All new heat pumps equipped with supplementary heaters are controlled to minimize the use of supplemental heat as defined in Section 1317.4.4.
The plans/specs show compliance in the following locations:
4-2
Exceptions Discussion of qualifying exceptions on page 4-18
Exceptions Discussion of qualifying exceptions on page 3-11
Exceptions Discussion of qualifying exceptions on page 4-18
Exceptions Discussion of qualifying exceptions on page 4-18
Exceptions Discussion of qualifying exceptions on page 4-18
Exceptions Discussion of qualifying exceptions on page 3-11

## Form4a-3
Form 4a |  |  |  | Project Name: |  | Page:
SYSTEMS - GENERAL
7. Economizer Cooling (Section 1317.3)
No Cooling. The building plans do not call for a new fan system with mechanical cooling.
Complies. Each new fan system has an air economizer capable of modulating outside-air and return-air dampers to provide up to 100 percent of the design supply air as outside air.
Exception At least one new fan system qualifies for an exception. The applicable code exception is Section 1317.3, Exception
If Exception 3 is selected complete the following:
(a) Total cooling capacity of exempt units (Btu/hr)
(b) Total installed building cooling capacity (Btu/hr)
Complies. Sum of exempt units rated at less than 54,000 Btu/hr is <240,000 Btu/hr or a/b < 0.10 (10% of total building cooling capacity).
Unit Identifier of exempt units:
The plans/specs show compliance in the following locations:
8. Economizer Pressure Relief & Integration (Section 1317.3.1 and 1317.3.2)
No Economizers Required. Project does not contain a new fan system requiring economizers.
Overpressurization Complies. The drawings specifically identify a pressure relief mechanism for each fan system that will relieve the extra air introduced by the economizer.
Integration Complies. Economizer is capable of providing partial cooling even when additional mechanical cooling is required to meet the remainder of the cooling load.
Exception. The applicable exception is Section 1317.3.2, Exception
The plans/specs show compliance in the following locations:
9. Hot Gas Bypass (Section 1317.5)
No Hot Gas Bypass
Complies. See allowable amount of hot gas bypass as a percentage of total cooling capacity in table below.
|  | Unit ID | Rated Cooling Capacity |  | Hot Gas Bypass Capacity
Allowable Hot Gas Bypass
|  |  | Rated Cooling Capacity |  | Max Hot Gas Bypass Capacity
|  |  | <240,000 Btu/hr |  | 50%
|  |  | >240,000 Btu/hr |  | 25%
Exception. Unitary packaged system with cooling capacity no greater than 90,000 Btu/h
4-3
Exceptions Discussion of qualifying exceptions on page 4-18
Exceptions Discussion of qualifying exceptions on page 3-11
Exceptions Discussion of qualifying exceptions on page 4-18
Exceptions Discussion of qualifying exceptions on page 4-18
Exceptions Discussion of qualifying exceptions on page 4-18
Exceptions Discussion of qualifying exceptions on page 3-11

## Form4a-4
Form 4a |  |  | Project Name: | Page:
SYSTEMS - GENERAL
10. Shutoff Dampers (1317.4.3.3)
Not Required. Shutoff dampers are not required on this project.
Complies. Each outdoor air supply & exhaust system shall be equipped with motorized dampers.
Exception. The building qualifies for an exception to the motorized damper requirement. The applicable code exception is Section 1317.4.3.3 Exception
The plans/specs show compliance in the following locations:
10.1. Shutoff Damper Controls (Section 1317.4.3.3.1)
Complies. Outdoor air supply and exhaust systems shall be provided dampers that automatically shut when systems or spaces served are not in use or during building warm-up, cooldown, or setback.
Complies. Stair and shaft vents are capable of being automatically closed during normal building operation and interlocked to open as required by fire and smoke detection systems.
The plans/specs show compliance in the following locations:
10.2. Motorized Damper Leakage (1317.4.3.3.2)
Complies. Motorized outdoor air supply and exhaust air dampers have a maximum leakage rate of 4 cfm/ft2 at 1.0 in w.g. when tested in accordance with AMCA Standard 500-1998.
Exception. Packaged HVAC equipment may have maximum leakage rate of 20 cfm/ft2 at 1.0 in w.g. when tested in accordance with AMCA Standard 500–1998.
The plans/specs show compliance in the following locations:
11. Piping Insulation (Section 1314)
No New Piping. The building plans and specifications do not call for new piping serving a heating or cooling system or part of a circulating service water heating system.
Complies. All new piping serving a heating or cooling system or part of a circulating service water heating system complies with the requirements of the Code, Section 1314.1.
Exception. New piping qualifies for exception: Section 1314.1, Exception
12. Occupancy Ventilation
Complies. Mechanical ventilation systems provide the required amount of ventilation is indicated in plans/specifications as specified in Chapter 4 of the Oregon Mechanical Specialty Code.
Complies. Natural ventilation systems provide required amount of ventilation as certified by a reg-istered architect or engineer as specified by Section1203.4.1, Exception. Attach worksheet 4m.
The plans/specs show compliance in the following locations:
The plans/specs show compliance on the following pages:
4-4
Exceptions Discussion of qualifying exceptions on page 4-18
Exceptions Discussion of qualifying exceptions on page 3-11
Exceptions Discussion of qualifying exceptions on page 4-18
Exceptions Discussion of qualifying exceptions on page 4-18
Exceptions Discussion of qualifying exceptions on page 4-18
Exceptions Discussion of qualifying exceptions on page 3-11

## Form4a-5
Form 4a |  |  | Project Name: | Page:
SYSTEMS - GENERAL
13. High Occupancy Ventilation (Section 1317.2.2)
Complies. HVAC systems with ventilation air capacities of 1,500 CFM or greater that serve areas having an average occupant load of 20 square feet per person or less from Table 1004.1.2 have a means to automatically reduce outside air intake.
Identify applicable systems:
Plans/specs indicate where equipment (i.e. carbon dioxide sensor) and sequence is specified:
Exception. HVAC systems are equipped with an energy recovery device with at least 50% recovery effectiveness.
No High Occupancy Systems. Project does not contain an HVAC system as described above.
14. Exhaust Air Heat Recovery (Section 1318.3)
Not Regulated. HVAC system does not have: 1) design supply air cap. of >10,000 cfm, and 2) min. outside air supply >70%, and 3) at least 1 exhaust fan rated at 75% of min outside air supply.
Complies. Heat recovery system increases outside air temperature by 20°F (Climte Zone 1) or 30°F (Zone 2) and has provision to provide bypass during air economizer mode.
Exception. An HVAC system qualifies for an exception to this requirement. Applicable exception from Section 1318.3 Exception
The plans/specs show compliance in the following locations:
15. Large Volume Fan Systems (Section 1318.4.2.4)
Not Regulated. The building plans or specifications do not call for fan systems over 15,000 CFM that serve a single zone and function for the purpose of temperature control.
Complies. Fan systems are equipped with variable frequency drive or two speed motor to reduce airflow as required by Section 1318.4.2.3.
The plans/specs show compliance in the following locations:
16. Variable Speed Drives (Section 1317.10.3.1)
Not Regulated. The building plans or specifications do not call for fan and pump motors 10 horsepower and greater that serve variable-flow air or liquid systems.
Complies. All fan and pump motors 10 hp and greater which serve variable-flow air or liquid systems are controlled by a variable-speed drive.
Exception. The building qualifies for an exception to the variable-speed drive requirement.
Portions of the building that qualify:
Applicable code exception is Section 1317.10.3.1, Exception
The plans/specs show compliance in the following locations:
17. Service Water Heating (Sec. 1315)
No New Water Heating. The building plans and specifications do not call for new water heaters, hot water storage tanks or service hot water distribution systems.
Complies. All new water heaters, hot water storage tanks or service hot water distribution systems comply with the requirements of the Section 1315.
|  | Exception. The applicable code exception is Section: |  | Exception:
Portions of the building that qualify:
The plans/specs show compliance in the following locations:
4-5
Exceptions Discussion of qualifying exceptions on page 4-18
Exceptions Discussion of qualifying exceptions on page 3-11
Exceptions Discussion of qualifying exceptions on page 4-18
Exceptions Discussion of qualifying exceptions on page 4-18
Exceptions Discussion of qualifying exceptions on page 4-18
Exceptions Discussion of qualifying exceptions on page 3-11

## Form4a-6
Form 4a |  |  |  | Project Name: | Page:
SYSTEMS - GENERAL
18. Swimming Pools, Spas and Hot Tubs (Section 1315.5)
No New Pools. The building plans and specifications do not call for new, swimming pools, spas or hot tubs.
On/Off Controls Complies. Spa and hot tub heaters are equipped with a readily accessible ON/OFF switch as required by Section 1315.5.1.
Ventilation Controls Complies. Pool ventilation system is controlled based on humidity.
Cover Complies. All heated pools, hot tubs and spas are equipped with a cover.
Heat Recovery Complies. Pools, Spas, and hot tubs, over 200 ft2 utilize recovered heat as required by Section 1315.5.3.
Exception. Heat recovery is not necessary as pool is heated by renewable energy or waste heat recovery sources capable of providing at least 70 percent of the heating energy required over an operating season.
19. Fume Hoods (Section 1317.2.1.)
No Fume Hoods. The building plans do not call for fume hood systems that have a total exhaust rate greater than 15,000 cfm.
Complies. Fume hood systems have at least one of the following features:
Variable air volume hood exhaust and room supply systems capable of reducing exhaust and makeup air volume to 50% or less of design values.
Direct makeup (auxiliary) air supply equal to at least 75% of the exhaust rate, heated no warmer than 2° F below room set point, cooled no cooler than 3° F above room set point, no humidification added, and no simultaneous heating and cooling used for dehumidification control.
Heat recovery systems to precondition makeup air from fume hood exhaust in accordance with 1318.3 - Exhaust Air Energy Recovery, without using any exception.
The plans/specs show compliance in the following locations:
20. Parking Garage Ventilation (Section 1317.2.3)
No Enclosed Garages. The building plans and specifications do not call for enclosed Group S-2 parking garages with a ventilation exhaust rate greater than 30,000 CFM.
Complies. The plans and specifications call for carbon monoxide sensing devices as required by Section 1317.2.3.
Exception. Open parking garages.
21. Kitchen Hoods (Section 1317.11)
Not Regulated. The plans/specs do not call for any new kitchen hoods with exhaust capacity greater than 5,000 cfm each.
Complies. All new kitchen hoods with a total exhaust capacity greater than 5,000 cfm have at least 50 percent of the required makeup air; (a) unheated or heated to no more than 60°F; and (b) uncooled or evaporatively cooled.
The plans/specs show compliance in the following locations:
22. Outside Heating Systems (Section 1317.12)
No Outside Heating Systems. The plans/specs do not call for new permanently installed heating systems outside the building.
Complies. All new permanently installed outside heating systems are radiant gas fired systems controlled by an occupancy sensor or timer switch as required by Section 1317.12.
4-6
Exceptions Discussion of qualifying exceptions on page 4-18
Exceptions Discussion of qualifying exceptions on page 3-11
Exceptions Discussion of qualifying exceptions on page 4-18
Exceptions Discussion of qualifying exceptions on page 4-18
Exceptions Discussion of qualifying exceptions on page 4-18
Exceptions Discussion of qualifying exceptions on page 3-11

## Form4b-1
Form 4b |  |  | Project Name: | Page:
COMPLEX HVAC SYSTEMS
1. Simple or Complex Systems (Section 1317.9, 1317.10 and 1318)
Note: This form is required for complex systems only. If your plans qualify as a simple system as defined by the code, this form is not required.
2. Air Transport Energy (Section 1318.4.2)
Not Regulated. Each HVAC system does not have total fan nameplate horsepower of 7.5 HP or greater (include sum of all supply, return, & exhaust fans operating at design conditions).
Brake Horsepower Complies. The energy demand of all HVAC fan systems meets code requirements. Complete and attach Worksheet 4l.
Nameplate Horsepower Complies. Selected fan motors have nameplate ratings no larger than is allowed by Section 1218.4.2.3. (Complete Worksheet 4L.)
Exception. Section 1318.4.2, Exception
Portions of the building that qualify:
The plans/specs show compliance in the following locations:
3. Cooling Tower Fans (Section 1317.5.4.1)
No Cooling Tower There is no cooling tower in this project.
Complies. Cooling tower fans have control devices that vary flow by controlling leaving fluid temperature or condenser temperature/pressure of the heat rejection device.
The plans/specs show compliance in the following locations:
4. Simultaneous Heating and Cooling (Section 1318.2.1)
No Cooling. The building HVAC system has no cooling.
Complies. Controls prevent reheating, recooling or mixing of mechanically heated and mechanically cooled air.
Exception. Code exception is Section 1318.2.1, Exception
If exception 1 is used, complete and attach Worksheet 4k
Portions of the building that qualify:
The plans/specs show compliance in the following locations:
5. Electric Motor Efficiency (Section 1317.10.3 & Table 13-T)
Not Regulated. There are no NEMA Design A&B squirrel cage,T-frame induction, permanently wired polyphase motors of one horsepower or more which serve built up HVAC systems.
Complies. The efficiency of all regulated motors meets code requirements.
Exception. Section 1317.10.3, Exception
Portions of the building that qualify:
The plans/specs show compliance in the following locations:
6. VAV System Static Pressure Reset Controls (Section 1318.2.3)
Not Regulated. The building plans or specifications do not call for a VAV system controlled by a static pressure sensor or direct digital control of individual zone boxes.
Complies. The system static pressure set point automatically resets to the lowest point possible while still providing the required air flow to the zones with the greatest demand.
Exception. Section 1318.2.3, Exception
The plans/specs show compliance in the following locations:
4-7
Applic-ability Discussion of qualifying excep-tions in instructions section.
Exceptions Discussion of qualifying exceptions on page 3-11
Fan Motor Energy See Section 1318.4.2 for maximum horse-power allowed.
Exceptions Discussion of qualifying exceptions on page 3-11
Exceptions Discussion of qualifying exceptions on page 3-11
Exceptions Discussion of qualifying exceptions in instructions section.
Exceptions Discussion of qualifying exceptions on page 4-22
Cooling Tower Fans

## Form 4b-2
Form 4b |  |  | Project Name: | Page:
COMPLEX HVAC SYSTEMS
7. VAV Terminal Units (Section 1317.4.2.1)
Not Regulated. Project does not contain VAV terminal units.
Complies. VAV terminal units are programmed to operate at the minimum airflow setting without addition of reheat when the zone temperature is within the set deadband. Complete Worksheet 4k.
Exception. Section 1317.4.2.1, Exception
The plans/specs show compliance in the following locations:
8. Supply-Air Temperature Reset Controls (Section 1318.2.5)
Not Regulated. The building plans or specifications do not call for multiple zone HVAC systems.
Complies. Multiple zone HVAC systems include controls that automatically reset the supply-air temperatures in response to building loads or outside air temperature.
Exception. The building qualifies for an exception to the supply-air reset controls requirement.
Applicable code exception is Section 1318.2.5, Exception
Portions of the building that qualify:
The plans/specs show compliance in the following locations:
9. Chilled and Hot Water Temperature Reset Controls (Section 1318.2.4)
Not Regulated. The building plans or specifications do not call for chilled or hot water systems with a design capacity exceeding 300,000 Btu/hr.
Complies. Chilled and hot water systems include controls that automatically reset supply water temperatures by representative building loads or by outside air temperature.
Exception. Section 1318.2.4, Exception
Portions of the building that qualify:
The plans/specs show compliance in the following locations:
10. Separate Air Distribution Systems (Section 1318.2.7)
Not Regulated. The building plans or specifications do not call for zones with special process temperature or humidity requirements.
Complies. Separate air distribution systems serve zones with special process temperature or humidity requirements from those zones serving only comfort conditions, or supplementary control provisions are included so primary systems are specifically controlled for comfort purposes only.
Exception. Section 1318.2.7, Exception
Identify zones with special process requirements:
The plans/specs show compliance in the following locations:
11. Zone Isolation Controls (Section 1318.2.6)
Not Regulated. Building plans or specifications do not call for HVAC systems serving multiple occupancies or floors with >240,000 Btu/hr cooling capacity, or >300,000 Btu/hr heating capacity.
Complies. HVAC systems serving multiple occupancies or floors with >240,000 Btu/hr cooling capacity, or >300,000 Btu/hr heating capacity are equipped with isolation devices capable of automatically shutting off supply air to and from each isolated area. Each isolated area is controlled independently and satisfies temperature setback (Section 1317.4.2) and optimum start control requirements. Central fan system air volume is reduced through fan speed reduction.
The plans/specs show compliance in the following locations:
4-8
Applicability Discussion of qualifying exceptions in instructions section.
Exceptions Discussion of qualifying exceptions on page 3-11
Exceptions Discussion of qualifying exceptions on page 3-11
Exceptions Discussion of qualifying exceptions on page 3-11
Exceptions Discussion of qualifying exceptions in instructions section.
Exceptions Discussion of qualifying exceptions on page 4-22

## Form4b-3
Form 4b |  |  | Project Name: |  | Page:
COMPLEX HVAC SYSTEMS
12. Humidity Controls (Section 1318.2.2)
No Moisture Added to Building. The building plans do not call for means to add moisture to maintain specific humidity levels.
Complies. All new humidity control systems equipped with a humidistat when required. All humidifier preheating devices have an automatic value to shut off preheat when humidification is not required.
The plans/specs show compliance in the following locations:
13. Hydronic System Controls (Section 1318.2.8)
No Hydronic System. The building plans or specifications do not call for a new hydronic system.
Complies. The hydronic system complies as follows:
13.1 Variable Flow Controls (Section 1318.2.8.4)
System does not have a 10 hp or greater motor
Complies. System has controls capable of varying pump flow
The plans/specs show compliance in the following locations:
13.2 Three-Pipe System (Section 1318.2.8.1)
System does not have a common return system (a three-pipe system) for both hot water and chilled water.
13.3 Two-Pipe Changeover System (Section 1318.2.8.2)
System is not a Two-Pipe Changeover System
Complies. System is:
a. Designed to allow a deadband between changeover from one mode to the other
of at least 15°F outside air temperature.
b. Designed to operate and provided with controls that will allow operation in one
mode for at least four hours before changing over to the other mode.
c. Provided with reset controls that allow heating and cooling supply temperatures
at the changeover point to be no more than 30°F apart.
The plans/specs show compliance in the following locations:
13.4 Hydronic (Water Loop) Heat Pump System (Section 1318.2.8.3)
System is not a Hydronic (Water Loop) Heat Pump System
Complies. Hydronic heat pumps connected to a common heat pump water loop with central devices for heat rejection (e.g., cooling tower) and heat addition (e.g., boiler) have the following:
a. Controls installed capable of providing a heat pump water supply temperature
deadband of at least 20°F between initiation of heat rejection and heat
addition by the central devices (e.g., tower and boiler).
b. Closed-circuit tower (fluid cooler) has either an automatic valve
installed to bypass all but a minimal flow of water around the tower
(for freeze protection), or low-leakage positive closure dampers.
c. Open-circuit tower installed directly in the heat pump loop has an automatic
valve installed to bypass all heat pump water flow around the tower. Open-
circuit towers used in conjunction with a separate heat exchanger to isolate
the tower from the heat pump loop are controlled by shutting down the
circulation pump on the cooling tower loop.
d. A two-position valve at each hydronic heat pump for hydronic systems
having a total pump system power exceeding 10 hp.
The plans/specs show compliance in the following locations:
4-9
Applicability Discussion of qualifying exceptions in instructions section.
Exceptions Discussion of qualifying exceptions on page 3-11
Exceptions Discussion of qualifying exceptions on page 3-11
Exceptions Discussion of qualifying exceptions on page 3-11
Exceptions Discussion of qualifying exceptions in instructions section.
Exceptions Discussion of qualifying exceptions on page 4-22

## Wksht 4a
Worksheet 4a |  |  | Project Name: |  |  |  | Page:
UNITARY AIR CONDITIONER - AIR COOLED
|  | (a) | (b) | ( c ) | (d) Proposed Performance |  | (e) | (f)
|  | Equip. ID | Model Designation | Cooling Capacity (Btu/h) | Steady State | Seasonal or Part Load | Compliance Schedule (A-E) | New or Replacemnt? *
Indicate source of information
ARI Unitary Directory, Section AC, page:
ARI Applied Products directory, Section ULE, page:
Product data (Attach data furnished by the equipment supplier, I.e., "cut sheets")
|  | Compliance Schedule | Equipment Type |  | Cooling Capacity (btu/hr) |  | Minimum Rating
[5 empty] | Over | But not over - | Steady State | Seasonal or Part Load
|  | A | Single Package Without a Heating Section or With Electric Resistance Heat | New * | 0 | 65000 | na | 13 SEER
|  |  |  | Replacement * | 0 | 65000 | na | 9.7 SEER
|  |  |  | All | 65000 | 135000 | 10.3 EER | n/a
[5 empty] | 135000 | 240000 | 9.7 EER | n/a
[5 empty] | 240000 | 760000 | 9.5 EER | 9.7 IPLV
[5 empty] | 760000 | - | 9.2 EER | 9.4 IPLV
|  | B | Split System Without a Heating Section or With Electric Resistance Heat | New * | 0 | 65000 | na | 13 SEER
|  |  |  | Replacement * | 0 | 65000 | na | 10 SEER
|  |  |  | All | 65000 | 135000 | 10.3 EER | n/a
[5 empty] | 135000 | 240000 | 9.7 EER | n/a
[5 empty] | 240000 | 760000 | 9.5 EER | 9.5 IPLV
[5 empty] | 760000 | - | 9.2 EER | 9.2 IPLV
|  | C | Single Package With a Heating Section Other Than Electric Resistance | New * | 0 | 65000 | na | 13 SEER
|  |  |  | Replacement * | 0 | 65000 | na | 9.7 SEER
|  |  |  | All | 65000 | 135000 | 10.1 EER | n/a
[5 empty] | 135000 | 240000 | 9.5 EER | n/a
[5 empty] | 240000 | 760000 | 9.3 EER | 9.5 IPLV
[5 empty] | 760000 | - | 9.0 EER | 9.2 IPLV
|  | D | Split System With a Heating Section Other Than Electric Resistance | New * | 0 | 65000 | na | 13 SEER
|  |  |  | Replacement * | 0 | 65000 | na | 10 SEER
|  |  |  | All | 65000 | 135000 | 10.1 EER | n/a
[5 empty] | 135000 | 240000 | 9.5 EER | n/a
[5 empty] | 240000 | 760000 | 9.3 EER | 9.7 IPLV
[5 empty] | 760000 | - | 9.0 EER | 9.4 IPLV
|  | E | Condensing Unit Only | All | 135000 | - | 10.1 EER | 11.2 IPLV
* Equipment is a new installation or replaces existing equipment
4-11
Equipment Discussion of equipment ratings and equipment definitions on page 4-19.
Exceptions Discussion of qualifying exceptions on page 3-11
Required Document-ation
Code Required Efficiencies
This schedule of equip-ment efficiencies was reformatted from code, Table 13-L.

## Wksht 4b
Worksheet 4b |  | Project Name: |  |  |  | Page:
UNITARY AIR COND. - WATER & EVAPORATIVELY COOLED
| (a) | (b) |  | (d) Proposed Performance |  | (e)
| Equip. ID | Model Designation | Cooling Capacity (Btu/h) | Steady State | Seasonal or Part Load | Compliance Schedule (A-E)
Indicate source of information
ARI Unitary Directory, Section AC, page:
ARI Applied Products directory, Section ULE, Page:
Product data (Attach data furnished by the equipment supplier, I.e., "cut sheets")
| Compliance Schedule | Equipment Type | Cooling Capacity (btu/hr) |  | Minimum Rating
|  |  | Over | But not over - | Steady State | Seasonal or Part Load
| A | Single Packaged and Split AC Without a Heating Section or With Electric Resistance Heat | 0 | 65000 | 12.1 EER | n/a
|  |  | 65000 | 135000 | 11.5 EER | na
|  |  | 135000 | 240000 | 11.0 EER | n/a
|  |  | 240000 | - | 11.0 EER | 10.3 IPLV
| B | Single Packaged and Split AC With a Heating Section Other Than Electric Resistance | 0 | 65000 | 12.1 EER | n/a
|  |  | 65000 | 135000 | 11.3 EER | na
|  |  | 135000 | 240000 | 10.8 EER | n/a
|  |  | 240000 | - | 10.8 EER | 10.1 IPLV
| C | Condensing Units | 135000 | - | 13.1 EER | 13.1 IPLV
4-12
Equipment Discussion of equip-ment ratings and equipment defini- tions on page 4-19.
Exceptions Discussion of qualifying exceptions on page 3-11
Required Document-ation
Code Required Efficiencies
This equipment efficie-ncies schedule was reformatted from code, Table 13-L.

## Wksht 4c
Worksheet 4c |  | Project Name: | [6 empty] | Page:
UNITARY HEAT PUMP - AIR COOLED
| (a) | (b) | ( c ) | (d) Proposed Rating |  | (e) Proposed Heating Rating |  |  | (f) | (g)
| Equip. ID | Model Designation | Cooling Capacity (Btu/h) | SEER | EER | HSPF | COP (47ºF) | COP (17ºF) | Compliance Schedule (A-E) | New or Replacmnt*
Indicate source of information
ARI Unitary Directory, Section AC, page:
ARI Applied Products directory, Section ULE, Page:
Product data (Attach data furnished by the equipment supplier, I.e., "cut sheets")
| Compliance Schedule | Equipment Type |  | Cooling Capacity (btu/hr) |  | Minimum Cooling Rating |  | Minimum Heating Rating
|  |  |  | Over | But not over | EER | Seasonal or Part Load | HSPF | COP (@ 47ºF) | COP (@ 17ºF)
| A | Single Package Without a Heating Section or With Electric Resistance Heat | New* | 0 | 65000 | - | 13 SEER | 7.7 | - | -
|  |  | Replcmnt* | 0 | 65000 | - | 9.7 SEER | 6.6 | - | -
|  |  | All | 65000 | 135000 | 10.1 | n/a | - | 3.2 | 2.2
|  |  |  | 135000 | 240000 | 9.3 | n/a | - | 3.1 | 2
|  |  |  | 240000 | - | 9 | 9.2 IPLV | - | 3.1 | 2
| B | Split System Without a Heating Section or With Electric Resistance Heat | New* | 0 | 65000 | - | 13 SEER | 7.7 | - | -
|  |  | Replcmnt* | 0 | 65000 | - | 10 SEER | 6.8 | - | -
|  |  | All | 65000 | 135000 | 10.1 | n/a | - | 3.2 | 2.2
|  |  |  | 135000 | 240000 | 9.3 | n/a | - | 3.1 | 2
|  |  |  | 240000 | - | 9 | 9.2 IPLV | - | 3.1 | 2
| C | Single Package With a Heating Section Other Than Electric Resistance | New* | 0 | 65000 | - | 13 SEER | 7.7 | - | -
|  |  | Replcmnt* | 0 | 65000 | - | 9.7 SEER | 6.6 | - | -
|  |  | All | 65000 | 135000 | 9.9 | n/a | - | 3.2 | 2.2
|  |  |  | 135000 | 240000 | 9.1 | n/a | - | 3.1 | 2
|  |  |  | 240000 | - | 8.8 | 9.0 IPLV | - | 3.1 | 2
| D | Split System With a Heating Section Other Than Electric Resistance | New* | 0 | 65000 | - | 13 SEER | 7.7 | - | -
|  |  | Replcmnt* | 0 | 65000 | - | 10 SEER | 6.8 | - | -
|  |  | All | 65000 | 135000 | 9.9 | n/a | - | 3.2 | 2.2
|  |  |  | 135000 | 240000 | 9.1 | n/a | - | 3.1 | 2
|  |  |  | 240000 | - | 8.8 | 9.0 IPLV | - | 3.1 | 2
* Equipment is new installation or replaces existing equipment
4-13
Equipment Discussion of equip-ment ratings and equipment definitions on page 4-19.
Exceptions Discussion of qualifying exceptions on page 3-11
Required Document-ation
Code Required Efficiencies
This schedule of equipment efficien-cies was reformat-ted from the code, Table 13-M.

## Wksht 4d
Worksheet 4d | Project Name: |  |  |  |  | Page:
UNITARY HEAT PUMP - WATER COOLED
| (a) | (b) | ( c ) | (d) | (e) | (f) | (g)
| Equip. ID | Model Designation | Cooling Capacity (Btu/hr) | Entering Water Temp. EWT (ºF) | Proposed EER | Proposed COP | Compliance Schedule (A, B, or C)
Indicate source of information
ARI Unitary Directory, Section AC, page:
ARI Applied Products directory, Section ULE, Page:
Product data (Attach data furnished by the equipment supplier, I.e., "cut sheets")
| Compliance Schedule | Equipment Type | Cooling Capacity (btu/hr) |  | Minimum Cooling Rating |  | Minimum Heating Rating
|  |  | Over | But not over | EER | @EWT | COP | @ EWT
| A | Water Source | 0 | 17000 | 11.2 | 86ºF | 4.2 | 68ºF
|  |  | 17000 | 65000 | 12 | 86ºF | 4.2 | 68ºF
|  |  | 65000 | 135000 | 12 | 86ºF | 4.2 | 68ºF
| B | Ground Water Source | 0 | 135000 | 16.2 | 59ºF | 3.6 | 50ºF
| C | Ground Source | 0 | 135000 | 13.4 | 77ºF | 3.1 | 32ºF
4-14
Equipment Discussion of equipment ratings and equipment definitions on page 4-19.
Exceptions Discussion of qualifying exceptions on page 3-11
Required Document-ation
Code Required Efficiencies
This schedule of equip-ment efficiencies was reformatted from the code, Table 13-M.

## Wksht 4e
Worksheet 4e | Project Name: |  |  |  | Page:
PACKAGED TERMINAL A.C. - AIR COOLED
|  | (a) | (b) | ( c ) | (d) Proposed | (e) Code Minimum
| Type of Equipment | Equip. ID | Model Designation | Cooling Capacity (Btu/hr) | EER (95ºF db) | EER (95ºF db)
Units Installed in New Construction
Replacement of Existing Units (installed prior to 10/01/03)
Indicate source of information
ARI Unitary Directory, Section AC, page:
ARI Applied Products directory, Section ULE, Page:
Product data (Attach data furnished by the equipment supplier, I.e., "cut sheets")
4-15
Equipment Enter the cooling capacity in column ( c ). If capacity is less than 7,000 Btu/hr, use 7,000. If above 15,000, use 15,000. Discussion of equipment ratings and equipment definitions on page 4-19.
Exceptions Discussion of qualifying exceptions on page 3-11
Required Documentation
Code Required Efficiencies
Calculate the code minimum EERs from the formulas below using the cooling capacity in column ( c ).
Enter the results in column (e).
New Construction: EER @ 95F Test Conditions = 12.5–(0.213x Cap/1000) Replacement Units : EER @ 95F Test Conditions = 10.9–(0.213x Cap/1000)

## Wksht 4f
Worksheet 4f |  | Project Name: |  |  |  |  | Page:
PACKAGED TERMINAL HEAT PUMP - AIR COOLED
|  | (a) | (b) | ( c ) | (d) Proposed |  | (e) Code Minimum
[5 empty] | Cooling Rating | Heating | Cooling Rating | Heating
| Type of Equipment | Equip. ID | Model Designation | Cooling Capacity (Btu/hr) | EER (95ºF db) |  | EER (95ºF db)
Units Installed in New Construction
Replacement of Existing Units (installed prior to 10/01/03)
Indicate source of information
ARI Unitary Directory, Section AC, page:
ARI Applied Products directory, Section ULE, Page:
Product data (Attach data furnished by the equipment supplier, I.e., "cut sheets")
4-16
Equipment Enter the cooling capacity in column (c). If capacity is less than 7,000 Btu/hr, use 7,000. If above 15,000, use 15,000. Calculate the code minimum EER's from formulas below using cooling capacity in the column (c). Enter results in column (e). Discussion of equipment ratings and equipment definitions on page 4-19.
Exceptions Discussion of qualifying exceptions on page 3-11
Required Document-ation
Code Required Efficiencies
Calculate the code minimum EERs and COP's from the formulas below using the cooling capacity in column (c).
Enter the results in column (e).
New Construction EER: EER @ 95F Test Conditions = 12.3–(0.213x Cap/1000) New Construction COP: COP = 3.2 - (0.026 x Cap/1000) Replacement Units EER: EER @ 95F Test Conditions = 10.8–(0.213x Cap/1000) Replacement Units COP: COP = 2.9 - (0.026 x Cap/1000)

## Wksht 4g
Worksheet 4g |  | Project Name: |  |  |  | Page:
WATER CHILLING PKGS. - WATER & AIR COOLED
|  | (a) | (b) | ( c ) | (d) | (e) | (f)
|  | Equip. ID | Model Designation | Cooling Capacity (Btu/hr) | Proposed Steady State COP | Proposed Part Load IPLV | Compliance Schedule (A - I)
Indicate source of information
ARI Unitary Directory, Section AC, page:
ARI Applied Products directory, Section ULE, Page:
Product data (Attach data furnished by the equipment supplier, I.e., "cut sheets")
|  | Compliance Schedule | Equipment Type | Cooling Capacity (Tons) |  | Minimum Rating
[6 empty] | COP | IPLV
|  | A | Air Cooled, With Condenser, Electrically Operated | All Capacities | 150 tons | 2.8 | 2.8
|  | B | Air Cooled, Without Condenser, Electrically Operated | All Capacities | 150 tons | 3.1 | 3.1
|  | C | Water Cooled, Electrically Operated, Positive Displacement (Reciprocating) | All Capacities | 151 tons | 4.2 | 4.65
|  | D | Water Cooled, Electrically Operated, Positive Displacement (Rotary, Screw and Scroll) | < 150 tons |  | 4.45 | 4.5
|  |  |  | >150, <300 tons |  | 4.9 | 4.95
|  |  |  | >300 tons |  | 5.5 | 5.6
|  | E | Water Cooled, Electrically Operated, Centrifugal | < 150 tons |  | 5 | 5
|  |  |  | >150, <300 tons |  | 5.5 | 5.5
|  |  |  | >300 tons |  | 6.1 | 6.1
|  | F | Air Cooled Absorption, Single Effect | All Capacities | 150 tons | 0.6 | --
|  | G | Water Cooled Absorption, Single Effect | All Capacities | 151 tons | 0.7 | --
|  | H | Absorption Double Effect, Indirect Fired | All Capacities | 150 tons | 1 | 1.05
|  | I | Absorption Double Effect, Direct Fired | All Capacities | 151 tons | 1 | 1
4-17
Equipment Discussion of equipment ratings and equipment definitions on page 4-19.
Exceptions Discussion of qualifying exceptions on page 3-11
Required Document-ation
Code Required Efficiencies
This schedule of equip-ment efficiencies was reformatted from code, Table 13-O.

## Wksht 4h
Worksheet 4h |  | Project Name: | [5 empty] | Page:
HEAT REJECT. EQUIPMT. - COOLING TOWERS & AIR COOLED CONDENSERS
| Cooling Tower - Equip. ID |  |  | Design Entering Water Temperature (EWT)
| Compliance Schedule |  |  | Design Leaving Water Temperature (LWT) |  |  |  | Fan Type
|  |  |  | Design Wet Bulb Temperature (WB) | [5 empty] | Centrifugal
| Location of Equipment Schedule for EWT, LWT and WB | [8 empty] | Propeller
| (a) |  | ( b ) | (c) | (d) | (e) | (f) | (g) | (h) | Axial
| Model Designation |  | Tower Pump GPM at Design Conditions | Tower Fan HP at Design Conditions | GPM/HP ((b)/(c)) at Design Conditions | Tower Pump GPM at CTI Rated Conditions | Tower Fan HP at CTI Rated Conditions | GPM/HP ((e)/(f)) at CTI Rated Conditions | Complies 1
1 Column (g) is less than value stated in table below
| Cooling Tower - Equip. ID |  |  | Design Entering Water Temperature (EWT)
| Compliance Schedule |  |  | Design Leaving Water Temperature (LWT) |  |  |  | Fan Type
Design Wet Bulb Temperature (WB)
Location of Equipment Schedule for EWT, LWT and WB
| (a) |  | ( b ) | (c) | (d) | (e) | (f) | (g) | (h)
| Model Designation |  | Tower Pump GPM at Design Conditions | Tower Fan HP at Design Conditions | GPM/HP ((b)/(c)) at Design Conditions | Tower Pump GPM at CTI Rated Conditions | Tower Fan HP at CTI Rated Conditions | GPM/HP ((e)/(f)) at CTI Rated Conditions | Complies 1
1 Column (g) is less than value stated in table below
| Air-Cooled Condenser-Equip. ID |  |  | Condenser Temperature (CT)
| Compliance Schedule |  |  | Air Temp. Entering Condenser (ATEC)
Location of CT & ATEC Schedule
| (a) |  | (b) | (c) | (d) | (e) | (f) | (g) | (h)
| Model Designation |  | Heat Rejected (Btu/h) at Design Conditions | Condenser Fan HP at Design Conditions | Btu/h-HP ((b)/(c)) at Design Conditions | Heat Rejected (Btu/h) at ARI Rated Conditions | Condenser Fan HP at ARI Rated Conditions | Btu/h-HP ((e)/(f)) at ARI Rated Conditions | Complies 1
1 Column (g) is greater than value stated in table below
| Air-Cooled Condenser-Equip. ID |  |  | Condenser Temperature (CT)
| Compliance Schedule |  |  | Air Temp. Entering Condenser (ATEC)
Location of CT & ATEC Schedule
| (a) |  | (b) | (c) | (d) | (e) | (f) | (g) | (h)
| Model Designation |  | Heat Rejected (Btu/h) at Design Conditions | Condenser Fan HP at Design Conditions | Btu/h-HP ((b)/(c)) at Design Conditions | Heat Rejected (Btu/h) at ARI Rated Conditions | Condenser Fan HP at ARI Rated Conditions | Btu/h-HP ((e)/(f)) at ARI Rated Conditions | Complies 1
1 Column (g) is greater than value stated in table below
| Indicate source of information |  | ARI Directory, Section, Page (for air cooled condensers only)
Product data (Attach data furnished by the equipment supplier: I.e., "cut sheets")
| Compliance Schedule | Equipment Type | Total System Heat Rejection Capacity at Rated Conditions | Subcategory or Rating Conditions |  |  | Performance Required 2, 3
[7 empty] | gpm/hp |  | Btu/h-hp
| A | Propeller or Axial Fan Cooling Towers | All | 95OF Entering Water |  |  | >38.2
85OF Leaving Water
75OF wb Outdoor Air
| B | Centrifugal Fan Cooling Towers | All | 95OF Entering Water |  |  | >20.0
85OF Leaving Water
75OF wb Outdoor Air
| C | Air Cooled Condensers | All | 125OF Condenser Temp. R-22 Test Fluid |  |  |  |  | >176,000
190OF Entering Gas Temperature
15OF Subcooling
95OF Entering db
2 For purposes of this table, cooling tower performance is defined as maximum flow rating of tower divided by the fan nameplate rated motor horsepower
3 For purposes of this table, air-cooled condenser performance is defined as heat rejected from refrigerant divided by the fan nameplate rated motor horsepower
4-18
Equipment- Cooling Towers Discussion of equip-ment ratings and equipment defin-itions on page 4-19.
Exceptions Discussion of qualifying exceptions on page 3-11
Required Document-ation
Code Required Efficiencies
This schedule of equipment efficien-cies was reformatted from code, Table 13-R.
Equipment- Air Cooled Condensers Discussion of equip-ment ratings and equipment definitions on page 4-19.

## Wksht 4i
Worksheet 4i | Project Name: |  |  |  |  | Page:
BOILER - GAS-FIRED & OIL-FIRED
| (a) | (b) | ( c ) | (d) | (e) | (f)
| Equip. ID | Model Designation | Heating Capacity (Btu/hr) | Proposed Minimum AFUE (%) | Proposed Minimum Ec or ET (%) | Compliance Schedule (A-D)
Indicate source of information
GAMA Consumer Directory, page(s):
Product data (Attach data furnished by the equipment supplier, I.e., "cut sheets").
| Compliance Schedule | Equipment Type | Heating Capacity (Btu/hr)
|  |  | Over | But not over | Minimum Efficiency
| A | Gas Fired Hot Water | 0 | 300000 | 80% AFUE
|  |  | 300000 | 2500000 | 75% Et
|  |  | 2500000 | - | 80% Ec
| B | Gas Fired Steam | 0 | 300000 | 75% AFUE
|  |  | 300000 | 2500000 | 75% Et
|  |  | 2500000 | - | 80% Ec
| C | Oil Fired Hot Water, Steam | 0 | 300000 | 80% AFUE
|  |  | 300000 | 2500000 | 78% Et
|  |  | 2500000 | - | 83% Ec
| D | All | 300000 | 2500000 | 78% Et
|  | Oil Fired Residual Hot Water | 2500000 | - | 83% Ec
|  | Steam | 2500000 | - | 83% Ec
4-19
Equipment Discussion of equip-ment ratings and equipment definitions on page 4-19.
Exceptions Discussion of qualifying exceptions on page 3-11
Required Document-ation
Code Required Efficiencies
This schedule of equipment efficien-cies was reformatted from the code, Table 13-Q.

## Wksht 4j
Worksheet 4j |  | Project Name: |  |  |  |  | Page:
FURNACE & UNIT HEATERS - GAS & OIL-FIRED
| (a) | (b) | ( c ) | (d) Proposed |  |  | (e)
| Equip. ID | Model Designation | Heating Capacity (Btu/hr) | Minimum EC (%) | Minimum ET (%) | Minimum AFUE (%) | Compliance Schedule (A-E)
Indicate source of information
GAMA Consumer Directory, page(s):
Product data (Attach data furnished by the equipment supplier, I.e., "cut sheets").
| Compliance Schedule | Equipment Type | Capacity (Btu/hr)
|  |  | Over | But not over | Minimum Efficiency
| A | Gas Fired Warm-Air Furnaces & Combustion Furnace/AC | 0 | 225000 | 78% AFUE or 80% Et
|  |  | 225000 | - | 80% Ec
| B | Oil-Fired Warm-Air Furnaces & Combustion Furnace/AC | 0 | 225000 | 78% AFUE or 80% Et
|  |  | 225000 | - | 81% Et
| C | Gas Fired Duct Furnaces | ALL |  | 80% Ec
| D | Gas Fired Unit Heaters | ALL |  | 80% Ec
| E | Oil-Fired Unit Heaters | ALL |  | 80% Ec
4-20
Equipment Discussion of equip-ment ratings and equipment definitions on page 4-19.
Exceptions Discussion of qualifying exceptions on page 3-11
Required Document-ation
Code Required Efficiencies
This schedule of equip-ment efficiencies was reformatted from code, Table 13-P.

## Wksht 4k
Worksheet 4k |  |  | Project Name: |  |  |  |  | Page:
Simultaneous Heating and Cooling
* Additional pages may be necessary if building has more terminal units than there are lines in this form. If needed use Add New Worksheet button at bottom
Complete this form for all terminal units with reheat to verify compliance with Section 1318.2.1 exception 1.
Terminal Unit (Variable Air Volume (VAV) Box) CFM Design Conditions
| Required Information |  |  |  |  | Compliance Method - At Least One Method Must Comply
| Terminal Unit ID or Description/Location | Sq. ft Area Served | Max. Cooling Airflow-CFM | Max. Heating Airflow-CFM | Occupancy Ventilation-CFM | Ht CFM < or = to 30% of Max | Ht. CFM < or = to 0.4 CFM per sq. ft | Ht. CFM < or = to Occupancy Ventilation | Maximum Airflow is < or = to 300 CFM
4-21
Exceptions Discussion of qualifying exceptions on page 3-11
Exceptions Discussion of qualifying exceptions on page 3-11
Exceptions Discussion of qualifying exceptions on page 3-11
Exceptions Discussion of qualifying exceptions on page 4-22
Exceptions Discussion of qualifying exceptions on page 4-22
Exceptions Discussion of qualifying exceptions on page 4-22
Exceptions Discussion of qualifying exceptions on page 4-22
Exceptions Discussion of qualifying exceptions on page 4-22

## Wksht 4l
Worksheet 4l - |  | Project Name: |  |  |  | Page: | 10
AIR TRANSPORT ENERGY
Complete one worksheet for each fan system > 7.5 horsepower. Fan system horsepower is the sum of motor brake horsepower of all supply, return, and exhaust fans (including series fan-powered terminal units) that operate during design conditions.
| Fan System ID: |  |  | Areas Served:
| System serves hospital or laboratory and include flow control device for maintaining precise pressure control. | [7 empty] | FALSE
| Fan Identifier (Tag) | Fan Type (Supply, Return, Exhaust, Series VAV) | CFM | Constant Volume or VAV | Motor Brake HP | Nameplate Motor HP | Maximum Nameplate Motor HP Allowed
[9 empty] | Supply | Constant Volume | 0 |  | 0
[9 empty] | Return | VAV | 0 |  | 0
[9 empty] | Exhaust |  | 0 |  | 0
[9 empty] | SVAV |  | 0 |  | 0
[11 empty] | 0 |  | 0
[11 empty] | 0 |  | 0
[11 empty] | 0 |  | 0
[11 empty] | 0 |  | 0
[11 empty] | 0 |  | 0
[11 empty] | 0 |  | 0
[11 empty] | 0 |  | 0
[11 empty] | 0 |  | 0
[11 empty] | 0 |  | 0
[11 empty] | 0 |  | 0
[11 empty] | 0 |  | 0
[11 empty] | 0 |  | 0
[11 empty] | 0 |  | 0
[11 empty] | 0 |  | 0
[11 empty] | 0 |  | 0
[11 empty] | 0 |  | 0
[11 empty] | 0 | FALSE | 0
The Plans/Specs show brake hp, nameplate hp, and CFM in the following locations:
| Total System Supply Fan CFM | Constant Volume, VAV, or Hospital/Lab | Total System Brake HP | Total System Max Brake HP Allowed | Brake HP Complies | Nameplate HP Complies
Additional Pressure Drop Credit (all systems). Complete the section below if system contains filtration with a pressure drop at design flow in excess of 1" w.c. ( when filters are clean), heat recovery, or direct evaporative humidifier/cooler.
Additional Pressure Drop Credit for Hospitals and Laboratories. Complete the section below if system serves a hospital or laboratory and contains rully ducted return/exhaust, return/exhaust air flow control devices, or individual filter system efficiencies.
| All Systems | Additional Pressure Drop Credits |  |  | Pressure Drop, Inches, W.C.
|  | Filtration Pressure Drop >1" w.c. | [5 empty] | FALSE
|  | Heat Recovery | [5 empty] | FALSE
|  | Direct Evaporative Humidifier/Cooler | [5 empty] | FALSE
| Hospital and Laboratory Systems Only | Fully Ducted Return/Exhaust (0.5" credit) | [5 empty] | FALSE
|  | Return/Exhaust Flow Control Device (0.5" credit) | [5 empty] | FALSE
|  | Individual Filter Efficiency > or = 85% (0.5" credit) | [5 empty] | FALSE
Total Additional Pressure Drop Credit:
Manufacturer's product data sheet(s) is attached and design values are shown in plans/specs in the following locations
| Supply CFM | Constant Volume or VAV (Use VAV for Hospital or Lab Systems) |  | Total Additional Pressure Drop | Adjusted Max Allowed Brake HP | Total Brake HP (from above) | Adjusted Brake HP Complies
Add New Worksheet 4l
4-22 | 0.1
Exceptions Discussion of qualifying exceptions on page 3-11

## Wksht 4m
Worksheet 4m |  |  |  | Project Name: |  |  |  |  | Page:
NATURAL VENTILATION
1. Fill in worksheet for all spaces that will be provided with natural ventilation.
(a) | (b) | (C) | (d) | (e) | (f) | (g) | (h) | (I) | (j) | (k)
Space (Room # or name from plans) | Room Area (sqft) | Estimated Max Occupant Load from OMSC Table 403.3 (persons/1000sqft.) | Check if Smoking Area | Actual Max Load used to determine ventilation requirements (persons/1000sqft.) | Required CFM/person (from Table 403.3) | Required CFM/Sqft (from Table 403.3)1 | Required Ventilation CFM | Net Free Area of Outside Air Openings | Opening Area / Floor Area | Calculated Natural Ventilation to Space (design conditions)2
1 Use this column when ventilation requirement is based on CFM/sq ft per OMSC Table 4.3.3.
2 Complete this column if net free opening is less than 5% of floor area or 20% of floor area for smoking areas, otherwise enter N/A. Attach calculations.
1. Fill in worksheet for all spaces that will be provided with natural ventilation. (b): Number of Additional Worksheets 4m | 0
1
1. Fill in worksheet for all spaces that will be provided with natural ventilation. (a): 2. Describe calculation method used to determine ventilation delivered. Attach additional sheets as necessary | 2
3
4
3. Attach manual calculations, spreadsheets, computer model input and outputs, and other technical documentation that verifies
required ventilation will be provided to each space.
4. I certify that to the best of my knowledge, the natural ventilation calculations provided are correct.
This line to be signed and stamped by Architect or Engineer Registered in the State of Oregon.
4-23
Exceptions Discussion of qualifying exeptions on page 3-11

## Worksheet 4m-2 (hidden)
Worksheet 4m-2 |  |  |  | Project Name: |  |  |  | Page:
NATURAL VENTILATION
1. Fill in worksheet for all spaces that will be provided with natural ventilation.
(a) | (b) | (C) | (d) | (e) | (f) | (g) | (h) | (I) | (j) | (k)
Space (Room # or name from plans) | Room Area (sqft) | Estimated Max Occupant Load from OMSC Table 403.3 (persons/1000sqft.) | Check if Smoking Area | Actual Max Load used to determine ventilation requirements (sqft/person) | Required CFM/person (from Table 403.3) | Required CFM/Sqft (from Table 403.3)1 | Required Ventilation CFM | Net Free Area of Outside Air Openings | Opening Area / Floor Area | Calculated Natural Ventilation to Space (design conditions)2
1 Use this column when ventilation requirement is based on CFM/sq ft per OMSC Table 4.3.3.
2. Complete this column if net free opening is less than 5% of floor area or 20% of floor area for smoking areas, otherwise enter N/A. Attach calculations.
4-23
Exceptions Discussion of qualifying exeptions on page 3-11

## Worksheet 4m-3 (hidden)
Worksheet 4m-3 |  |  |  | Project Name: |  |  |  | Page:
NATURAL VENTILATION
1. Fill in worksheet for all spaces that will be provided with natural ventilation.
(a) | (b) | (C) | (d) | (e) | (f) | (g) | (h) | (I) | (j) | (k)
Space (Room # or name from plans) | Room Area (sqft) | Estimated Max Occupant Load from OMSC Table 403.3 (persons/1000sqft.) | Check if Smoking Area | Actual Max Load used to determine ventilation requirements (sqft/person) | Required CFM/person (from Table 403.3) | Required CFM/Sqft (from Table 403.3)1 | Required Ventilation CFM | Net Free Area of Outside Air Openings | Opening Area / Floor Area | Calculated Natural Ventilation to Space (design conditions)2
1 Use this column when ventilation requirement is based on CFM/sq ft per OMSC Table 4.3.3.
2. Complete this column if net free opening is less than 5% of floor area or 20% of floor area for smoking areas, otherwise enter N/A. Attach calculations.
4-23
Exceptions Discussion of qualifying exeptions on page 3-11

## Worksheet 4m-4 (hidden)
Worksheet 4m-3 |  |  |  | Project Name: |  |  |  | Page:
NATURAL VENTILATION
1. Fill in worksheet for all spaces that will be provided with natural ventilation.
(a) | (b) | (C) | (d) | (e) | (f) | (g) | (h) | (I) | (j) | (k)
Space (Room # or name from plans) | Room Area (sqft) | Estimated Max Occupant Load from OMSC Table 403.3 (persons/1000sqft.) | Check if Smoking Area | Actual Max Load used to determine ventilation requirements (sqft/person) | Required CFM/person (from Table 403.3) | Required CFM/Sqft (from Table 403.3)1 | Required Ventilation CFM | Net Free Area of Outside Air Openings | Opening Area / Floor Area | Calculated Natural Ventilation to Space (design conditions)2
1 Use this column when ventilation requirement is based on CFM/sq ft per OMSC Table 4.3.3.
2. Complete this column if net free opening is less than 5% of floor area or 20% of floor area for smoking areas, otherwise enter N/A. Attach calculations.
4-23
Exceptions Discussion of qualifying exeptions on page 3-11

## Worksheet 4m-5 (hidden)
Worksheet 4m-3 |  |  |  | Project Name: |  |  |  | Page:
NATURAL VENTILATION
1. Fill in worksheet for all spaces that will be provided with natural ventilation.
(a) | (b) | (C) | (d) | (e) | (f) | (g) | (h) | (I) | (j) | (k)
Space (Room # or name from plans) | Room Area (sqft) | Estimated Max Occupant Load from OMSC Table 403.3 (persons/1000sqft.) | Check if Smoking Area | Actual Max Load used to determine ventilation requirements (sqft/person) | Required CFM/person (from Table 403.3) | Required CFM/Sqft (from Table 403.3)1 | Required Ventilation CFM | Net Free Area of Outside Air Openings | Opening Area / Floor Area | Calculated Natural Ventilation to Space (design conditions)2
1 Use this column when ventilation requirement is based on CFM/sq ft per OMSC Table 4.3.3.
2. Complete this column if net free opening is less than 5% of floor area or 20% of floor area for smoking areas, otherwise enter N/A. Attach calculations.
4-23
Exceptions Discussion of qualifying exeptions on page 3-11

## Motor Lookup (hidden)
Look-up Table to return values from code table (to right) on worksheet 4l |  |  | TABLE 13-U - MAXIMUM ALLOWABLE FAN SYSTEM MOTOR HORSEPOWER
VARIABLE AIR VOLUME SYSTEMS | CONSTANT VOLUME SYSTEMS | MAXIMUM FAN MOTOR HORSEPOWER ALLOWED: | VARIABLE AIR VOLUME SYSTEMS | CONSTANT VOLUME SYSTEMS | MAXIMUM FAN MOTOR HORSEPOWER ALLOWED:
If maximum design airflow, in CFM,= or greater than: | If maximum design airflow, in CFM, is = or greater than: |  | If maximum design airflow, in CFM, is no more than1: | If maximum design airflow, in CFM, is no more than2:
0 | 0 | 8.5
5001 | 7001 | 13 | 5000 | 7000 | 8.5
7501 | 10501 | 17 | 7500 | 10500 | 13
10001 | 14001 | 21 | 10000 | 14000 | 17
12501 | 17501 | 25.5 | 12500 | 17500 | 21
15001 | 21251 | 30 | 15000 | 21250 | 25.5
17501 | 27001 | 34 | 17500 | 27000 | 30
20001 | 31001 | 37.5 | 20000 | 31000 | 34
25001 | 34001 | 49 | 25000 | 34000 | 37.5
32501 | 44301 | 60 | 32500 | 44300 | 49
40001 | 54501 | 75 | 40000 | 54500 | 60
50001 | 68001 | 94 | 50000 | 68000 | 75
62501 | 85201 | 113 | 62500 | 85200 | 94
75001 | 102201 | 150 | 75000 | 102200 | 113
|  |  | 100000 | 135500 | 150
1 For VAV system volumes over 100,000 CFM use the following formula:
Maximum fan motor horsepower (HP) = (design airflow CFM * 5.6) / 3718
2 For CV system volumes over 135,500 CFM use the following formula:
Maximum fan motor horsepower (HP) = (design airflow CFM *4.1) / 3718
MotorLook
200
150
125
100
75
60
50
40
30
25
20
15
10
7.5
5
3
2
1.5
1