## Form 5a
Form 5a | Project Name: |  | Page:
LIGHTING - GENERAL
1. Interior Exceptions (Section 1313.1)
No Interior Lighting. The building plans and specifications do not call for new or altered interior lighting.
Skip to item 5, Exterior building Lighting - General, below.
Exceptions. 1. The building or part of the building qualifies for an exception from code lighting
requirements. Applicable code exception is number:
2. Lighting equipment that qualifies for an exception - in addition to general lighting and is separately
controlled. Applicable code exception is number:
Areas of the building and equipment that qualify for any exceptions:
2. Local Shut-off controls (Section 1313.3.1.1)
Complies. At least one local shut-off lighting control for every 2,000 square feet of
lighted floor area and for all spaces enclosed by walls or ceiling height partitions.
This control is detailed in the building plans on drawing number:
Exception. The building or part of the building qualifies for an exception.
Applicable code exception is Section 1313.3.1.1, Exception:
Portions of the building that qualify:
3. Automatic Shutoff Controls (Section 1313.3.1.2)
Not Applicable. Office floor area is not over 2,000 square feet of contiguous office floor area or
permitted space is not over 5,000 square feet. No offices less than 300 square feet, meeting or conference rooms, or school classrooms.
Complies. All interior lighting systems are equipped with a separate automatic control to shut off lighting
during unoccupied periods. Offices less than 300 square feet, meeting and conference rooms, and school
classrooms are equipped with occupancy sensors that comply with Section 1313.3.1.2.1.
Compliance details in plans/specs:
Exception. The building or part of the building qualifies for an exception.
Applicable code exception is Section 1313.3.1,2, Exception:
Portions of the building that qualify:
4. Daylighting Controls (1313.3.1.3)
No classrooms or atriums with skylights or window to wall ratio greater than 50%.
Complies. All classrooms and atriums with window to wall ratio greater than 50% and/or skylights are
equipped with automatic daylight sensing controls, as required by Section 1313.3.1.3.1 and Section
1313.3.1.3.2. The daylight sensors specified comply with Section 1313.3.1.3.3.
Compliance details in plans/specs:
5. Exterior Lighting (Section 1313.5)
Complies. The plans do not call for use of incandescent or mercury vapor lamps for use on building exterior.
Exception. The building plans indicate luminaires with incandescent or mercury vapor lamps, but are
specified for use in or around swimming pools, water features, or other locations subject to requirements
of Article 680 of the 2002 National Electrical Code.
6. Exterior and Canopy Lighting Controls (Section 1313.3.2)
Complies. The building plans and specifications include photoelectric and/or clock switches on all exterior
lighting systems which are designed and programmed to extinguish lights when daylight is present, as
required by Section 1313.3.2.
7. Connected Lighting Power (Section 1313.4)
| NO | Complies. The lighting power does not exceed the power allowance established
in either the Tenant Space Method (Form 5b) or the Space-by-Space Method (Form 5c).
5-1
1
Exterior Build-ing Lighting
is lighting directed to illuminate the exterior of the building and adjacent walkways and loading areas with or without canopies.
Clock Switches shall be astronomic (seasonal correcting) type with separate programs for each day of the week and shall store energy to maintain timekeeping during power outages.
Plans/Specs
Show compliance by including a drawing sheet, detail number, and/or specification section and subparagraph.
Exceptions
Discussion of qualifying exceptions in instructions section.

## Form 5b
Form 5b | Project Name: |  |  | Page:
INTERIOR LIGHTING POWER - Tenant Space Method | [5 empty] | TABLE 13-G — TENANT SPACE METHOD MAXIMUM ALLOWABLE LIGHTING POWER DENSITY (LPD)
[6 empty] | Tenant or Building Type | Lighting Power Density (W/ft2)
|  | (a) | (b) | (c) | (d)
|  | Tenant or Building Type (Table-13G) | Floor Area (sq ft) | Max Power Density (W/ft2) | Lighting Power Budget (W) |  | 0
[6 empty] | Automotive Facility | 0.9
| 1. | Total Interior Lighting Power Budget (Watts) for Building. |  |  |  | Convention Center | 1.2
[6 empty] | Court House | 1.2
| 2. | Total length of track lighting (ft) |  |  | 0 | Dining: Bar Lounge/Leisure | 1.3
| 3. | Line 2 multiplied by 50 Watts/ft |  |  |  | Dining: Cafeteria/Fast Food | 1.4
| 4. | Total amperage of circuit breaker(s) serving track lighting (amps) |  |  |  | Dining: Family | 1.5
| 5. | Voltage of circuit breaker serving track lighting (volts) |  |  |  | Exercise Center | 1
| 6. | Maximum wattage of track lighting (multiply line 4 by line 5) |  |  |  | Fire Station | 0.8
| 7. | VA rating of the inline current limiter or the low voltage transformers |  |  |  | Gymnasium | 1.1
| 8. | Track Lighting Power (the lesser value of line 3, 6 or 7) |  |  |  | Healthcare – Clinic | 1
[6 empty] | Hospital | 1.2
[6 empty] | Hotel | 1
| 9. | Total Interior Lighting Power from Worksheet 5b-1 (Sum of Column (m)) |  | + |  | Library | 1.3
| 10. | Total Adjusted Interior Lighting Power (line 8 + line 9) |  | = |  | Manufacturing Facility, Non-process Areas3 | 1.3
| 11. | Does Interior Lighting Design Meet Budget? Line 10 must be no greater than line 1. |  |  |  | Motel | 1
[6 empty] | Motion Picture Theater | 1.2
| 12. | Do Exterior Canopies Meet Budget (Worksheets 5c)? |  |  | N/A | Multi-Family | 0.7
| 13. | Does Parking Garage Meet Budget (Worksheets 5c)? |  |  | N/A | Museum | 1.1
[6 empty] | Office | 1
[6 empty] | Parking Garage | 0.3
[6 empty] | Performing Arts Theater | 1.6
[6 empty] | Police Station | 1
[6 empty] | Religious Building | 1.3
[6 empty] | Retail | 1.5
[6 empty] | School/University | 1.1
[6 empty] | Service station canopies, including all types of vehicle fueling and service (except enclosed garages) | 2
[6 empty] | Sports Arena | 1.1
[6 empty] | Town Hall | 1
[6 empty] | Transportation | 1
[6 empty] | Warehouse | 0.8
[6 empty] | Workshop | 1.4
5-2
1 | A
2 | B | [6 empty] | 25 | 26 | 27
3 | E | [6 empty] | N/A | N/A | N/A
4 | F | [6 empty] | 0 | n/a | n/a
5 | H | [6 empty] | 0 | n/a | n/a
6 | I | [6 empty] | 0 | n/a | n/a
7 | R | [6 empty] | 0 | n/a | n/a
8 | S | [6 empty] | 0 | n/a | n/a
9 | U | [6 empty] | 0 | n/a | n/a
[8 empty] | 0 | n/a | n/a
[8 empty] | 0 | n/a | n/a
[8 empty] | 0 | n/a | n/a
[8 empty] | 0 | n/a | n/a
[8 empty] | 0 | n/a | n/a
[8 empty] | 0 | n/a | n/a
[8 empty] | 0 | n/a | n/a
[8 empty] | 0 | n/a | n/a
[8 empty] | 0 | n/a | n/a
[8 empty] | 0 | n/a | n/a
[8 empty] | 0 | n/a | n/a
[8 empty] | 0 | n/a | n/a
Lighting Budget
Track Lighting Power
Building's Interior Lighting Power
Occupancy/
Use Types
See instructions for desc-ription of occupancy types
Lighting Power Budget
Exterior Canopy Parking Garage Lighting Power

## Form 5c (hidden)
Form 5c |  | Project Name: |  | Page:
INTERIOR LIGHTING POWER - Space-by-Space Method
|  | 1. | Total Interior Lighting Power Budget from Worksheet 5b-1 (Sum of Column (l)) |  | 0 | 13 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
|  | 2. | Total length of track lighting (ft) |  | 0 | 15 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
|  | 3. | Line 2 multiplied by 50 Watts/ft |  |  | 16 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
|  | 4. | Total amperage of circuit breaker(s) serving track lighting (amps) |  |  | 17 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
|  | 5. | Voltage of circuit breaker serving track lighting (volts) |  |  | 18 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
|  | 6. | Maximum wattage of track lighting (multiply line 4 by line 5) |  |  | 19 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
|  | 7. | VA rating of the inline current limiter or the low voltage transformers
|  | 8. | Track Lighting Power (the lesser value of line 3, 6 or 7) |  |  | 20 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
|  | 9. | Total Interior Lighting Power from Worksheet 5b-1 (Sum of Column (m)) | +
|  | 10. | Total Adjusted Lighting Power (line 8 + line 9) | =
|  | 11. | Does Interior Lighting Design Meet Budget? Line 10 must be no greater than line 1.
|  | 12. | Do Exterior Canopies Meet Budget (Worksheets 5c)? |  | N/A
|  | 13. | Does Parking Garage Meet Budget (Worksheets 5c)? |  | N/A
|  | 14. | Does Each Space With Retail Display Lighting Meet Budget (Worksheets 5d)? |  | N/A
|  | 15. | Is The Total Retail Display Lighting Additional Power Less Than 17,500 W (sum of line 9 on Worksheets 5d)? |  | N/A
|  | 16. | Does Retail Display Lighting Meet Budget? |  | N/A
5-3
1 | A | [5 empty] | A |  |  | B
2 | B | [5 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27
3 | E |  |  |  |  | 1 | Restaurants | 1.5 | 1.5 | Barber shops and beauty parlors | 1.5 | 1.5 | Educational occupancies K-12 | 1.2 | 1.5 | Manufacturing spaces | exempt | exempt | Repair garage | 1.2 | 1.5 | Jails | exempt | exempt | Hotels (non guest rooms) | 1.2 | 1.5 | Repair garage | 1.5 | 1.5 | N/A | N/A | N/A
4 | F |  |  |  |  | 2 | 0 | n/a | n/a | Motor vehicle showrooms | 1.5 | 1.5 | Day care facility | 1.2 | 1.5 | 0 | n/a | n/a | Aircraft repair hangars | 1.2 | 1.5 | Prisons | exempt | exempt | Motels (non guest rooms) | 1.2 | 1.5 | Aircraft repair hangar | 1.5 | 1.5 | 0 | n/a | n/a
5 | H |  |  |  |  | 3 | Amusement arcades and buildings | 1.1 | 1.4 | Print shops | 1.5 | 1.5 | Schools for business or vocational training | 1.2 | 1.5 | Manufacturing Offices | 1.2 | 1.5 | 0 | n/a | n/a | Reformatories | exempt | exempt | Boarding housing (transient) | 1.2 | 1.5 | 0 | n/a | n/a | 0 | n/a | n/a
6 | I |  |  |  |  | 4 | Art galleries and museums | 1.1 | 1.4 | Research labs | 1.5 | 1.5 | 0 | n/a | n/a | Other non-manufacturing spaces | 1.2 | 1.5 | Other | Exempt | Exempt | Other detention facilities | exempt | exempt | 0 | n/a | n/a | Aircraft hangar, storage | 0.5 | 0.5 | 0 | n/a | n/a
7 | R |  |  |  |  | 5 | Athletic facilities - indoor | 1.1 | 1.4 | Restaurants | 1.5 | 1.5 | 0 | n/a | n/a | 0 | n/a | n/a | 0 | n/a | n/a | 0 | n/a | n/a | Guest rooms | exempt | exempt | 0 | n/a | n/a | 0 | n/a | n/a
8 | S |  |  |  |  | 6 | Auditoriums and lecture halls | 1.1 | 1.4 | 0 | n/a | n/a | 0 | n/a | n/a | 0 | n/a | n/a | 0 | n/a | n/a | Hospitals | 1.5 | 1.5 | 0 | n/a | n/a | Parking garage | 0.3 | 0.3 | 0 | n/a | n/a
9 | U |  |  |  |  | 7 | Churches | 1.1 | 1.4 | Animal hospitals, kennels, pounds | 1.2 | 1.5 | 0 | n/a | n/a | 0 | n/a | n/a | 0 | n/a | n/a | Nursing homes | 1.5 | 1.5 | Apartment houses | exempt | exempt | 0 | n/a | n/a | 0 | n/a | n/a
[6 empty] | 8 | Night clubs, bars, billiard parlors, taverns | 1.1 | 1.4 | Banks | 1.2 | 1.5 | 0 | n/a | n/a | 0 | n/a | n/a | 0 | n/a | n/a | Sanitariums | 1.5 | 1.5 | One- and two-family dwellings | exempt | exempt | Warehouse/storage | 0.8 | 1 | 0 | n/a | n/a
[6 empty] | 9 | Courtrooms | 1.1 | 1.4 | Car washes and motor vehicle stations | 1.2 | 1.5 | 0 | n/a | n/a | 0 | n/a | n/a | 0 | n/a | n/a | Health-care centers | 1.5 | 1.5 | 0 | n/a | n/a | 0 | n/a | n/a | 0 | n/a | n/a
[6 empty] | 10 | Funeral parlors | 1.1 | 1.4 | Civic administration | 1.2 | 1.5 | 0 | n/a | n/a | 0 | n/a | n/a | 0 | n/a | n/a | Convalescent hospitals | 1.5 | 1.5 | 0 | n/a | n/a | 0 | n/a | n/a | 0 | n/a | n/a
[6 empty] | 11 | Halls - banquet, community, dance, exhibition | 1.1 | 1.4 | Educational occupancies above the 12th grade | 1.2 | 1.5 | 0 | n/a | n/a | 0 | n/a | n/a | 0 | n/a | n/a | Orphanages | 1.5 | 1.5 | 0 | n/a | n/a | 0 | n/a | n/a | 0 | n/a | n/a
[6 empty] | 12 | Indoor tennis courts | 1.1 | 1.4 | Electronic data processing | 1.2 | 1.5 | 0 | n/a | n/a | 0 | n/a | n/a | 0 | n/a | n/a | Nursing homes | 1.5 | 1.5 | 0 | n/a | n/a | 0 | n/a | n/a | 0 | n/a | n/a
[6 empty] | 13 | Libraries | 1.1 | 1.4 | Laundry & dry cleaning | 1.2 | 1.5 | 0 | n/a | n/a | 0 | n/a | n/a | 0 | n/a | n/a | Homes for the aged | 1.5 | 1.5 | 0 | n/a | n/a | 0 | n/a | n/a | 0 | n/a | n/a
[6 empty] | 14 | Other | 1.1 | 1.4 | Offices | 1.2 | 1.5 | 0 | n/a | n/a | 0 | n/a | n/a | 0 | n/a | n/a | Mental care institutions | 1.5 | 1.5 | 0 | n/a | n/a | 0 | n/a | n/a | 0 | n/a | n/a
[6 empty] | 15 | Passenger stations (waiting areas) | 1.1 | 1.4 | Physician services and outpatient clinics | 1.2 | 1.5 | 0 | n/a | n/a | 0 | n/a | n/a | 0 | n/a | n/a | 0 | n/a | n/a | 0 | n/a | n/a | 0 | n/a | n/a | 0 | n/a | n/a
[6 empty] | 16 | Theaters - movie, drama | 1.1 | 1.4 | Police stations, fire stations and post offices | 1.2 | 1.5 | 0 | n/a | n/a | 0 | n/a | n/a | 0 | n/a | n/a | 0 | n/a | n/a | 0 | n/a | n/a | 0 | n/a | n/a | 0 | n/a | n/a
[6 empty] | 17 | TV and radio studios w/audience | 1.1 | 1.4 | Professional services (attorney, dentist, engineer, etc) | 1.2 | 1.5 | 0 | n/a | n/a | 0 | n/a | n/a | 0 | n/a | n/a | 0 | n/a | n/a | 0 | n/a | n/a | 0 | n/a | n/a | 0 | n/a | n/a
[6 empty] | 18 | 0 | n/a | n/a | Radio and television stations | 1.2 | 1.5 | 0 | n/a | n/a | 0 | n/a | n/a | 0 | n/a | n/a | 0 | n/a | n/a | 0 | n/a | n/a | 0 | n/a | n/a | 0 | n/a | n/a
[6 empty] | 19 | Athletic facilities - outdoor | exempt | exempt | 0 | n/a | n/a | 0 | n/a | n/a | 0 | n/a | n/a | 0 | n/a | n/a | 0 | n/a | n/a | 0 | n/a | n/a | 0 | n/a | n/a | 0 | n/a | n/a
Lighting Power Budget
Building's Interior Lighting Power
Track Lighting Power
Retail Display Lighting Power
Exterior Canopy Parking Garage Lighting Power

## Worksheet 5a
| Worksheet 5a | Project Name: |  |  |  |  | Page:
| LIGHTING FIXTURE SCHEDULE (see Table 5c in instructions for default luminaire power). | [9 empty] | Luminarie Power
| (a) | (b) |  | (c) |  | (d) |  | (e) | (f) |  |  | Lamp |  | Ballast |  |  | Watts/
| Lum ID | Luminaire |  | Lamp |  | Ballasts |  | Luminaire Power | Is Luminaire From |  |  | No. | Designation | No. | Abbreviation | Description | Luminaire | Comments
|  | Type | Description | No. | Description | No. | Description | (watts) | Table 5c | [9 empty] | Luminaire Types | Row_Start | Row_End
[10 empty] | TRUE | Fluorescent Circline
[10 empty] | FALSE | Rapid Start (20W) | [7 empty] | User Defined | 682 | 682
[10 empty] | FALSE | 1-FC6T9-MAG STD-25W | 1 | FC6T9 | 1 | MAG STD | Magnetic Standard. RS | 25 | 6” OD | Track Lighting | 681 | 681
[10 empty] | FALSE | Rapid Start (22 W) | [7 empty] | Fluorescent Circline | 8 | 27
[10 empty] | FALSE | 1-FC8T9-MAG STD-27W | 1 | FC8T9 | 1 | MAG STD | Magnetic Standard. RS | 27 | 8" OD | Compact Fluorescent 2D | 29 | 47
[10 empty] | FALSE | Rapid Start (32 W) | [7 empty] | Compact Fluorescent Twin | 49 | 69
[10 empty] | FALSE | 1-FC12T9-MAG STD-45W | 1 | FC12T9 | 1 | MAG STD | Magnetic Standard. RS | 45 | 12" OD | Compact Fluorescent Quad | 71 | 128
[10 empty] | FALSE | Rapid Start (40 W) | [7 empty] | Compact Fluorescent Triple | 130 | 151
[10 empty] | FALSE | 1-FC16T9-MAG STD-57W | 1 | FC16T9 | 1 | MAG STD | Magnetic Standard. RS | 57 | 16" OD | Compact Fluorescent Triple or Quad | 153 | 163
[10 empty] | FALSE | T5 Program Start (22 W) | [7 empty] | Long Compact Fluorescent Twin - T5 (18-24W) | 165 | 186
[10 empty] | FALSE | 1-FC9T5-ELECT NO-28W | 1 | FC9T5 | 1 | ELECT NO | Electronic Normal Light. PS | 28 | 8" OD | Long Compact Fluorescent Twin - T5 (36W) | 188 | 199
[10 empty] | FALSE | 2-FC9T5-ELECT NO-53W | 2 | FC9T5 | 1 | ELECT NO | Electronic Normal Light. PS | 53 |  | Long Compact Fluorescent Twin - T5 (40W) | 201 | 215
[10 empty] | FALSE | T5 Program Start (40 W) | [7 empty] | Long Compact Fluorescent Twin - T5 (50-55-80W) | 217 | 233
[10 empty] | FALSE | 1-FC12T5-ELECT NO-41W | 1 | FC12T5 | 1 | ELECT NO | Electronic Normal Light. PS | 41 | 12" OD | Fluorescent U-Tube - T8 | 235 | 250
[10 empty] | FALSE | 2-FC12T5-ELECT NO-80W | 2 | FC12T5 | 1 | ELECT NO | Electronic Normal Light. PS | 80 |  | Fluorescent U-Tube - T12 | 252 | 277
[10 empty] | FALSE | T5 Rapid Start (55 W) | [7 empty] | Fluorescent Linear Lamps - Preheat | 279 | 300
[10 empty] | FALSE | 1-FC12T5HO-ELECT NO-55W | 1 | FC12T5HO | 1 | ELECT NO | Electronic Normal Light. RS | 55 | 12" OD | Fluorescent Linear Lamps T5 | 302 | 326
[10 empty] | FALSE | 2-FC12T5HO-ELECT NO-103W | 2 | FC12T5HO | 1 | ELECT NO | Electronic Normal Light. RS | 103 |  | Fluorescent Rapid Start T8 - 2 foot | 328 | 340
[10 empty] | FALSE | 1-FC12T5HO-ELECT DIM-59W | 1 | FC12T5HO | 1 | ELECT DIM | Electronic Dimming. RS | 59 |  | Fluorescent Rapid Start T8 - 3 foot | 342 | 365
[10 empty] | FALSE | T5 Rapid Start (40 + 22 W) | [7 empty] | Fluorescent T8 - 4 foot | 367 | 423
[10 empty] | FALSE | 1-FC12T5/FC9T5-ELECT NO-68W | 1 | FC12T5/FC9T5 | 1 | ELECT NO | Electronic Normal Light. RS | 68 | 8” & 12" OD | Fluorescent Rapid Start T12 - 3 foot | 425 | 440
[10 empty] | FALSE | Compact Fluorescent 2D | [7 empty] | Fluorescent Rapid Start T12 - 4 foot (32 to 34 W) | 442 | 480
[10 empty] | FALSE | 10W, GR10q-4 Four Pin Base | [7 empty] | Fluorescent Rapid Start T12 - 4 foot (40 W) | 482 | 522
[10 empty] | FALSE | 1-CFS10W/GR10q-MAG STD-16W | 1 | CFS10W/GR10q | 1 | MAG STD | Magnetic Standard | 16 | 3.6" across | Fluorescent Rapid Start T10 - 4 foot | 524 | 545
[10 empty] | FALSE | 1-CFS10W/GR10q-ELECT-13W | 1 | CFS10W/GR10q | 1 | ELECT | Electronic | 13 |  | Fluorescent Rapid Start High Output T8 & T12 - 8 ft | 547 | 566
[10 empty] | FALSE | 2-CFS10W/GR10q-ELECT-26W | 2 | CFS10W/GR10q | 1 | ELECT | Electronic | 26 |  | Fluorescent Instant Start (Slimline) T8 & T12 | 568 | 591
[10 empty] | FALSE | 16W, GR10q-4 Four Pin Base | [7 empty] | High Intensity Discharge - Mercury Vapor | 593 | 600
[10 empty] | FALSE | 1-CFS16W/GR10q-MAG STD-23W | 1 | CFS16W/GR10q | 1 | MAG STD | Magnetic Standard | 23 | 5.5" across | High Intensity Discharge - Metal Halide | 602 | 637
[10 empty] | FALSE | 1-CFS16W/GR10q-ELECT-15W | 1 | CFS16W/GR10q | 1 | ELECT | Electronic | 15 |  | High Intensity Discharge - High Pressure Sodium | 639 | 652
[10 empty] | FALSE | 2-CFS16W/GR10q-ELECT-30W | 2 | CFS16W/GR10q | 1 | ELECT | Electronic | 30 |  | High Intensity Discharge - Low Pressure Sodium | 654 | 659
[10 empty] | FALSE | 21W, GR10q-4 Four Pin Base | [7 empty] | 12 Volt Tungsten Halogen Lamps | 661 | 680
[10 empty] | FALSE | 1-CFS21W/GR10q-MAG STD-31W | 1 | CFS21W/GR10q | 1 | MAG STD | Magnetic Standard | 31 | 5.5" across
[10 empty] | FALSE | 1-CFS21W/GR10q-ELECT-21W | 1 | CFS21W/GR10q | 1 | ELECT | Electronic | 21
[10 empty] | FALSE | 2-CFS21W/GR10q-ELECT-42W | 2 | CFS21W/GR10q | 1 | ELECT | Electronic | 42
[10 empty] | FALSE | 28W, GR10q-4 Four Pin Base
[10 empty] | FALSE | 1-CFS28W/GR10q-MAG STD-38W | 1 | CFS28W/GR10q | 1 | MAG STD | Magnetic Standard | 38 | 8.1" across
[10 empty] | FALSE | 1-CFS28W/GR10q-ELECT-28W | 1 | CFS28W/GR10q | 1 | ELECT | Electronic | 28
[10 empty] | FALSE | 2-CFS28W/GR10q-ELECT-56W | 2 | CFS28W/GR10q | 1 | ELECT | Electronic | 56
[10 empty] | FALSE | 38W, GR10q-4 Four Pin Base
[10 empty] | FALSE | 1-CFS38W/GR10q-ELECT-37W | 1 | CFS38W/GR10q | 1 | ELECT | Electronic | 37 | 8.1" across
[10 empty] | FALSE | 2-CFS38W/GR10q-ELECT-74W | 2 | CFS38W/GR10q | 1 | ELECT | Electronic | 74
[10 empty] | FALSE | Compact Fluorescent Twin
[10 empty] | FALSE | 5 W, G23 Two Pin Base - F5TT Lamp
[10 empty] | FALSE | 1-CFT5W/G23-MAG STD-9W | 1 | CFT5W/G23 | 1 | MAG STD | Magnetic Standard | 9 | 4.1" MOL
[10 empty] | FALSE | 2-CFT5W/G23-MAG STD-18W | 2 | CFT5W/G23 | 2 | MAG STD | Magnetic Standard | 18
[10 empty] | FALSE | 7 W, G23 Two Pin Base - F7TT Lamp
[10 empty] | FALSE | 1-CFT7W/G23-MAG STD-11W | 1 | CFT7W/G23 | 1 | MAG STD | Magnetic Standard | 11 | 5.3" MOL
[10 empty] | FALSE | 2-CFT7W/G23-MAG STD-22W | 2 | CFT7W/G23 | 2 | MAG STD | Magnetic Standard | 22
[10 empty] | FALSE | 7 W, 2G7 Four Pin Base - F7TT Lamp
[10 empty] | FALSE | 1-CFT7W/2G7-ELECT-8W | 1 | CFT7W/2G7 | 1 | ELECT | Electronic | 8 | 5.3" MOL
[10 empty] | FALSE | 2-CFT7W/2G7-ELECT-16W | 2 | CFT7W/2G7 | 2 | ELECT | Electronic | 16
[10 empty] | FALSE | 9 W, G23 Two Pin Base - F9TT Lamp
[10 empty] | FALSE | 1-CFT9W/G23-MAG STD-13W | 1 | CFT9W/G23 | 1 | MAG STD | Magnetic Standard | 13 | 6.5" MOL
[10 empty] | FALSE | 2-CFT9W/G23-MAG STD-26W | 2 | CFT9W/G23 | 2 | MAG STD | Magnetic Standard | 26
[10 empty] | FALSE | 9 W, 2G7 Four Pin Base - F9TT Lamp
[10 empty] | FALSE | 1-CFT9W/2G7-ELECT-10W | 1 | CFT9W/2G7 | 1 | ELECT | Electronic | 10 | 6.5" MOL
[10 empty] | FALSE | 2-CFT9W/2G7-ELECT-20W | 2 | CFT9W/2G7 | 2 | ELECT | Electronic | 20
[10 empty] | FALSE | 13 W, GX23 Two Pin Base - F13TT
[10 empty] | FALSE | 1-CFT13W/GX23-MAG STD-17W | 1 | CFT13W/GX23 | 1 | MAG STD | Magnetic Standard | 17 | 7.5" MOL
[10 empty] | FALSE | 2-CFT13W/GX23-MAG STD-34W | 2 | CFT13W/GX23 | 2 | MAG STD | Magnetic Standard | 34
[10 empty] | FALSE | 13 W, 2GX7 Four Pin Base - F13TT
[10 empty] | FALSE | 1-CFT13W/2GX7-ELECT-17W | 1 | CFT13W/2GX7 | 1 | ELECT | Electronic | 17 | 7.5" MOL
[10 empty] | FALSE | 2-CFT13W/2GX7-ELECT-34W | 2 | CFT13W/2GX7 | 2 | ELECT | Electronic | 34
[10 empty] | FALSE | Compact Fluorescent Quad
[10 empty] | FALSE | 9 W, G23-2 Two Pin Base - F9DTT Lamp
[10 empty] | FALSE | 1-CFQ9W/G23-2-MAG STD 120-13W | 1 | CFQ9W/G23-2 | 1 | MAG STD 120 | 120 V Magnetic Standard | 13 | 4.4" MOL
[10 empty] | FALSE | 2-CFQ9W/G23-2-MAG STD 120-26W | 2 | CFQ9W/G23-2 | 2 | MAG STD 120 | 120 V Magnetic Standard | 26
[10 empty] | FALSE | 13 W, G24d-1 Two Pin Base - F13DTT Lamp
[10 empty] | FALSE | 1-CFQ13W/G24d-1-MAG STD 120-18W | 1 | CFQ13W/G24d-1 | 1 | MAG STD 120 | 120 V Magnetic Standard | 18 | 6.0" MOL
[10 empty] | FALSE | 2-CFQ13W/G24d-1-MAG STD 120-36W | 2 | CFQ13W/G24d-1 | 2 | MAG STD 120 | 120 V Magnetic Standard | 36
[10 empty] | FALSE | 1-CFQ13W/G24d-1-MAG STD 277-16W | 1 | CFQ13W/G24d-1 | 1 | MAG STD 277 | 277 V Magnetic Standard | 16
[10 empty] | FALSE | 2-CFQ13W/G24d-1-MAG STD 277-32W | 2 | CFQ13W/G24d-1 | 2 | MAG STD 277 | 227 V Magnetic Standard | 32
[10 empty] | FALSE | 13 W, GX23-2 Two Pin Base
[10 empty] | FALSE | 1-CFQ13W/GX23-2-MAG STD-17W | 1 | CFQ13W/GX23-2 | 1 | MAG STD | Magnetic Standard | 17 | 4.8" MOL
[10 empty] | FALSE | 2-CFQ13W/GX23-2-MAG STD-34W | 2 | CFQ13W/GX23-2 | 2 | MAG STD | Magnetic Standard | 34
[10 empty] | FALSE | 16W GX32d-1 Two Pin Base
[10 empty] | FALSE | 1-CFQ16W/GX32d-1-MAG STD-20W | 1 | CFQ16W/GX32d-1 | 1 | MAG STD | Magnetic Standard | 20 | 5.5" MOL
[10 empty] | FALSE | 2-CFQ16W/GX32d-1-MAG STD-40W | 2 | CFQ16W/GX32d-1 | 2 | MAG STD | Magnetic Standard | 40
[10 empty] | FALSE | 18 W, G24d-2 Two Pin Base - F18DTT Lamp
[10 empty] | FALSE | 1-CFQ18W/G24d-2-MAG STD 120-25W | 1 | CFQ18W/G24d-2 | 1 | MAG STD 120 | 120 V Magnetic Standard | 25 | 6.8" MOL
[10 empty] | FALSE | 2-CFQ18W/G24d-2-MAG STD 120-50W | 2 | CFQ18W/G24d-2 | 2 | MAG STD 120 | 120 V Magnetic Standard | 50
[10 empty] | FALSE | 1-CFQ18W/G24d-2-MAG STD 277-22W | 1 | CFQ18W/G24d-2 | 1 | MAG STD 277 | 227 V Magnetic Standard | 22
[10 empty] | FALSE | 2-CFQ18W/G24d-2-MAG STD 277-44W | 2 | CFQ18W/G24d-2 | 2 | MAG STD 277 | 227 V Magnetic Standard | 44
[10 empty] | FALSE | 22W, GX32d Two Pin Base
[10 empty] | FALSE | 1-CFQ22W/GX32d-2-MAG STD-27W | 1 | CFQ22W/GX32d-2 | 1 | MAG STD | Magnetic Standard | 27 | 6.0” MOL
[10 empty] | FALSE | 2-CFQ22W/GX32d-2-MAG STD-54W | 2 | CFQ22W/GX32d-2 | 2 | MAG STD | Magnetic Standard | 54
[10 empty] | FALSE | 26 W, G24d-3 Two Pin Base - F26DTT Lamp
[10 empty] | FALSE | 1-CFQ26W/G24d-3-MAG STD 120-37W | 1 | CFQ26W/G24d-3 | 1 | MAG STD 120 | 120 V Magnetic Standard | 37 | 7.6" MOL
[10 empty] | FALSE | 2-CFQ26W/G24d-3-MAG STD 120-74W | 2 | CFQ26W/G24d-3 | 2 | MAG STD 120 | 120 V Magnetic Standard | 74
[10 empty] | FALSE | 1-CFQ26W/G24d-3-MAG STD 277-33W | 1 | CFQ26W/G24d-3 | 1 | MAG STD 277 | 227 V Magnetic Standard | 33
[10 empty] | FALSE | 2-CFQ26W/G24d-3-MAG STD 277-66W | 2 | CFQ26W/G24d-3 | 2 | MAG STD 277 | 227 V Magnetic Standard | 66
[10 empty] | FALSE | 1-CFQ26W/G24d-3-ELECT 277V-27W | 1 | CFQ26W/G24d-3 | 1 | ELECT 277V | 277 V Electronic | 27
[10 empty] | FALSE | 2-CFQ26W/G24d-3-ELECT 277V-54W | 2 | CFQ26W/G24d-3 | 2 | ELECT 277V | 277 V Electronic | 54
[10 empty] | FALSE | 26W, G24q-3 Four Pin Base
[10 empty] | FALSE | 1-CFQ26W/G24q-3-ELECT-26W | 1 | CFQ26W/G24q-3 | 1 | ELECT | Electronic | 26 | 7.6” MOL
[10 empty] | FALSE | 2-CFQ26W/G24q-3-ELECT-52W | 2 | CFQ26W/G24q-3 | 2 | ELECT | Electronic | 52
[10 empty] | FALSE | 28W GX32d Two Pin Base
[10 empty] | FALSE | 1-CFQ28W/GX32d-3-MAG STD-34W | 1 | CFQ28W/GX32d-3 | 1 | MAG STD | Magnetic Standard | 34 | 6.8" MOL
[10 empty] | FALSE | 2-CFQ28W/GX32d-3-MAG STD-68W | 2 | CFQ28W/GX32d-3 | 2 | MAG STD | Magnetic Standard | 68
[10 empty] | FALSE | 10 W, G24q-1 Four Pin Base
[11 empty] | 1-CFQ10W/G24q-1-MAG STD 120-16W | 1 | CFQ10W/G24q-1 | 1 | MAG STD 120 | 120 V Magnetic Standard | 16 | 4.6" MOL
5-4 | [10 empty] | 2-CFQ10W/G24q-1-MAG STD 120-32W | 2 | CFQ10W/G24q-1 | 2 | MAG STD 120 | 120 V Magnetic Standard | 32
[11 empty] | 1-CFQ10W/G24q-1-MAG STD 277-13W | 1 | CFQ10W/G24q-1 | 1 | MAG STD 277 | 227 V Magnetic Standard | 13
[11 empty] | 2-CFQ10W/G24q-1-MAG STD 277-26W | 2 | CFQ10W/G24q-1 | 2 | MAG STD 277 | 227 V Magnetic Standard | 26
13 W, G24q-1 Four Pin Base
[11 empty] | 1-CFQ13W/G24q-1-MAG STD 120-18W | 1 | CFQ13W/G24q-1 | 1 | MAG STD 120 | 120 V Magnetic Standard | 18 | 6.0" MOL
[11 empty] | 2-CFQ13W/G24q-1-MAG STD 120-36W | 2 | CFQ13W/G24q-1 | 2 | MAG STD 120 | 120 V Magnetic Standard | 36
[11 empty] | 1-CFQ13W/G24q-1-MAG STD 277-16W | 1 | CFQ13W/G24q-1 | 1 | MAG STD 277 | 227 V Magnetic Standard | 16
[11 empty] | 2-CFQ13W/G24q-1-MAG STD 277-32W | 2 | CFQ13W/G24q-1 | 2 | MAG STD 277 | 227 V Magnetic Standard | 32
[11 empty] | 1-CFQ13W/G24q-1-ELECT-14W | 1 | CFQ13W/G24q-1 | 1 | ELECT | Electronic | 14
[11 empty] | 2-CFQ13W/G24q-1-ELECT-25W | 2 | CFQ13W/G24q-1 | 2 | ELECT | Electronic | 25
13 W, GX7 Four Pin Base
[11 empty] | 1-CFQ13W/GX7-MAG STD-17W | 1 | CFQ13W/GX7 | 1 | MAG STD | Magnetic Standard | 17 | 4.8" MOL
[11 empty] | 2-CFQ13W/GX7-MAG STD-34W | 2 | CFQ13W/GX7 | 2 | MAG STD | Magnetic Standard | 34
18 W, G24q-2 Four Pin Base
[11 empty] | 1-CFQ18W/G24q-2-MAG STD 120-25W | 1 | CFQ18W/G24q-2 | 1 | MAG STD 120 | 120 V Magnetic Standard | 25 | 6.8" MOL
[11 empty] | 2-CFQ18W/G24q-2-MAG STD 120-50W | 2 | CFQ18W/G24q-2 | 2 | MAG STD 120 | 120 V Magnetic Standard | 50
[11 empty] | 1-CFQ18W/G24q-2-MAG STD 277-22W | 1 | CFQ18W/G24q-2 | 1 | MAG STD 277 | 227 V Magnetic Standard | 22
[11 empty] | 2-CFQ18W/G24q-2-MAG STD 277-44W | 2 | CFQ18W/G24q-2 | 2 | MAG STD 277 | 227 V Magnetic Standard | 44
[11 empty] | 1-CFQ18W/G24q-2-ELECT-21W | 1 | CFQ18W/G24q-2 | 1 | ELECT | Electronic | 21
[11 empty] | 2-CFQ18W/G24q-2-ELECT-38W | 2 | CFQ18W/G24q-2 | 2 | ELECT | Electronic | 38
[11 empty] | 3-CFQ18W/G24q-2-ELECT-50W | 3 | CFQ18W/G24q-2 | 1 | ELECT | Electronic | 50
Compact Fluorescent Triple
13 W, GX24q-1 Four Pin Base
[11 empty] | 1-CFM 13W/GX24q-1-MAG STD-18W | 1 | CFM 13W/GX24q-1 | 1 | MAG STD | Magnetic Standard | 18 | 4.2" MOL
[11 empty] | 2-CFM 13W/GX24q-1-MAG STD-36W | 2 | CFM 13W/GX24q-1 | 2 | MAG STD | Magnetic Standard | 36
[11 empty] | 1-CFM 13W/GX24q-1-ELECT-14W | 1 | CFM 13W/GX24q-1 | 1 | ELECT | Electronic | 14
[11 empty] | 2-CFM 13W/GX24q-1-ELECT-25W | 2 | CFM 13W/GX24q-1 | 2 | ELECT | Electronic | 25
18W, GX24q-2 Four Pin Base
[11 empty] | 1-CFM 18W/GX24q-2-MAG STD-25W | 1 | CFM 18W/GX24q-2 | 1 | MAG STD | Magnetic Standard | 25 | 5.0" MOL
[11 empty] | 2-CFM 18W/GX24q-2-MAG STD-50W | 2 | CFM 18W/GX24q-2 | 2 | MAG STD | Magnetic Standard | 50
[11 empty] | 1-CFM 18W/GX24q-2-ELECT-21W | 1 | CFM 18W/GX24q-2 | 1 | ELECT | Electronic | 21
[11 empty] | 2-CFM 18W/GX24q-2-ELECT-38W | 2 | CFM 18W/GX24q-2 | 2 | ELECT | Electronic | 38
26W, GX24q-3 Four Pin Base
[11 empty] | 1-CFTR26W/GX24q-3-MAG STD-37W | 1 | CFTR26W/GX24q-3 | 1 | MAG STD | Magnetic Standard | 37 | 4.9 to 5.4" MOL
[11 empty] | 2-CFTR26W/GX24q-3-MAG STD-74W | 2 | CFTR26W/GX24q-3 | 2 | MAG STD | Magnetic Standard | 74
[11 empty] | 1-CFTR26W/GX24q-3-ELECT-28W | 1 | CFTR26W/GX24q-3 | 1 | ELECT | Electronic | 28
[11 empty] | 2-CFTR26W/GX24q-3-ELECT-55W | 2 | CFTR26W/GX24q-3 | 1 | ELECT | Electronic | 55
[11 empty] | 1-CFTR26W/GX24q-3-ELECT DIM-29W | 1 | CFTR26W/GX24q-3 | 1 | ELECT DIM | Electronic DImming | 29
[11 empty] | 2-CFTR26W/GX24q-3-ELECT DIM-57W | 2 | CFTR26W/GX24q-3 | 1 | ELECT DIM | Electronic Dimming | 57
32 W, GX24q-3 Four Pin Base
[11 empty] | 1-CFTR32WGX24q-3-ELECT-35W | 1 | CFTR32WGX24q-3 | 1 | ELECT | Electronic | 35
[11 empty] | 2-CFTR32WGX24q-3-ELECT-69W | 2 | CFTR32WGX24q-3 | 1 | ELECT | Electronic | 69
[11 empty] | 1-CFTR32WGX24q-3-ELECT DIM-38W | 1 | CFTR32WGX24q-3 | 1 | ELECT DIM | Electronic DImming | 38 | BF~1.05
[11 empty] | 2-CFTR32WGX24q-3-ELECT DIM-76W | 2 | CFTR32WGX24q-3 | 1 | ELECT DIM | Electronic Dimming | 76 | BF~1.05
Compact Fluorescent Triple or Quad
42W, GX24q-4 Four Pin Base
[11 empty] | 1-CFTR42WGX24q-4-ELECT-46W | 1 | CFTR42WGX24q-4 | 1 | ELECT | Electronic | 46
[11 empty] | 2-CFTR42WGX24q-4-ELECT-94W | 2 | CFTR42WGX24q-4 | 1 | ELECT | Electronic | 94
[11 empty] | 1-CFTR42WGX24q-4-ELECT DIM-49W | 1 | CFTR42WGX24q-4 | 1 | ELECT DIM | Electronic DImming | 49 | BF~1.05
[11 empty] | 2-CFTR42WGX24q-4-ELECT DIM-98W | 2 | CFTR42WGX24q-4 | 1 | ELECT DIM | Electronic Dimming | 98 | BF~1.05
57W, GX24q-5 Four Pin Base
[11 empty] | 1-CFTR57WGX24q-5-ELECT-62W | 1 | CFTR57WGX24q-5 | 1 | ELECT | Electronic | 62
[11 empty] | 1-CFTR57WGX24q-5-ELECT DIM-66W | 1 | CFTR57WGX24q-5 | 1 | ELECT DIM | Electronic Dimming | 66 | BF~1.05
70W, GX24q-6 Four Pin Base
[11 empty] | 1-CFTR70WGX24q-6-ELECT-75W | 1 | CFTR70WGX24q-6 | 1 | ELECT | Electronic | 75
[11 empty] | 1-CFTR70WGX24q-6-ELECT DIM-80W | 1 | CFTR70WGX24q-6 | 1 | ELECT DIM | Electronic DImming | 80 | BF~1.00
Long Compact Fluorescent Twin - T5 (18-24W)
T5 (18W - F18TT Lamp)
[11 empty] | 1-FT18W/2G11-MAGNETIC-23W | 1 | FT18W/2G11 | 1 | MAGNETIC | Magnetic Energy Efficient | 23 | BF~1.0
[11 empty] | 2-FT18W/2G11-MAGNETIC-46W | 2 | FT18W/2G11 | 1 | MAGNETIC | Magnetic Energy Efficient | 46 | BF~1.0
[11 empty] | 3-FT18W/2G11-MAGNETIC-69W | 3 | FT18W/2G11 | 1 | MAGNETIC | Magnetic Energy Efficient | 69
[11 empty] | 3-FT18W/2G11-MAGNETIC-69W | 3 | FT18W/2G11 | 2 | MAGNETIC | Magnetic Energy Efficient | 69
[11 empty] | 4-FT18W/2G11-MAGNETIC-92W | 4 | FT18W/2G11 | 2 | MAGNETIC | Magnetic Energy Efficient | 92 | (2) 2-lamp ballasts
[11 empty] | 1-FT18W/2G11-ELECT-24W | 1 | FT18W/2G11 | 1 | ELECT | Electronic | 24
[11 empty] | 2-FT18W/2G11-ELECT-35W | 2 | FT18W/2G11 | 1 | ELECT | Electronic | 35
[11 empty] | 3-FT18W/2G11-ELECT-52W | 3 | FT18W/2G11 | 1 | ELECT | Electronic | 52
[11 empty] | 3-FT18W/2G11-ELECT-52W | 3 | FT18W/2G11 | 2 | ELECT | Electronic | 52
[11 empty] | 4-FT18W/2G11-ELECT-70W | 4 | FT18W/2G11 | 2 | ELECT | Electronic | 70 | (2) 2-lamp ballasts
T5 (24-27W- F24TT or F27TT Lamp)
[11 empty] | 1-FT24W/2G11-MAGNETIC-32W | 1 | FT24W/2G11 | 1 | MAGNETIC | Magnetic Energy Efficient | 32
[11 empty] | 2-FT24W/2G11-MAGNETIC-66W | 2 | FT24W/2G11 | 1 | MAGNETIC | Magnetic Energy Efficient | 66
[11 empty] | 3-FT24W/2G11-MAGNETIC-99W | 3 | FT24W/2G11 | 1.5 | MAGNETIC | Magnetic Energy Efficient | 99 | Tandem Wired
[11 empty] | 3-FT24W/2G11-MAGNETIC-98W | 3 | FT24W/2G11 | 2 | MAGNETIC | Magnetic Energy Efficient | 98
[11 empty] | 4-FT24W/2G11-MAGNETIC-132W | 4 | FT24W/2G11 | 2 | MAGNETIC | Magnetic Energy Effcient | 132 | (2) 2-lamp Ballasts
[11 empty] | 1-FT24W/2G11-ELECT-27W | 1 | FT24W/2G11 | 1 | ELECT | Electronic | 27 | BF~1.0
[11 empty] | 2-FT24W/2G11-ELECT-52W | 2 | FT24W/2G11 | 1 | ELECT | Electronic | 52 | BF~1.0
[11 empty] | 3-FT24W/2G11-ELECT-64W | 3 | FT24W/2G11 | 1.5 | ELECT | Electronic | 64 | Tandem Wired
[11 empty] | 3-FT24W/2G11-ELECT-64W | 3 | FT24W/2G11 | 2 | ELECT | Electronic | 64
[11 empty] | 4-FT24W/2G11-ELECT-88W | 4 | FT24W/2G11 | 2 | ELECT | Electronic | 88 | (2) 2-lamp ballasts
Long Compact Fluorescent Twin - T5 (36W)
T5 (36-39W - F36TT or F39TT Lamp)
[11 empty] | 1-FT36W/2G11-MAG EE-51W | 1 | FT36W/2G11 | 1 | MAG EE | Magnetic Energy Efficient | 51
[11 empty] | 2-FT36W/2G11-MAG EE-66W | 2 | FT36W/2G11 | 1 | MAG EE | Magnetic Energy Efficient | 66
[11 empty] | 3-FT36W/2G11-MAG EE-117W | 3 | FT36W/2G11 | 2 | MAG EE | Magnetic Energy Efficient | 117
[11 empty] | 4-FT36W/2G11-MAG EE-132W | 4 | FT36W/2G11 | 2 | MAG EE | Magnetic Energy Efficient | 132
[11 empty] | 1-FT36W/2G11-ELECT-37W | 1 | FT36W/2G11 | 1 | ELECT | Electronic | 37
[11 empty] | 2-FT36W/2G11-ELECT-70W | 2 | FT36W/2G11 | 1 | ELECT | Electronic | 70
[11 empty] | 3-FT36W/2G11-ELECT-105W | 3 | FT36W/2G11 | 1.5 | ELECT | Electronic | 105
[11 empty] | 3-FT36W/2G11-ELECT-107W | 3 | FT36W/2G11 | 2 | ELECT | Electronic | 107
[11 empty] | 4-FT36W/2G11-ELECT -140W | 4 | FT36W/2G11 | 2 | ELECT | Electronic | 140
[11 empty] | 1-FT36W/2G11-ELECTHO-46W | 1 | FT36W/2G11 | 1 | ELECTHO | Electronic High Output | 46 | BF~1.22
[11 empty] | 2-FT36W/2G11-ELECTHO-86W | 2 | FT36W/2G11 | 1 | ELECTHO | Electronic High Output | 86 | BF~1.20
Long Compact Fluorescent Twin - T5 (40W)
T5 (40 W - F40TT Lamp)
[11 empty] | 1-FT40W/2G11-MAG EE-43W | 1 | FT40W/2G11 | 1 | MAG EE | Magnetic Energy Efficient | 43
[11 empty] | 2-FT40W/2G11-MAG EE-86W | 2 | FT40W/2G11 | 1 | MAG EE | Magnetic Energy Efficient | 86
[11 empty] | 3-FT40W/2G11-MAG EE-129W | 3 | FT40W/2G11 | 1.5 | MAG EE | Magnetic Energy Efficient | 129
[11 empty] | 3-FT40W/2G11-MAG EE-130W | 3 | FT40W/2G11 | 2 | MAG EE | Magnetic Energy Efficient | 130
[11 empty] | 4-FT40W/2G11-MAG EE-172W | 4 | FT40W/2G11 | 2 | MAG EE | Magnetic Energy Efficient | 172
[11 empty] | T5 (40 W - Electronic Ballasts) | RO=ballast factor 70 to 85% NO = ballast factor 85 to 100% HO = ballast factor >100%
[11 empty] | 1-FT40W/2G11-ELECT NO-41W | 1 | FT40W/2G11 | 1 | ELECT NO | Electronic | 41 | BF~.90
[11 empty] | 2-FT40W/2G11-ELECT NO-78W | 2 | FT40W/2G11 | 1 | ELECT NO | Electronic | 78 | BF~.97
[11 empty] | 3-FT40W/2G11-ELECT NO-103W | 3 | FT40W/2G11 | 1 | ELECT NO | Electronic | 103 | BF~.86
[11 empty] | 1-FT40W/2G11-ELECT HO-50W | 1 | FT40W/2G11 | 1 | ELECT HO | Electronic High Output | 50 | BF~1.1
[11 empty] | 1-FT40W/2G11 -ELECT DIM-41W | 1 | FT40W/2G11 | 1 | ELECT DIM | Electronic Dimming | 41 | BF~1.0
[11 empty] | 2-FT40W/2G11 -ELECT DIM-80W | 2 | FT40W/2G11 | 1 | ELECT DIM | Electronic Dimming | 80 | BF~1.0
[11 empty] | 3-FT40W/2G11-ELECT-107W | 3 | FT40W/2G11 | 2 | ELECT | Electronic | 107
[11 empty] | 4-FT40W/2G11-ELECT-142W | 4 | FT40W/2G11 | 2 | ELECT | Electronic | 142
Long Compact Fluorescent Twin - T5 (50-55-80W)
[11 empty] | T5 (50 W - Electronic Ballasts) | RO=ballast factor 70 to 85% NO = ballast factor 85 to 100% HO = ballast factor >100%
[11 empty] | 1-FT50W/2G11-ELECT NO-54W | 1 | FT50W/2G11 | 1 | ELECT NO | Electronic Normal Output | 54 | BF~.98
[11 empty] | 2-FT50W/2G11-ELECT NO-106W | 2 | FT50W/2G11 | 1 | ELECT NO | Electronic Normal Output | 106 | BF~.98
[11 empty] | 3-FT50W/2G11-ELECT NO-98W | 3 | FT50W/2G11 | 1 | ELECT NO | Electronic Normal output | 98 | BF~.98
[11 empty] | 3-FT50W/2G11-ELECT-160W | 3 | FT50W/2G11 | 2 | ELECT | Electronic | 160
[11 empty] | 4-FT50W/2G11-ELECT-212W | 4 | FT50W/2G11 | 2 | ELECT | Electronic | 212
[11 empty] | 1-FT50W/2G11-ELECT HO-61W | 1 | FT50W/2G11 | 1 | ELECT HO | Electronic High Output | 61 | BF~1.12
[11 empty] | 2-FT50W/2G11-ELECT HO-115W | 2 | FT50W/2G11 | 1 | ELECT HO | Electronic High Output | 115 | BF~1.10
[11 empty] | 1-FT50W/2G11-ELECT DIM-51W | 1 | FT50W/2G11 | 1 | ELECT DIM | Electronic Dimming | 51
[11 empty] | 2-FT50W/2G11-ELECT DIM-92W | 2 | FT50W/2G11 | 1 | ELECT DIM | Electronic Dimming | 92
T5 (55 W - F55TT Lamp)
[11 empty] | 1-FT55W/2G11-ELECT NO-58W | 1 | FT55W/2G11 | 1 | ELECT NO | Electronic Normal Output | 58 | BF~.92
[11 empty] | 2-FT55W/2G11-ELECT NO-109W | 2 | FT55W/2G11 | 1 | ELECT NO | Electronic Normal Output | 109 | BF~.90
[11 empty] | 1-FT55W/2G11 -ELECT DIM-59W | 1 | FT55W/2G11 | 1 | ELECT DIM | Electronic Dimming | 59 | BF~.90
[11 empty] | 2-FT55W/2G11 -ELECT DIM-114W | 2 | FT55W/2G11 | 1 | ELECT DIM | Electronic Dimming | 114 | BF~.90
T5 (80 W – F80TT Lamp)
[11 empty] | 1-FT80W/2G11-ELECT NO-91W | 1 | FT80W/2G11 | 1 | ELECT NO | Electronic | 91 | BF~1.00
Fluorescent U-Tube - T8
2 ft. T8 (32W - FBO31T8 or F32T8/U/6 Lamp)
[11 empty] | 1-FB31T8/F32T8U-MAGNETIC-35W | 1 | FB31T8/F32T8U | 0.5 | MAGNETIC | Magnetic Energy Efficient | 35 | Tandem wired
[11 empty] | 1-FB31T8/F32T8U-MAGNETIC-36W | 1 | FB31T8/F32T8U | 1 | MAGNETIC | Magnetic Energy Efficient | 36
[11 empty] | 2-FB31T8/F32T8U-MAGNETIC-69W | 2 | FB31T8/F32T8U | 1 | MAGNETIC | Magnetic Energy Efficient | 69
[11 empty] | 3-FB31T8/F32T8U-MAGNETIC-104W | 3 | FB31T8/F32T8U | 1.5 | MAGNETIC | Magnetic Energy Efficient | 104 | Tandem wired
[11 empty] | 3-FB31T8/F32T8U-MAGNETIC-105W | 3 | FB31T8/F32T8U | 2 | MAGNETIC | Magnetic Energy Efficient | 105
[11 empty] | 1-FB31T8/F32T8U-ELECT NO-39W | 1 | FB31T8/F32T8U | 1 | ELECT NO | Electronic Normal Output | 39
[11 empty] | 2-FB31T8/F32T8U-ELECT NO-62W | 2 | FB31T8/F32T8U | 1 | ELECT NO | Electronic Normal Output | 62
[11 empty] | 3-FB31T8/F32T8U-ELECT NO-92W | 3 | FB31T8/F32T8U | 1 | ELECT NO | Electronic Normal Output | 92
[11 empty] | 4-FB31T8/F32T8U-ELECT NO-W | 4 | FB31T8/F32T8U | 1 | ELECT NO | Electronic Normal Output
[11 empty] | 1-FB31T8/F32T8U -ELECT DIM-33W | 1 | FB31T8/F32T8U | 1 | ELECT DIM | Electronic Dimming | 33 | BF~.88
[11 empty] | 2-FB31T8/F32T8U -ELECT DIM-64W | 2 | FB31T8/F32T8U | 1 | ELECT DIM | Electronic Dimming | 64 | BF~.88
[11 empty] | 3-FB31T8/F32T8U -ELECT DIM-93W | 3 | FB31T8/F32T8U | 1 | ELECT DIM | Electronic Dimming | 93 | BF~.88
[11 empty] | 4-FB31T8/F32T8U -ELECT DIM-116W | 4 | FB31T8/F32T8U | 1 | ELECT DIM | Electronic Dimming | 116 | BF~.88
[11 empty] | 2-FB31T8/F32T8U-ELECT IS-61W | 2 | FB31T8/F32T8U | 1 | ELECT IS | Electronic Instant Start | 61
[11 empty] | 3-FB31T8/F32T8U-ELECT IS-88W | 3 | FB31T8/F32T8U | 1 | ELECT IS | Electronic Instant Start | 88
Fluorescent U-Tube - T12
2 ft. T12 (“Energy Savings” 34W)
[11 empty] | 1-FB40T12/ES-MAGNETIC-36W | 1 | FB40T12/ES | 0.5 | MAGNETIC | Magnetic Energy Efficient | 36 | Tandem wired
[11 empty] | 1-FB40T12/ES-MAGNETIC-43W | 1 | FB40T12/ES | 1 | MAGNETIC | Magnetic Energy Efficient | 43
[11 empty] | 2-FB40T12/ES-MAGNETIC-72W | 2 | FB40T12/ES | 1 | MAGNETIC | Magnetic Energy Efficient | 72
[11 empty] | 3-FB40T12/ES-MAGNETIC-105W | 3 | FB40T12/ES | 1 | MAGNETIC | Magnetic Energy Efficient | 105
[11 empty] | 3-FB40T12/ES-MAGNETIC-108W | 3 | FB40T12/ES | 1.5 | MAGNETIC | Magnetic Energy Efficient | 108 | Tandem wired
[11 empty] | 3-FB40T12/ES-MAGNETIC-115W | 3 | FB40T12/ES | 2 | MAGNETIC | Magnetic Energy Efficient | 115
[11 empty] | 1-FB40T12/ES-ELECT-30W | 1 | FB40T12/ES | 0.5 | ELECT | Electronic | 30 | Tandem wired
[11 empty] | 1-FB40T12/ES-ELECT-31W | 1 | FB40T12/ES | 1 | ELECT | Electronic | 31
[11 empty] | 2-FB40T12/ES-ELECT-59W | 2 | FB40T12/ES | 1 | ELECT | Electronic | 59
[11 empty] | 3-FB40T12/ES-ELECT-90W | 3 | FB40T12/ES | 1 | ELECT | Electronic | 90
[11 empty] | 3-FB40T12/ES-ELECT-88W | 3 | FB40T12/ES | 1.5 | ELECT | Electronic | 88 | Tandem wired
[11 empty] | 3-FB40T12/ES-ELECT-90W | 3 | FB40T12/ES | 2 | ELECT | Electronic | 90
2 ft. T12 (“Standard” 40W)
[11 empty] | 1-FB40T12-MAGNETIC-43W | 1 | FB40T12 | 0.5 | MAGNETIC | Magnetic Energy Efficient | 43 | Tandem wired
[11 empty] | 1-FB40T12-MAGNETIC-48W | 1 | FB40T12 | 1 | MAGNETIC | Magnetic Energy Efficient | 48
[11 empty] | 2-FB40T12-MAGNETIC-86W | 2 | FB40T12 | 1 | MAGNETIC | Magnetic Energy Efficient | 86
[11 empty] | 3-FB40T12-MAGNETIC-127W | 3 | FB40T12 | 1 | MAGNETIC | Magnetic Energy Efficient | 127
[11 empty] | 3-FB40T12-MAGNETIC-129W | 3 | FB40T12 | 1.5 | MAGNETIC | Magnetic Energy Efficient | 129 | Tandem wired
[11 empty] | 3-FB40T12-MAGNETIC-134W | 3 | FB40T12 | 2 | MAGNETIC | Magnetic Energy Efficient | 134
[11 empty] | 1-FB40T12-ELECT-35W | 1 | FB40T12 | 0.5 | ELECT | Electronic | 35 | Tandem wired
[11 empty] | 1-FB40T12-ELECT-36W | 1 | FB40T12 | 1 | ELECT | Electronic | 36
[11 empty] | 2-FB40T12-ELECT-67W | 2 | FB40T12 | 1 | ELECT | Electronic | 67
[11 empty] | 3-FB40T12-ELECT-100W | 3 | FB40T12 | 1 | ELECT | Electronic | 100
[11 empty] | 3-FB40T12-ELECT-101W | 3 | FB40T12 | 1.5 | ELECT | Electronic | 101 | Tandem wired
[11 empty] | 3-FB40T12-ELECT-103W | 3 | FB40T12 | 2 | ELECT | Electronic | 103
Fluorescent Linear Lamps - Preheat
Fluorescent Preheat T5 (4W)
[11 empty] | 1-F4T5-MAG STD-8W | 1 | F4T5 | 1 | MAG STD | Magnetic Standard | 8 | 6" MOL
Fluorescent Preheat T5 (6W)
[11 empty] | 1-F6T5-MAG STD-10W | 1 | F6T5 | 1 | MAG STD | Magnetic Standard | 10 | 9" MOL
Fluorescent Preheat T5 (8W)
[11 empty] | 1-F8T5-MAG STD-12W | 1 | F8T5 | 1 | MAG STD | Magnetic Standard | 12 | 12" MOL
Fluorescent Preheat T8 (15W)
[11 empty] | 1-F15T8-MAG STD-19W | 1 | F15T8 | 1 | MAG STD | Magnetic Standard | 19 | 18" MOL
Fluorescent Preheat T12 (15W)
[11 empty] | 1-F15T12-MAG STD-19W | 1 | F15T12 | 1 | MAG STD | Magnetic Standard | 19 | 18" MOL
Fluorescent Preheat T12 (20W)
[11 empty] | 1-F20T12-MAG STD-25W | 1 | F20T12 | 1 | MAG STD | Magnetic Standard | 25 | 24" MOL
[11 empty] | 2-F20T12-MAG STD-50W | 2 | F20T12 | 1 | MAG STD | Magnetic Standard | 50 | 24" MOL
Fluorescent Preheat T8 (30W)
[11 empty] | 1-F30T8-MAG STD-46W | 1 | F30T8 | 1 | MAG STD | Magnetic Standard | 46 | 30" MOL
[11 empty] | 2-F30T8-MAG STD-79W | 2 | F30T8 | 1 | MAG STD | Magnetic Standard | 79 | 30" MOL
Fluorescent Preheat T12 (30W)
[11 empty] | 1-F30T12-MAG STD-46W | 1 | F30T12 | 1 | MAG STD | Magnetic Standard | 46 | 30" MOL
[11 empty] | 2-F30T12-MAG STD-79W | 2 | F30T12 | 1 | MAG STD | Magnetic Standard | 79 | 30" MOL
[11 empty] | 2-F30T12-MAGNETIC-74W | 2 | F30T12 | 1 | MAGNETIC | Magnetic Energy Efficient | 74 | 30" MOL
[11 empty] | 1-F30T12-ELECT-31W | 1 | F30T12 | 1 | ELECT | Electronic | 31 | 30" MOL
[11 empty] | 2-F30T12-ELECT-63W | 2 | F30T12 | 2 | ELECT | Electronic | 63 | 30" MOL
Fluorescent Linear Lamps T5
~23” Fluorescent Program Start T5 (14W)
[11 empty] | 1-F14T5-ELECT-18W | 1 | F14T5 | 1 | ELECT | Elect. Program Start | 18 | BF~1.0
[11 empty] | 2-F14T5-ELECT-34W | 2 | F14T5 | 1 | ELECT | Elect. Program Start | 34 | BF~1.0
~34.5” Fluorescent Program Start T5 (21W)
[11 empty] | 1-F21T5-ELECT-27W | 1 | F21T5 | 1 | ELECT | Elect. Program Start | 27 | BF~1.0
[11 empty] | 2-F21T5-ELECT-50W | 2 | F21T5 | 1 | ELECT | Elect. Program Start | 50 | BF~1.0
~46” Fluorescent Program Start T5 (28W)
[11 empty] | 1-F28T5-ELECT-30W | 1 | F28T5 | 1 | ELECT | Elect. Program Start | 30 | BF~1.0
[11 empty] | 2-F28T5-ELECT-60W | 2 | F28T5 | 1 | ELECT | Elect. Program Start | 60 | BF~1.0
~58.5” Fluorescent Program Start T5 (35W)
[11 empty] | 1-F35T5-ELECT-40W | 1 | F35T5 | 1 | ELECT | Elect. Program Start | 40 | BF~1.0
[11 empty] | 2-F35T5-ELECT-78W | 2 | F35T5 | 1 | ELECT | Elect. Program Start | 78 | BF~1.0
~23” Fluorescent Program Start T5 High Output (24W)
[11 empty] | 1-F24T5HO-ELECT-27W | 1 | F24T5HO | 1 | ELECT | Elect. Program Start | 27 | BF~1.0
[11 empty] | 2-F24T5HO-ELECT-52W | 2 | F24T5HO | 1 | ELECT | Elect. Program Start | 52 | BF~1.0
~34.5” Fluorescent Program Start T5 High Output(39W)
[11 empty] | 1-F39T5-ELECT-43W | 1 | F39T5 | 1 | ELECT | Elect. Program Start | 43 | BF~1.0
[11 empty] | 2-F39T5-ELECT-85W | 2 | F39T5 | 1 | ELECT | Elect. Program Start | 85 | BF~1.0
~46” Fluorescent Program Start T5 High Output (54W)
[11 empty] | 1-F54T5-ELECT-62W | 1 | F54T5 | 1 | ELECT | Elect. Program Start | 62 | BF~1.0
[11 empty] | 2-F54T5-ELECT-117W | 2 | F54T5 | 1 | ELECT | Elect. Program Start | 117 | BF~1.0
[11 empty] | 3-F54T5-ELECT-176W | 3 | F54T5 | 2 | ELECT | Elect. Program Start | 176 | BF~1.0
[11 empty] | 4-F54T5-ELECT-234W | 4 | F54T5 | 2 | ELECT | Elect. Program Start | 234 | BF~1.0
~57.5” Fluorescent Program Start T5 High Output (80W)
[11 empty] | 1-F80T5-ELECT-89W | 1 | F80T5 | 1 | ELECT | Elect. Program Start | 89 | BF~1
Fluorescent Rapid Start T8 - 2 foot
2 foot (17W)
[11 empty] | 1-F17T8-MAGNETIC-24W | 1 | F17T8 | 1 | MAGNETIC | Magnetic Energy Efficient. RS | 24
[11 empty] | 2-F17T8-MAGNETIC-45W | 2 | F17T8 | 1 | MAGNETIC | Magnetic Energy Efficient. RS | 45
[11 empty] | 2 foot (Electronic Ballasts) | RO=ballast factor 70 to 85% NO = ballast factor 85 to 100% HO = ballast factor >100%
[11 empty] | 1-F17T8-ELECT NO-22W | 1 | F17T8 | 1 | ELECT NO | Electronic Normal Output. RS | 22
[11 empty] | 2-F17T8-ELECT NO-33W | 2 | F17T8 | 1 | ELECT NO | Electronic Normal Output. RS | 33
[11 empty] | 3-F17T8-ELECT NO-53W | 3 | F17T8 | 1 | ELECT NO | Electronic Normal Output. RS | 53
[11 empty] | 3-F17T8-ELECT NO-55W | 3 | F17T8 | 2 | ELECT NO | Electronic Normal Output. RS | 55
[11 empty] | 4-F17T8-ELECT NO-63W | 4 | F17T8 | 1 | ELECT NO | Electronic Normal Output | 63
[11 empty] | 1-F17T8-ELECT DIM-20W | 1 | F17T8 | 1 | ELECT DIM | Electronic Dimming. RS | 20 | BF~.88
[11 empty] | 2-F17T8-ELECT DIM-37W | 2 | F17T8 | 1 | ELECT DIM | Electronic Dimming. RS | 37 | BF~.88
[11 empty] | 3-F17T8-ELECT DIM-56W | 3 | F17T8 | 1 | ELECT DIM | Electronic Dimming. RS | 56 | BF~.88
[11 empty] | 4-F17T8-ELECT DIM-69W | 4 | F17T8 | 1 | ELECT DIM | Electronic Dimming. RS | 69 | BF~.88
Fluorescent Rapid Start T8 - 3 foot
3 foot (25W)
[11 empty] | 1-F25T8-MAGNETIC-33W | 1 | F25T8 | 1 | MAGNETIC | Magnetic Energy Efficient. RS | 33
[11 empty] | 2-F25T8-MAGNETIC-65W | 2 | F25T8 | 1 | MAGNETIC | Magnetic Energy Efficient. RS | 65
[11 empty] | 3 foot (Electronic Ballasts) | RO=ballast factor 70 to 85% NO = ballast factor 85 to 100% HO = ballast factor >100% EE = efficient electronic
[11 empty] | 1-F25T8-ELECT NO-27W | 1 | F25T8 | 1 | ELECT NO | Electronic Normal Output. RS | 27
[11 empty] | 2-F25T8-ELECT NO-48W | 2 | F25T8 | 1 | ELECT NO | Electronic Normal Output. RS | 48
[11 empty] | 3-F25T8-ELECT NO-68W | 3 | F25T8 | 1 | ELECT NO | Electronic Normal Output. RS | 68
[11 empty] | 4-F25T8-ELECT NO-89W | 4 | F25T8 | 1 | ELECT NO | Electronic Normal Output. RS | 89
[11 empty] | 1-F25T8-ELECT RO-24W | 1 | F25T8 | 1 | ELECT RO | Electronic Reduced Output. RS | 24 | BF~.82
[11 empty] | 2-F25T8-ELECT RO-41W | 2 | F25T8 | 1 | ELECT RO | Electronic Reduced Output. RS | 41 | BF~.78
[11 empty] | 3-F25T8-ELECT RO-59W | 3 | F25T8 | 1 | ELECT RO | Electronic Reduced Output. RS | 59 | BF~.77
[11 empty] | 4-F25T8-ELECT RO-77W | 4 | F25T8 | 1 | ELECT RO | Electronic Reduced Output. RS | 77 | BF~.76
[11 empty] | 1-F25T8-ELECT HO-29W | 1 | F25T8 | 1 | ELECT HO | Electronic High Output. RS | 29 | BF~1.05
[11 empty] | 2-F25T8-ELECT HO-51W | 2 | F25T8 | 1 | ELECT HO | Electronic High Output. RS | 51 | BF~1.05
[11 empty] | 3-F25T8-ELECT HO-74W | 3 | F25T8 | 1 | ELECT HO | Electronic High Output. RS | 74 | BF~1.05
[11 empty] | 1-F25T8-ELECT DIM-25W | 1 | F25T8 | 1 | ELECT DIM | Electronic Dimming. RS | 25 | BF~.94
[11 empty] | 2-F25T8-ELECT DIM-49W | 2 | F25T8 | 1 | ELECT DIM | Electronic Dimming. RS | 49 | BF~.94
[11 empty] | 3-F25T8-ELECT DIM-76W | 3 | F25T8 | 1 | ELECT DIM | Electronic Dimming. RS | 76 | BF~.94
[11 empty] | 4-F25T8-ELECT DIM-96W | 4 | F25T8 | 1 | ELECT DIM | Electronic Dimming. RS | 96 | BF~.88
3 foot (“Energy Saving” 25W)
[11 empty] | 1-F25T8ES-ELECT NO-27W | 1 | F25T8ES | 1 | ELECT NO | Electronic Normal Output. RS | 27
[11 empty] | 2-F25T8ES-ELECT NO-52W | 2 | F25T8ES | 1 | ELECT NO | Electronic Normal Output. RS | 52
[11 empty] | 3-F25T8ES-ELECT NO-77W | 3 | F25T8ES | 1 | ELECT NO | Electronic Normal Output. RS | 77
[11 empty] | 4-F25T8ES-ELECT NO-95W | 4 | F25T8ES | 1 | ELECT NO | Electronic Normal Output. RS | 95
Fluorescent T8 - 4 foot
4 foot Instant Start (“Energy Saving” 30W)
[11 empty] | 1-F32T8/30ES-ELECT NO-29W | 1 | F32T8/30ES | 1 | ELECT NO | Electronic Normal Output. IS | 29
[11 empty] | 2-F32T8/30ES-ELECT NO-54W | 2 | F32T8/30ES | 1 | ELECT NO | Electronic Normal Output. IS | 54
[11 empty] | 3-F32T8/30ES-ELECT NO-79W | 3 | F32T8/30ES | 1 | ELECT NO | Electronic Normal Output. IS | 79
[11 empty] | 4-F32T8/30ES-ELECT NO-104W | 4 | F32T8/30ES | 1 | ELECT NO | Electronic Normal Output. IS | 104
[11 empty] | 1-F32T8/30ES-ELECT RO-27W | 1 | F32T8/30ES | 1 | ELECT RO | Electronic Reduced Output. IS | 27 | BF~.75
[11 empty] | 2-F32T8/30ES-ELECT RO-48W | 2 | F32T8/30ES | 1 | ELECT RO | Electronic Reduced Output. IS | 48 | BF~.75
[11 empty] | 3-F32T8/30ES-ELECT RO-70W | 3 | F32T8/30ES | 1 | ELECT RO | Electronic Reduced Output. IS | 70 | BF~.75
[11 empty] | 4-F32T8/30ES-ELECT RO-91W | 4 | F32T8/30ES | 1 | ELECT RO | Electronic Reduced Output. IS | 91 | BF~.75
[11 empty] | 1-F32T8/30ES-ELECT NO EE-33W | 1 | F32T8/30ES | 1 | ELECT NO EE | EE Normal Output. IS | 33
[11 empty] | 2-F32T8/30ES-ELECT NO EE-52W | 2 | F32T8/30ES | 1 | ELECT NO EE | EE Normal Output. IS | 52
[11 empty] | 3-F32T8/30ES-ELECT NO EE-77W | 3 | F32T8/30ES | 1 | ELECT NO EE | EE Normal Output. IS | 77
[11 empty] | 4-F32T8/30ES-ELECT NO EE-101W | 4 | F32T8/30ES | 1 | ELECT NO EE | EE Normal Output. IS | 101
[11 empty] | 1-F32T8/30ES-ELECT RO EE-28W | 1 | F32T8/30ES | 1 | ELECT RO EE | EE Reduced Output. IS | 28 | BF~.78
[11 empty] | 2-F32T8/30ES-ELECT RO EE-45W | 2 | F32T8/30ES | 1 | ELECT RO EE | EE Reduced Output. IS | 45 | BF~.78
[11 empty] | 3-F32T8/30ES-ELECT RO EE-66W | 3 | F32T8/30ES | 1 | ELECT RO EE | EE Reduced Output. IS | 66 | BF~.78
[11 empty] | 4-F32T8/30ES-ELECT RO EE-88W | 4 | F32T8/30ES | 1 | ELECT RO EE | EE Reduced Output. IS | 88 | BF~.78
4 foot Rapid Start (32W)
[11 empty] | 1-F32T8-MAGNETIC-35W | 1 | F32T8 | 0.5 | MAGNETIC | Magnetic Energy Efficient. RS | 35 | Tandem wired
[11 empty] | 1-F32T8-MAGNETIC-39W | 1 | F32T8 | 1 | MAGNETIC | Magnetic Energy Efficient. RS | 39
[11 empty] | 2-F32T8-MAGNETIC-70W | 2 | F32T8 | 1 | MAGNETIC | Magnetic Energy Efficient. RS | 70
[11 empty] | 3-F32T8-MAGNETIC-105W | 3 | F32T8 | 1.5 | MAGNETIC | Magnetic Energy Efficient. RS | 105 | Tandem wired
[11 empty] | 3-F32T8-MAGNETIC-109W | 3 | F32T8 | 2 | MAGNETIC | Magnetic Energy Efficient. RS | 109
[11 empty] | 4-F32T8-MAGNETIC-140W | 4 | F32T8 | 2 | MAGNETIC | Magnetic Energy Efficient. RS | 140 | (2) Two-lamp ballasts
[11 empty] | 4 foot Rapid Start (32W - Electronic Ballasts) | RO=ballast factor 70 to 85% NO = ballast factor 85 to 100% HO = ballast factor >100% EE = efficient electronic
[11 empty] | 1-F32T8-ELECT NO-31W | 1 | F32T8 | 0.5 | ELECT NO | Electronic Normal Output. RS | 31
[11 empty] | 1-F32T8-ELECT NO-32W | 1 | F32T8 | 1 | ELECT NO | Electronic Normal Output. RS | 32
[11 empty] | 2-F32T8-ELECT NO-62W | 2 | F32T8 | 1 | ELECT NO | Electronic Normal Output. RS | 62
[11 empty] | 3-F32T8-ELECT NO-93W | 3 | F32T8 | 1 | ELECT NO | Electronic Normal Output. RS | 93
[11 empty] | 3-F32T8-ELECT NO-93W | 3 | F32T8 | 1.5 | ELECT NO | Electronic Normal Output. RS | 93 | Tandem wired
[11 empty] | 4-F32T8-ELECT NO-114W | 4 | F32T8 | 1 | ELECT NO | Electronic Normal Output. RS | 114
[11 empty] | 1-F32T8-EE NO -35W | 1 | F32T8 | 1 | EE NO | EE Normal Output. RS | 35
[11 empty] | 2-F32T8-EE NO-55W | 2 | F32T8 | 1 | EE NO | EE Normal Output. RS | 55
[11 empty] | 3-F32T8-EE NO-82W | 3 | F32T8 | 1 | EE NO | EE Normal Output. RS | 82
[11 empty] | 4-F32T8-EE NO-107W | 4 | F32T8 | 1 | EE NO | EE Normal Output. RS | 107
[11 empty] | 1-F32T8-ELECT RO-29W | 1 | F32T8 | 1 | ELECT RO | Electronic Reduced Output. RS | 29 | BF~.75
[11 empty] | 2-F32T8-ELECT RO-51W | 2 | F32T8 | 1 | ELECT RO | Electronic Reduced Output. RS | 51 | BF~.75
[11 empty] | 3-F32T8-ELECT RO-76W | 3 | F32T8 | 1 | ELECT RO | Electronic Reduced Output. RS | 76 | BF~.75
[11 empty] | 4-F32T8-ELECT RO-100W | 4 | F32T8 | 1 | ELECT RO | Electronic Reduced Output. RS | 100 | BF~.75
[11 empty] | 2-F32T8-ELECT HO-77W | 2 | F32T8 | 1 | ELECT HO | Electronic High Output. RS | 77 | BF~1.13
[11 empty] | 3-F32T8-ELECT HO-112W | 3 | F32T8 | 1 | ELECT HO | Electronic High Output. RS | 112 | BF~1.18
[11 empty] | 1-F32T8-EE RO-30W | 1 | F32T8 | 1 | EE RO | EE Reduced Output. RS | 30 | BF~.74
[11 empty] | 2-F32T8-EE RO-48W | 2 | F32T8 | 1 | EE RO | EE Reduced Output. RS | 48 | BF~.74
[11 empty] | 3-F32T8-EE RO-73W | 3 | F32T8 | 1 | EE RO | EE Reduced Output. RS | 73 | BF~.74
[11 empty] | 4-F32T8-EE RO-96W | 4 | F32T8 | 1 | EE RO | EE Reduced Output. RS | 96 | BF~.74
[11 empty] | 2-F32T8-ELECT TL-65W | 2 | F32T8 | 1 | ELECT TL | Electronic Two Level (50 & 100%). RS | 65
[11 empty] | 3-F32T8-ELECT TL-98W | 3 | F32T8 | 1.5 | ELECT TL | Electronic Two Level (50 & 100%). RS | 98 | Tandem wired
[11 empty] | 4-F32T8-ELECT TL-130W | 4 | F32T8 | 2 | ELECT TL | Electronic Two Level (50 & 100%). RS | 130 | (2) Two-lamp ballasts
[11 empty] | 1-F32T8-ELECT DIM-35W | 1 | F32T8 | 1 | ELECT DIM | Electronic Dimming. RS | 35 | BF~1.0
[11 empty] | 2-F32T8-ELECT DIM-68W | 2 | F32T8 | 1 | ELECT DIM | Electronic Dimming. RS | 68 | BF~1.0
[11 empty] | 3-F32T8-ELECT DIM-102W | 3 | F32T8 | 1 | ELECT DIM | Electronic Dimming. RS | 102 | BF~1.0
[11 empty] | 4-F32T8-ELECT DIM-116W | 4 | F32T8 | 1 | ELECT DIM | Electronic Dimming. RS | 116 | BF~.88
[11 empty] | 1-F40T8-MAGNETIC-50W | 1 | F40T8 | 1 | MAGNETIC | Magnetic Energy Efficient. RS | 50
[11 empty] | 2-F40T8-MAGNETIC-92W | 2 | F40T8 | 1 | MAGNETIC | Magnetic Energy Efficient. RS | 92
[11 empty] | 1-F40T8-ELECT-46W | 1 | F40T8 | 1 | ELECT | Electronic. RS | 46
[11 empty] | 2-F40T8-ELECT-79W | 2 | F40T8 | 1 | ELECT | Electronic. RS | 79
[11 empty] | 3-F40T8-ELECT-112W | 3 | F40T8 | 1 | ELECT | Electronic. RS | 112
Fluorescent Rapid Start T12 - 3 foot
3 foot (“Energy-Saving” 25W)
[11 empty] | 1-F30T12/ES-MAG STD-42W | 1 | F30T12/ES | 1 | MAG STD | Magnetic Standard. RS | 42
[11 empty] | 2-F30T12/ES-MAG STD-74W | 2 | F30T12/ES | 1 | MAG STD | Magnetic Standard. RS | 74
[11 empty] | 3-F30T12/ES-MAG STD-111W | 3 | F30T12/ES | 1.5 | MAG STD | Magnetic Standard. RS | 111 | Tandem wired
[11 empty] | 3-F30T12/ES-MAG STD-116W | 3 | F30T12/ES | 2 | MAG STD | Magnetic Standard. RS | 116
[11 empty] | 2-F30T12/ES-MAGNETIC-66W | 2 | F30T12/ES | 1 | MAGNETIC | Magnetic Energy Efficient. RS | 66
[11 empty] | 1-F30T12/ES-ELECT-26W | 1 | F30T12/ES | 1 | ELECT | Electronic. RS | 26
[11 empty] | 2-F30T12/ES-ELECT-53W | 2 | F30T12/ES | 1 | ELECT | Electronic. RS | 53
3 foot (“Standard” 30W)
[11 empty] | 1-F30T12-MAG STD-46W | 1 | F30T12 | 1 | MAG STD | Magnetic Standard. RS | 46
[11 empty] | 2-F30T12-MAG STD-79W | 2 | F30T12 | 1 | MAG STD | Magnetic Standard. RS | 79
[11 empty] | 3-F30T12-MAG STD-118W | 3 | F30T12 | 1.5 | MAG STD | Magnetic Standard. RS | 118 | Tandem wired
[11 empty] | 3-F30T12-MAG STD-125W | 3 | F30T12 | 2 | MAG STD | Magnetic Standard. RS | 125
[11 empty] | 2-F30T12-MAGNETIC-73W | 2 | F30T12 | 1 | MAGNETIC | Magnetic Energy Efficient. RS | 73
[11 empty] | 1-F30T12-ELECT-30W | 1 | F30T12 | 1 | ELECT | Electronic. RS | 30
[11 empty] | 2-F30T12-ELECT-60W | 2 | F30T12 | 1 | ELECT | Electronic. RS | 60
Fluorescent Rapid Start T12 - 4 foot (32 to 34 W)
4 foot (“Energy-Saving Plus”32W)
[11 empty] | 1-F40T12/ES Plus-MAGNETIC-34W | 1 | F40T12/ES Plus | 0.5 | MAGNETIC | Magnetic Energy Efficient. RS | 34 | Tandem wired
[11 empty] | 1-F40T12/ES Plus-MAGNETIC-41W | 1 | F40T12/ES Plus | 1 | MAGNETIC | Magnetic Energy Efficient. RS | 41
[11 empty] | 2-F40T12/ES Plus-MAGNETIC-68W | 2 | F40T12/ES Plus | 1 | MAGNETIC | Magnetic Energy Efficient. RS | 68
[11 empty] | 3-F40T12/ES Plus-MAGNETIC-99W | 3 | F40T12/ES Plus | 1 | MAGNETIC | Magnetic Energy Efficient. RS | 99
[11 empty] | 3-F40T12/ES Plus-MAGNETIC-102W | 3 | F40T12/ES Plus | 1.5 | MAGNETIC | Magnetic Energy Efficient. RS | 102 | Tandem wired
[11 empty] | 3-F40T12/ES Plus-MAGNETIC-109W | 3 | F40T12/ES Plus | 2 | MAGNETIC | Magnetic Energy Efficient. RS | 109
[11 empty] | 4-F40T12/ES Plus-MAGNETIC-136W | 4 | F40T12/ES Plus | 2 | MAGNETIC | Magnetic Energy Efficient. RS | 136 | (2) Two-lamp ballasts
4 foot (“Energy-Saving”34W)
[11 empty] | 1-F40T12/ES-MAG STD-42W | 1 | F40T12/ES | 0.5 | MAG STD | Magnetic Standard. RS | 42 | Tandem wired
[11 empty] | 1-F40T12/ES-MAG STD-48W | 1 | F40T12/ES | 1 | MAG STD | Magnetic Standard.RS | 48
[11 empty] | 2-F40T12/ES-MAG STD-82W | 2 | F40T12/ES | 1 | MAG STD | Magnetic Standard.RS | 82
[11 empty] | 3-F40T12/ES-MAG STD-122W | 3 | F40T12/ES | 1.5 | MAG STD | Magnetic Standard.RS | 122 | Tandem wired
[11 empty] | 3-F40T12/ES-MAG STD-130W | 3 | F40T12/ES | 2 | MAG STD | Magnetic Standard.RS | 130
[11 empty] | 4-F40T12/ES-MAG STD-164W | 4 | F40T12/ES | 2 | MAG STD | Magnetic Standard.RS | 164 | (2) Two-lamp ballasts
[11 empty] | 1-F40T12/ES-MAGNETIC-36W | 1 | F40T12/ES | 0.5 | MAGNETIC | Magnetic Energy Efficient. RS | 36 | Tandem wired
[11 empty] | 1-F40T12/ES-MAGNETIC-43W | 1 | F40T12/ES | 1 | MAGNETIC | Magnetic Energy Efficient. RS | 43
[11 empty] | 2-F40T12/ES-MAGNETIC-72W | 2 | F40T12/ES | 1 | MAGNETIC | Magnetic Energy Efficient. RS | 72
[11 empty] | 3-F40T12/ES-MAGNETIC-105W | 3 | F40T12/ES | 1 | MAGNETIC | Magnetic Energy Efficient. RS | 105
[11 empty] | 3-F40T12/ES-MAGNETIC-108W | 3 | F40T12/ES | 1.5 | MAGNETIC | Magnetic Energy Efficient. RS | 108 | Tandem wired
[11 empty] | 3-F40T12/ES-MAGNETIC-112W | 3 | F40T12/ES | 2 | MAGNETIC | Magnetic Energy Efficient. RS | 112
[11 empty] | 4-F40T12/ES-MAGNETIC-144W | 4 | F40T12/ES | 2 | MAGNETIC | Magnetic Energy Efficient. RS | 144 | (2) Two-lamp ballasts
[11 empty] | 2-F40T12/ES-MAG HC-58W | 2 | F40T12/ES | 1 | MAG HC | Magnetic Heater Cutout. RS | 58
[11 empty] | 3-F40T12/ES-MAG HC-87W | 3 | F40T12/ES | 1.5 | MAG HC | Magnetic Heater Cutout. RS | 87 | Tandem wired
[11 empty] | 4-F40T12/ES-MAG HC-116W | 4 | F40T12/ES | 2 | MAG HC | Magnetic Heater Cutout. RS | 116 | (2) Two-lamp ballasts
[11 empty] | 2-F40T12/ES-MAG HC FO-66W | 2 | F40T12/ES | 1 | MAG HC FO | Mag. Heater Cutout Full Light. RS | 66
[11 empty] | 3-F40T12/ES-MAG HC FO-99W | 3 | F40T12/ES | 1.5 | MAG HC FO | Mag. Heater Cutout Full Light. RS | 99 | Tandem wired
[11 empty] | 4-F40T12/ES-MAG HC FO-132W | 4 | F40T12/ES | 2 | MAG HC FO | Mag. Heater Cutout Full Light. RS | 132 | (2) Two-lamp ballasts
[11 empty] | 1-F40T12/ES-ELECT-30W | 1 | F40T12/ES | 0.5 | ELECT | Electronic. RS | 30 | Tandem wired
[11 empty] | 1-F40T12/ES-ELECT-31W | 1 | F40T12/ES | 1 | ELECT | Electronic. RS | 31
[11 empty] | 2-F40T12/ES-ELECT-62W | 2 | F40T12/ES | 1 | ELECT | Electronic. RS | 62
[11 empty] | 3-F40T12/ES-ELECT-90W | 3 | F40T12/ES | 1 | ELECT | Electronic. RS | 90
[11 empty] | 3-F40T12/ES-ELECT-93W | 3 | F40T12/ES | 1.5 | ELECT | Electronic. RS | 93 | Tandem wired
[11 empty] | 3-F40T12/ES-ELECT-93W | 3 | F40T12/ES | 2 | ELECT | Electronic. RS | 93
[11 empty] | 4-F40T12/ES-ELECT-121W | 4 | F40T12/ES | 1 | ELECT | Electronic. RS | 121
[11 empty] | 4-F40T12/ES-ELECT-124W | 4 | F40T12/ES | 2 | ELECT | Electronic. RS | 124 | (2) Two-lamp ballasts
[11 empty] | 2-F40T12/ES-ELECT AO-60W | 2 | F40T12/ES | 1 | ELECT AO | Elec. Adjustable Output (to 15%). RS | 60
[11 empty] | 3-F40T12/ES-ELECT AO-90W | 3 | F40T12/ES | 1.5 | ELECT AO | Elec. Adjustable Output (to 15%). RS | 90 | Tandem wired
[11 empty] | 4-F40T12/ES-ELECT AO-120W | 4 | F40T12/ES | 2 | ELECT AO | Elec. Adjustable Output (to 15%). RS | 120 | (2) Two-lamp ballasts
Fluorescent Rapid Start T12 - 4 foot (40 W)
4 foot Standard (40W)
[11 empty] | 1-F40T12-MAG STD-26W | 1 | F40T12 | 0.5 | MAG STD | Magnetic Standard. RS | 26 | Tandem wired
[11 empty] | 1-F40T12-MAG STD-52W | 1 | F40T12 | 1 | MAG STD | Magnetic Standard. RS | 52
[11 empty] | 2-F40T12-MAG STD-96W | 2 | F40T12 | 1 | MAG STD | Magnetic Standard. RS | 96
[11 empty] | 3-F40T12-MAG STD-144W | 3 | F40T12 | 1.5 | MAG STD | Magnetic Standard. RS | 144 | Tandem wired
[11 empty] | 3-F40T12-MAG STD-148W | 3 | F40T12 | 2 | MAG STD | Magnetic Standard. RS | 148
[11 empty] | 4-F40T12-MAG STD-192W | 4 | F40T12 | 2 | MAG STD | Magnetic Standard. RS | 192 | (2) Two-lamp ballasts
[11 empty] | 1-F40T12-MAGNETIC-44W | 1 | F40T12 | 0.5 | MAGNETIC | Magnetic Energy Efficient. RS | 44 | Tandem wired
[11 empty] | 1-F40T12-MAGNETIC-46W | 1 | F40T12 | 1 | MAGNETIC | Magnetic Energy Efficient. RS | 46
[11 empty] | 2-F40T12-MAGNETIC-88W | 2 | F40T12 | 1 | MAGNETIC | Magnetic Energy Efficient. RS | 88
[11 empty] | 3-F40T12-MAGNETIC-127W | 3 | F40T12 | 1 | MAGNETIC | Magnetic Energy Efficient. RS | 127
[11 empty] | 3-F40T12-MAGNETIC-132W | 3 | F40T12 | 1.5 | MAGNETIC | Magnetic Energy Efficient. RS | 132 | Tandem wired
[11 empty] | 3-F40T12-MAGNETIC-134W | 3 | F40T12 | 2 | MAGNETIC | Magnetic Energy Efficient. RS | 134
[11 empty] | 4-F40T12-MAGNETIC-176W | 4 | F40T12 | 2 | MAGNETIC | Magnetic Energy Efficient. RS | 176 | (2) Two-lamp ballasts
[11 empty] | 2-F40T12-MAG HC-71W | 2 | F40T12 | 1 | MAG HC | Magnetic Heater Cutout. RS | 71
[11 empty] | 3-F40T12-MAG HC-107W | 3 | F40T12 | 1.5 | MAG HC | Magnetic Heater Cutout. RS | 107 | Tandem wired
[11 empty] | 4-F40T12-MAG HC-142W | 4 | F40T12 | 2 | MAG HC | Magnetic Heater Cutout. RS | 142 | (2) Two-lamp ballasts
[11 empty] | 2-F40T12-MAG HC FO-80W | 2 | F40T12 | 1 | MAG HC FO | Magnetic Heater Cutout Full Light. RS | 80
[11 empty] | 3-F40T12-MAG HC FO-120W | 3 | F40T12 | 1.5 | MAG HC FO | Magnetic Heater Cutout Full Light. RS | 120 | Tandem wired
[11 empty] | 4-F40T12-MAG HC FO-160W | 4 | F40T12 | 2 | MAG HC FO | Magnetic Heater Cutout Full Light. RS | 160 | (2) Two-lamp ballasts
[11 empty] | 1-F40T12-ELECT-36W | 1 | F40T12 | 0.5 | ELECT | Electronic. RS | 36 | Tandem wired
[11 empty] | 1-F40T12-ELECT-37W | 1 | F40T12 | 1 | ELECT | Electronic. RS | 37
[11 empty] | 2-F40T12-ELECT-72W | 2 | F40T12 | 1 | ELECT | Electronic. RS | 72
[11 empty] | 3-F40T12-ELECT-107W | 3 | F40T12 | 1 | ELECT | Electronic. RS | 107
[11 empty] | 3-F40T12-ELECT-108W | 3 | F40T12 | 1.5 | ELECT | Electronic. RS | 108 | Tandem wired
[11 empty] | 3-F40T12-ELECT-109W | 3 | F40T12 | 2 | ELECT | Electronic. RS | 109
[11 empty] | 4-F40T12-ELECT-135W | 4 | F40T12 | 1 | ELECT | Electronic. RS | 135
[11 empty] | 4-F40T12-ELECT-144W | 4 | F40T12 | 2 | ELECT | Electronic. RS | 144 | (2) Two-lamp ballasts
[11 empty] | 2-F40T12-ELECT RO-61W | 2 | F40T12 | 1 | ELECT RO | Electronic Reduce Output (75%). RS | 61
[11 empty] | 3-F40T12-ELECT RO-90W | 3 | F40T12 | 1 | ELECT RO | Electronic Reduce Output (75%). RS | 90
[11 empty] | 3-F40T12-ELECT RO-92W | 3 | F40T12 | 1.5 | ELECT RO | Electronic Reduce Output (75%). RS | 92 | Tandem wired
[11 empty] | 4-F40T12-ELECT RO-122W | 4 | F40T12 | 2 | ELECT RO | Electronic Reduce Output (75%). RS | 122 | (2) Two-lamp ballasts
[11 empty] | 2-F40T12-ELECT TL-69W | 2 | F40T12 | 1 | ELECT TL | Elec. Two Level (50 & 100%). RS | 69
[11 empty] | 3-F40T12-ELECT TL-104W | 3 | F40T12 | 1.5 | ELECT TL | Elec. Two Level (50 & 100%). RS | 104 | Tandem wired
[11 empty] | 4-F40T12-ELECT TL-138W | 4 | F40T12 | 2 | ELECT TL | Elec. Two Level (50 & 100%). RS | 138 | (2) Two-lamp ballasts
[11 empty] | 2-F40T12-ELECT AO-73W | 2 | F40T12 | 1 | ELECT AO | Elec. Adjustable Output (to 15%). RS | 73
[11 empty] | 3-F40T12-ELECT AO-110W | 3 | F40T12 | 1.5 | ELECT AO | Elec. Adjustable Output (to 15%). RS | 110 | Tandem wired
[11 empty] | 4-F40T12-ELECT AO-146W | 4 | F40T12 | 2 | ELECT AO | Elec. Adjustable Output (to 15%). RS | 146 | (2) Two-lamp ballasts
[11 empty] | 2-F40T12-ELECT DIM-83W | 2 | F40T12 | 1 | ELECT DIM | Electronic Dimming (to 1%). RS | 83
[11 empty] | 3-F40T12-ELECT DIM-125W | 3 | F40T12 | 1.5 | ELECT DIM | Electronic Dimming (to 1%). RS | 125 | Tandem wired
[11 empty] | 4-F40T12-ELECT DIM-166W | 4 | F40T12 | 2 | ELECT DIM | Electronic Dimming (to 1%). RS | 166 | (2) Two-lamp ballasts
Fluorescent Rapid Start T10 - 4 foot (42W)
Extended Output (42W)
[11 empty] | 2-F40T10/EO-MAGNETIC-92W | 2 | F40T10/EO | 1 | MAGNETIC | Magnetic Energy Efficient. RS | 92
[11 empty] | 3-F40T10/EO-MAGNETIC-138W | 3 | F40T10/EO | 1.5 | MAGNETIC | Magnetic Energy Efficient. RS | 138 | Tandem wired
[11 empty] | 4-F40T10/EO-MAGNETIC-184W | 4 | F40T10/EO | 2 | MAGNETIC | Magnetic Energy Efficient. RS | 184 | (2) Two-lamp ballasts
[11 empty] | 2-F40T10/EO-MAG HC-74W | 2 | F40T10/EO | 1 | MAG HC | Magnetic Heater Cutout. RS | 74
[11 empty] | 3-F40T10/EO-MAG HC-111W | 3 | F40T10/EO | 1.5 | MAG HC | Magnetic Heater Cutout. RS | 111 | Tandem wired
[11 empty] | 4-F40T10/EO-MAG HC-148W | 4 | F40T10/EO | 2 | MAG HC | Magnetic Heater Cutout. RS | 148 | (2) Two-lamp ballasts
[11 empty] | 2-F40T10/EO-ELECT-74W | 2 | F40T10/EO | 1 | ELECT | Electronic. RS | 74
[11 empty] | 3-F40T10/EO-ELECT-111W | 3 | F40T10/EO | 1.5 | ELECT | Electronic. RS | 111 | Tandem wired
[11 empty] | 4-F40T10/EO-ELECT-148W | 4 | F40T10/EO | 2 | ELECT | Electronic. RS | 148 | (2) Two-lamp ballasts
[11 empty] | 2-F40T10/EO-ELECT RO-63W | 2 | F40T10/EO | 1 | ELECT RO | Electronic Reduce Output (75%). RS | 63
[11 empty] | 3-F40T10/EO-ELECT RO-95W | 3 | F40T10/EO | 1.5 | ELECT RO | Electronic Reduce Output (75%). RS | 95 | Tandem wired
[11 empty] | 4-F40T10/EO-ELECT RO-126W | 4 | F40T10/EO | 2 | ELECT RO | Electronic Reduce Output (75%). RS | 126 | (2) Two-lamp ballasts
[11 empty] | 2-F40T10/EO-ELECT TL-72W | 2 | F40T10/EO | 1 | ELECT TL | Elec. Two Level (50 & 100%). RS | 72
[11 empty] | 3-F40T10/EO-ELECT TL-108W | 3 | F40T10/EO | 1.5 | ELECT TL | Elec. Two Level (50 & 100%). RS | 108 | Tandem wired
[11 empty] | 4-F40T10/EO-ELECT TL-144W | 4 | F40T10/EO | 2 | ELECT TL | Elec. Two Level (50 & 100%). RS | 144 | (2) Two-lamp ballasts
[11 empty] | 2-F40T10/EO-ELECT AO-73W | 2 | F40T10/EO | 1 | ELECT AO | Elec. Adjustable Output (to 15%). RS | 73
[11 empty] | 3-F40T10/EO-ELECT AO-110W | 3 | F40T10/EO | 1.5 | ELECT AO | Elec. Adjustable Output (to 15%). RS | 110 | Tandem wired
[11 empty] | 4-F40T10/EO-ELECT AO-146W | 4 | F40T10/EO | 2 | ELECT AO | Elec. Adjustable Output (to 15%). RS | 146 | (2) Two-lamp ballasts
[11 empty] | 2-F40T10/EO-ELECT DIM-85W | 2 | F40T10/EO | 1 | ELECT DIM | Electronic Dimming (to 1%). RS | 85
[11 empty] | 3-F40T10/EO-ELECT DIM-128W | 3 | F40T10/EO | 1.5 | ELECT DIM | Electronic Dimming (to 1%). RS | 128 | Tandem wired
[11 empty] | 4-F40T10/EO-ELECT DIM-170W | 4 | F40T10/EO | 2 | ELECT DIM | Electronic Dimming (to 1%). RS | 170 | (2) Two-lamp ballasts
Fluorescent Rapid Start High Output T8 & T12 - 8 ft
8 foot T8 High Output (86W)
[11 empty] | 1-F96T8/HO-ELECT-88W | 1 | F96T8/HO | 1 | ELECT | Electronic. RS | 88
[11 empty] | 2-F96T8/HO-ELECT-160W | 2 | F96T8/HO | 1 | ELECT | Electronic. RS | 160
8 foot T12 High Output (“Energy-Saving” 95W)
[11 empty] | 1-F96T12/HO/ES-MAG STD -125W | 1 | F96T12/HO/ES | 1 | MAG STD | Magnetic Standard. RS | 125
[11 empty] | 2-F96T12/HO/ES-MAG STD-227W | 2 | F96T12/HO/ES | 1 | MAG STD | Magnetic Standard. RS | 227
[11 empty] | 2-F96T12/HO/ES-MAGNETIC-208W | 2 | F96T12/HO/ES | 1 | MAGNETIC | Magnetic Energy Efficient. RS | 208
[11 empty] | 2-F96T12/HO/ES-ELECT-170W | 2 | F96T12/HO/ES | 1 | ELECT | Electronic. RS | 170
8 foot T12 High Output (“Standard” 110W)
[11 empty] | 1-F96T12/HO-MAG STD -140W | 1 | F96T12/HO | 1 | MAG STD | Magnetic Standard. RS | 140
[11 empty] | 2-F96T12/HO-MAG STD-252W | 2 | F96T12/HO | 1 | MAG STD | Magnetic Standard. RS | 252
[11 empty] | 2-F96T12/HO-MAGNETIC-237W | 2 | F96T12/HO | 1 | MAGNETIC | Magnetic Energy Efficient. RS | 237
[11 empty] | 1-F96T12/HO-ELECT-119W | 1 | F96T12/HO | 1 | ELECT | Electronic. RS | 119
[11 empty] | 2-F96T12/HO-ELECT-205W | 2 | F96T12/HO | 1 | ELECT | Electronic. RS | 205
8 foot T12 Very High Output (“Energy-Saving” 195W)
[11 empty] | 1-F96T12/VHO/ES-MAG STD-200W | 1 | F96T12/VHO/ES | 1 | MAG STD | Magnetic Standard. RS | 200
[11 empty] | 2-F96T12/VHO/ES-MAG STD-325W | 2 | F96T12/VHO/ES | 1 | MAG STD | Magnetic Standard. RS | 325
8 foot T12 Very High Output (“Standard” 215W)
[11 empty] | 1-F96T12/VHO-MAG STD-230W | 1 | F96T12/VHO | 1 | MAG STD | Magnetic Standard. RS | 230
[11 empty] | 2-F96T12/VHO-MAG STD-440W | 2 | F96T12/VHO | 1 | MAG STD | Magnetic Standard. RS | 440
Fluorescent Instant Start (single pin base "Slimline") T8 & T12
4 foot Fluorescent Slimline Energy-Saving T12 (32W)
[11 empty] | 1-F48T12/ES-MAG STD-51W | 1 | F48T12/ES | 1 | MAG STD | Magnetic Standard. IS | 51
[11 empty] | 2-F48T12/ES-MAG STD-82W | 2 | F48T12/ES | 1 | MAG STD | Magnetic Standard. IS | 82
4 foot Fluorescent Slimline Standard T12 (39W)
[11 empty] | 1-F48T12-MAG STD-59W | 1 | F48T12 | 1 | MAG STD | Magnetic Standard. IS | 59
[11 empty] | 2-F48T12-MAG STD-98W | 2 | F48T12 | 1 | MAG STD | Magnetic Standard. IS | 98
8 foot Fluorescent T8 Slimline (59W)
[11 empty] | 1-F96T8-MAGNETIC-58W | 1 | F96T8 | 1 | MAGNETIC | Magnetic Standard. IS | 58
[11 empty] | 2-F96T8-MAGNETIC-120W | 2 | F96T8 | 1 | MAGNETIC | Magnetic Standard. IS | 120
[11 empty] | 2-F96T8-ELECT NO-110W | 2 | F96T8 | 1 | ELECT NO | Electronic Normal Output. IS | 110
[11 empty] | 1-F96T8-ELECT HO-72W | 1 | F96T8 | 1 | ELECT HO | Electronic High Output. IS | 72 | BF~1.10
[11 empty] | 2-F96T8-ELECT HO-151W | 2 | F96T8 | 1 | ELECT HO | Electronic High Output. IS | 151 | BF~1.20
8 foot Fluorescent T12 Slimline (“Energy-Saving” 60W)
[11 empty] | 1-F96T12/ES-MAG STD -74W | 1 | F96T12/ES | 1 | MAG STD | Magnetic Standard. IS | 74
[11 empty] | 2-F96T12/ES-MAG STD-131W | 2 | F96T12/ES | 1 | MAG STD | Magnetic Standard. IS | 131
[11 empty] | 2-F96T12/ES-MAGNETIC-112W | 2 | F96T12/ES | 1 | MAGNETIC | Magnetic Energy Efficient. IS | 112
[11 empty] | 1-F96T12/ES-ELECT-70W | 1 | F96T12/ES | 1 | ELECT | Electronic. IS | 70
[11 empty] | 2-F96T12/ES-ELECT-107W | 2 | F96T12/ES | 1 | ELECT | Electronic. IS | 107
8 foot Fluorescent T12 Slimline (“Standard” 75W)
[11 empty] | 1-F96T12-MAG STD -92W | 1 | F96T12 | 1 | MAG STD | Magnetic Standard. IS | 92
[11 empty] | 2-F96T12-MAG STD-158W | 2 | F96T12 | 1 | MAG STD | Magnetic Standard. IS | 158
[11 empty] | 2-F96T12-MAGNETIC-144W | 2 | F96T12 | 1 | MAGNETIC | Magnetic Energy Efficient. IS | 144
[11 empty] | 1-F96T12-ELECT-85W | 1 | F96T12 | 1 | ELECT | Electronic. IS | 85
[11 empty] | 2-F96T12-ELECT-132W | 2 | F96T12 | 1 | ELECT | Electronic. IS | 132
High Intensity Discharge - Mercury Vapor
[11 empty] | 1-H40-MAG STD-51W | 1 | H40 | 1 | MAG STD | Magnetic Standard | 51
[11 empty] | 1-H50-MAG STD-63W | 1 | H50 | 1 | MAG STD | Magnetic Standard | 63
[11 empty] | 1-H75-MAG STD-88W | 1 | H75 | 1 | MAG STD | Magnetic Standard | 88
[11 empty] | 1-H100-MAG STD-119W | 1 | H100 | 1 | MAG STD | Magnetic Standard | 119
[11 empty] | 1-H175-MAG STD-197W | 1 | H175 | 1 | MAG STD | Magnetic Standard | 197
[11 empty] | 1-H250-MAG STD-285W | 1 | H250 | 1 | MAG STD | Magnetic Standard | 285
[11 empty] | 1-H400-MAG STD-450W | 1 | H400 | 1 | MAG STD | Magnetic Standard | 450
[11 empty] | 1-H1000-MAG STD-1080W | 1 | H1000 | 1 | MAG STD | Magnetic Standard | 1080
High Intensity Discharge - Metal Halide
[11 empty] | 1-M32-MAG STD-42W | 1 | M32 | 1 | MAG STD | Magnetic Standard | 42
[11 empty] | 1-M35/39-MAG STD-48W | 1 | M35/39 | 1 | MAG STD | Magnetic Standard | 48
[11 empty] | 1-M35/39-ELECT-44W | 1 | M35/39 | 1 | ELECT | Electronic | 44
[11 empty] | 1-M50-MAG STD-68W | 1 | M50 | 1 | MAG STD | Magnetic Standard | 68
[11 empty] | 1-M50-ELECT-58W | 1 | M50 | 1 | ELECT | Electronic | 58
[11 empty] | 1-M70-MAG STD-92W | 1 | M70 | 1 | MAG STD | Magnetic Standard | 92
[11 empty] | 1-M70-ELECT-86W | 1 | M70 | 1 | ELECT | Electronic | 86
[11 empty] | 1-M100-MAG STD-122W | 1 | M100 | 1 | MAG STD | Magnetic Standard | 122
[11 empty] | 1-M100-ELECT-110W | 1 | M100 | 1 | ELECT | Electronic | 110
[11 empty] | 1-M125-MAG STD-150W | 1 | M125 | 1 | MAG STD | Magnetic Standard | 150
[11 empty] | 1-M150-MAG STD-186W | 1 | M150 | 1 | MAG STD | Magnetic Standard | 186
[11 empty] | 1-M150-ELECT-168W | 1 | M150 | 1 | ELECT | Electronic | 168
[11 empty] | 1-M175-MAG STD-205W | 1 | M175 | 1 | MAG STD | Magnetic Standard | 205
[11 empty] | 1-M200-MAG STD-232W | 1 | M200 | 1 | MAG STD | Magnetic Standard | 232
[11 empty] | 1-M225-MAG STD-258W | 1 | M225 | 1 | MAG STD | Magnetic Standard | 258
[11 empty] | 1-M250-MAG STD-295W | 1 | M250 | 1 | MAG STD | Magnetic Standard | 295
[11 empty] | 1-M320-MAG STD-365W | 1 | M320 | 1 | MAG STD | Magnetic Standard | 365
[11 empty] | 1-M320-MAG LR-345W | 1 | M320 | 1 | MAG LR | 277v Linear Reactor | 345
[11 empty] | 1-M320-ELECT-345W | 1 | M320 | 1 | ELECT | Electronic | 345
[11 empty] | 2-M320-ELECT DIM-679W | 2 | M320 | 1 | ELECT DIM | Electronic Dimming | 679 | Dimming to 50%
[11 empty] | 1-M350-ELECT-375W | 1 | M350 | 1 | ELECT | Electronic | 375
[11 empty] | 2-M350-ELECT DIM-740W | 2 | M350 | 1 | ELECT DIM | Electronic Dimming | 740 | Dimming to 50%
[11 empty] | 1-M360-MAG STD-422W | 1 | M360 | 1 | MAG STD | Magnetic Standard | 422
[11 empty] | 1-M360-MAG LR-388W | 1 | M360 | 1 | MAG LR | 277v Linear Reactor | 388
[11 empty] | 1-M400-MAG STD-461W | 1 | M400 | 1 | MAG STD | Magnetic Standard | 461
[11 empty] | 1-M400-MAG LR-426W | 1 | M400 | 1 | MAG LR | 277v Linear Reactor | 426
[11 empty] | 1-M400-ELECT-430W | 1 | M400 | 1 | ELECT | Electronic | 430
[11 empty] | 2-M400-ELECT DIM-843W | 2 | M400 | 1 | ELECT DIM | Electronic Dimming | 843 | Dimming to 50%
[11 empty] | 1-M450-MAG STD-502W | 1 | M450 | 1 | MAG STD | Magnetic Standard | 502
[11 empty] | 1-M450-MAG LR-478W | 1 | M450 | 1 | MAG LR | 277v Linear Reactor | 478
[11 empty] | 1-M750-MAG STD-820W | 1 | M750 | 1 | MAG STD | Magnetic Standard | 820
[11 empty] | 1-M900-MAG STD-990W | 1 | M900 | 1 | MAG STD | Magnetic Standard | 990
[11 empty] | 1-M1000-MAG STD-1080W | 1 | M1000 | 1 | MAG STD | Magnetic Standard | 1080
[11 empty] | 2-M1000-ELECT-2100W | 2 | M1000 | 1 | ELECT | Electronic | 2100 | 277 Volt
[11 empty] | 1-M1500-MAG STD-1650W | 1 | M1500 | 1 | MAG STD | Magnetic Standard | 1650
[11 empty] | 1-M1650-MAG STD-1810W | 1 | M1650 | 1 | MAG STD | Magnetic Standard | 1810
High Intensity Discharge - High Pressure Sodium
[11 empty] | 1-S35-MAG STD-44W | 1 | S35 | 1 | MAG STD | Magnetic Standard | 44
[11 empty] | 1-S50-MAG STD-61W | 1 | S50 | 1 | MAG STD | Magnetic Standard | 61
[11 empty] | 1-S70-MAG STD-93W | 1 | S70 | 1 | MAG STD | Magnetic Standard | 93
[11 empty] | 1-S70-ELECT DIM-81W | 1 | S70 | 1 | ELECT DIM | Electronic Dimming | 81
[11 empty] | 1-S100-MAG STD-116W | 1 | S100 | 1 | MAG STD | Magnetic Standard | 116
[11 empty] | 1-S100-ELECT DIM-114W | 1 | S100 | 1 | ELECT DIM | Electronic Dimming | 114
[11 empty] | 1-S150-MAG STD-173W | 1 | S150 | 1 | MAG STD | Magnetic Standard | 173
[11 empty] | 1-S150-ELECT DIM-166W | 1 | S150 | 1 | ELECT DIM | Electronic Dimming | 166
[11 empty] | 1-S200-MAG STD-240W | 1 | S200 | 1 | MAG STD | Magnetic Standard | 240
[11 empty] | 1-S250-MAG STD-302W | 1 | S250 | 1 | MAG STD | Magnetic Standard | 302
[11 empty] | 1-S250-ELECT DIM-285W | 1 | S250 | 1 | ELECT DIM | Electronic Dimming | 285
[11 empty] | 1-S400-MAG STD-469W | 1 | S400 | 1 | MAG STD | Magnetic Standard | 469
[11 empty] | 1-S400-ELECT DIM-435W | 1 | S400 | 1 | ELECT DIM | Electronic Dimming | 435
[11 empty] | 1-S1000-MAG STD-1090W | 1 | S1000 | 1 | MAG STD | Magnetic Standard | 1090
High Intensity Discharge - Low Pressure Sodium
[11 empty] | 1-LPS18-MAG STD-30W | 1 | LPS18 | 1 | MAG STD | Magnetic Standard | 30
[11 empty] | 1-LPS35-MAG STD-60W | 1 | LPS35 | 1 | MAG STD | Magnetic Standard | 60
[11 empty] | 1-LPS55-MAG STD-80W | 1 | LPS55 | 1 | MAG STD | Magnetic Standard | 80
[11 empty] | 1-LPS90-MAG STD-125W | 1 | LPS90 | 1 | MAG STD | Magnetic Standard | 125
[11 empty] | 1-LPS135-MAG STD-178W | 1 | LPS135 | 1 | MAG STD | Magnetic Standard | 178
[11 empty] | 1-LPS180-MAG STD-220W | 1 | LPS180 | 1 | MAG STD | Magnetic Standard | 220
[11 empty] | 12 Volt Tungsten Halogen Lamps | Including MR16, Bi-pin, AR70, AR111, PAR36
[11 empty] | 1-20 watt lamp-EPS-23W | 1 | 20 watt lamp | 1 | EPS | Electronic Power Supply | 23
[11 empty] | 1-25 watt lamp-EPS-28W | 1 | 25 watt lamp | 1 | EPS | Electronic Power Supply | 28
[11 empty] | 1-35 watt lamp-EPS-38W | 1 | 35 watt lamp | 1 | EPS | Electronic Power Supply | 38
[11 empty] | 1-37 watt lamp-EPS-41W | 1 | 37 watt lamp | 1 | EPS | Electronic Power Supply | 41
[11 empty] | 1-42 watt lamp-EPS-45W | 1 | 42 watt lamp | 1 | EPS | Electronic Power Supply | 45
[11 empty] | 1-50 watt lamp-EPS-54W | 1 | 50 watt lamp | 1 | EPS | Electronic Power Supply | 54
[11 empty] | 1-65 watt lamp-EPS-69W | 1 | 65 watt lamp | 1 | EPS | Electronic Power Supply | 69
[11 empty] | 1-71 watt lamp-EPS-75W | 1 | 71 watt lamp | 1 | EPS | Electronic Power Supply | 75
[11 empty] | 1-75 watt lamp-EPS-80W | 1 | 75 watt lamp | 1 | EPS | Electronic Power Supply | 80
[11 empty] | 1-100 watt lamp-EPS-106W | 1 | 100 watt lamp | 1 | EPS | Electronic Power Supply | 106
[11 empty] | 1-20 watt lamp-MT-24W | 1 | 20 watt lamp | 1 | MT | Magnetic Transformer | 24
[11 empty] | 1-25 watt lamp-MT-29W | 1 | 25 watt lamp | 1 | MT | Magnetic Transformer | 29
[11 empty] | 1-35 watt lamp-MT-39W | 1 | 35 watt lamp | 1 | MT | Magnetic Transformer | 39
[11 empty] | 1-37 watt lamp-MT-42W | 1 | 37 watt lamp | 1 | MT | Magnetic Transformer | 42
[11 empty] | 1-42 watt lamp-MT-46W | 1 | 42 watt lamp | 1 | MT | Magnetic Transformer | 46
[11 empty] | 1-50 watt lamp-MT-55W | 1 | 50 watt lamp | 1 | MT | Magnetic Transformer | 55
[11 empty] | 1-65 watt lamp-MT-70W | 1 | 65 watt lamp | 1 | MT | Magnetic Transformer | 70
[11 empty] | 1-71 watt lamp-MT-76W | 1 | 71 watt lamp | 1 | MT | Magnetic Transformer | 76
[11 empty] | 1-75 watt lamp-MT-81W | 1 | 75 watt lamp | 1 | MT | Magnetic Transformer | 81
[11 empty] | 1-100 watt lamp-MT-108W | 1 | 100 watt lamp | 1 | MT | Magnetic Transformer | 108
[11 empty] | Track Lighting | N/A | N/A | N/A | N/A | N/A | 37.5
[11 empty] | User Defined | N/A | N/A | N/A | N/A | N/A
Note on Q361: Tianzhen Hong: corrected. T8 not T12

## Worksheet 5b-1
Worksheet 5b-1 | Project Name: | [6 empty] | Page:
INTERIOR LIGHTING POWER | [13 empty] | TABLE 13-H — SPACE-BY-SPACE METHOD MAXIMUM ALLOWABLE LIGHTING POWER DENSITY (LPD)
|  | Space-by-Space Method Only Skip to column (f) if using the Tenant Space Method |  |  |  | (f) Lum ID from Worksheet 5a Column (a) | [8 empty] | Common Space Types | LPD (W/ft2)
| (a) | (b) | (c) | (d) | (e) |  | (g) | (h) | (i) | (j) | (k) | [6 empty] | 0
| Room ID (do not leave any blanks) | Area (ft2) | Space Type (Table 13-H) (enter space type only once per room) | Space Type LPD | Lighting Power Budget (b) x (d) |  | Quantity of Luminaires (or lineal ft. for track lighting) | Luminaire Power (Watts) | Exempt Fixtures | Lighting Power (g) x (h) | Room Total Ltg. Power |  |  |  | Active Storage | 0.8
|  |  |  | -- | -- |  |  | 0 |  | 0 | 0 | FALSE | 2 | FALSE | Active Storage - Hospitals | 0.9 | FALSE | 5
|  |  |  | -- | -- |  |  | 0 |  | 0 | -- | FALSE | 3 | FALSE | Air/Train/Bus – Baggage Area | 1 | FALSE | 49
|  |  |  | -- | -- |  |  | 0 |  | 0 | -- | FALSE | 6 | FALSE | Airport - Concourse | 0.6 | FALSE | 5
|  |  |  | -- | -- |  |  | 0 |  | 0 | -- | FALSE | 1 | FALSE | Atrium-each additional floors | 0.2 | FALSE | 6
|  |  |  | -- | -- |  |  | 0 |  | 0 | -- | FALSE | 1 | FALSE | Atrium-first three floors | 0.6 | FALSE | 3
|  |  |  | -- | -- |  |  | 0 |  | 0 | -- | FALSE | 1 | FALSE | Audience/Seating Area | 0.9 | FALSE | 1
|  |  |  | -- | -- |  |  | 0 |  | 0 | -- | FALSE | 1 | FALSE | Audience/Seating Area - Convention Center | 0.7 | FALSE | 29
|  |  |  | -- | -- |  |  | 0 |  | 0 | -- | FALSE | 1 | FALSE | Audience/Seating Area - Exercise Center | 0.3 | FALSE | 1
|  |  |  | -- | -- |  |  | 0 |  | 0 | -- | FALSE | 1 | FALSE | Audience/Seating Area - Gymnasium | 0.4 | FALSE | 1
|  |  |  | -- | -- |  |  | 0 |  | 0 | -- | FALSE | 1 | FALSE | Audience/Seating Area - Motion Picture Theater | 1.2 | FALSE | 42
|  |  |  | -- | -- |  |  | 0 |  | 0 | -- | FALSE | 1 | FALSE | Audience/Seating Area -Performing Arts Theater | 2.6 | FALSE | 1
|  |  |  | -- | -- |  |  | 0 |  | 0 | -- | FALSE | 1 | FALSE | Audience/Seating Area -Religious Buildings | 1.7 | FALSE | 1
|  |  |  | -- | -- |  |  | 0 |  | 0 | -- | FALSE | 1 | FALSE | Audience/Seating Area -Sports Arenas | 0.4 | FALSE | 1
|  |  |  | -- | -- |  |  | 0 |  | 0 | -- | FALSE | 1 | FALSE | Audience/Seating Area -Transportation | 0.5 | FALSE | 1
|  |  |  | -- | -- |  |  | 0 |  | 0 | -- | FALSE | 1 | FALSE | Automotive – Service/Repair | 0.7 | FALSE | 1
|  |  |  | -- | -- |  |  | 0 |  | 0 | -- | FALSE | 1 | FALSE | Bank/Office – Banking Activity Area | 1.5 | FALSE | 1
|  |  |  | -- | -- |  |  | 0 |  | 0 | -- | FALSE | 1 | FALSE | Classroom/Lecture/Training | 1.4 | FALSE | 1
|  |  |  | -- | -- |  |  | 0 |  | 0 | -- | FALSE | 1 | FALSE | Conference/Meeting/Multipurpose | 1.3 | FALSE | 1
|  |  |  | -- | -- |  |  | 0 |  | 0 | -- | FALSE | 1 | FALSE | Convention Center – Exhibit Space | 1.3 | FALSE | 1
|  |  |  | -- | -- |  |  | 0 |  | 0 | -- | FALSE | 1 | FALSE | Corridor/Transition | 0.5 | FALSE | 1
|  |  |  | -- | -- |  |  | 0 |  | 0 | -- | FALSE | 1 | FALSE | Corridor/Transition - Hospital | 1 | FALSE | 1
|  |  |  | -- | -- |  |  | 0 |  | 0 | -- | FALSE | 1 | FALSE | Corridor/Transition - Manufacturing Facility | 0.5 | FALSE | 2
|  |  |  | -- | -- |  |  | 0 |  | 0 | -- | FALSE | 1 | FALSE | Courthouse/Police Station - Courtroom | 1.9 | FALSE | 1
|  |  |  | -- | -- |  |  | 0 |  | 0 | -- | FALSE | 1 | FALSE | Courthouse/Police Station - Judges Chambers | 1.3 | FALSE | 1
|  |  |  | -- | -- |  |  | 0 |  | 0 | -- | FALSE | 1 | FALSE | Dining Area - Bar Lounge/Leisure Dining | 1.4 | FALSE | 1
|  |  |  | -- | -- |  |  | 0 |  | 0 | -- | FALSE | 1 | FALSE | Dining Area - Family Dining | 2.1 | FALSE | 1
|  |  |  | -- | -- |  |  | 0 |  | 0 | -- | FALSE | 1 | FALSE | Dining Area - Hotel/Motel | 1.3 | FALSE | 1
|  |  |  | -- | -- |  |  | 0 |  | 0 | -- | FALSE | 1 | FALSE | Dressing/Locker/Fitting Room | 0.6 | FALSE | 1
|  |  |  | -- | -- |  |  | 0 |  | 0 | -- | FALSE | 1 | FALSE | Electrical/Mechanical | 1.5 | FALSE | 1
|  |  |  | -- | -- |  |  | 0 |  | 0 | -- | FALSE | 1 | FALSE | Fire Station - Engine Room | 0.8 | FALSE | 1
|  |  |  | -- | -- |  |  | 0 |  | 0 | -- | FALSE | 1 | FALSE | Fire Stations - Sleeping Quarters | 0.3 | FALSE | 1
|  |  |  | -- | -- |  |  | 0 |  | 0 | -- | FALSE | 1 | FALSE | Food Preparation | 1.2 | FALSE | 1
|  |  |  | -- | -- |  |  | 0 |  | 0 | -- | FALSE | 1 | FALSE | Gymnasium/Exercise Center - Exercise Area | 0.9 | FALSE | 1
|  |  |  | -- | -- |  |  | 0 |  | 0 | -- | FALSE | 1 | FALSE | Gymnasium/Exercise Center - Playing Area | 1.4 | FALSE | 1
|  |  |  | -- | -- |  |  | 0 |  | 0 | -- | FALSE | 1 | FALSE | Hospital - Emergency | 2.7 | FALSE | 1
|  |  |  | -- | -- |  |  | 0 |  | 0 | -- | FALSE | 1 | FALSE | Hospital - Exam/Treatment | 1.5 | FALSE | 2
|  |  |  | -- | -- |  |  | 0 |  | 0 | -- | FALSE | 1 | FALSE | Hospital - Laundry-Washing | 0.6 | FALSE | 1
|  |  |  | -- | -- |  |  | 0 |  | 0 | -- | FALSE | 1 | FALSE | Hospital - Medical Supply | 1.4 | FALSE | 1
|  |  |  | -- | -- |  |  | 0 |  | 0 | -- | FALSE | 1 | FALSE | Hospital - Nurse Station | 1 | FALSE | 1
|  |  |  | -- | -- |  |  | 0 |  | 0 | -- | FALSE | 1 | FALSE | Hospital - Nursery | 0.6 | FALSE | 1
|  |  |  | -- | -- |  |  | 0 |  | 0 | -- | FALSE | 1 | FALSE | Hospital - Operating Room | 2.2 | FALSE | 1
|  |  |  | -- | -- |  |  | 0 |  | 0 | -- | FALSE | 1 | FALSE | Hospital - Patient Room | 0.7 | FALSE | 1
|  | 0 | Worksheet 5b-1 Total Budget |  | 0 |  |  |  |  | Wksht 5b-1 Total Lighting Power (excluding exempt/track fixtures) | 0 |  |  |  | Hospital - Pharmacy | 1.2
[15 empty] | Hospital - Physical Therapy | 0.9
| Total Number of Additional Worksheet 5b | [13 empty] | Hospital - Radiology | 0.4
[15 empty] | Hospital - Recovery | 0.8
|  | Worksheet Number |  |  | (l) Lighting Power Budget: Space-by-Space only (Total of column (e)) |  | (m) Proposed Buiding Lighting Power (Total of column (k), excluding exempt/track) |  | (n) Area Sqft. (not required for Tenant Method) | [5 empty] | Inactive Storage | 0.3
|  |  |  | 5b-1 | 0 |  | 0 |  | 0 | [5 empty] | Inactive Storage - Museum | 0.8 |  | 0
|  |  |  | 5b-2 | [10 empty] | Laboratory | 1.4 |  | 1
|  |  |  | 5b-3 | [10 empty] | Library - Card File & Cataloging | 1.1 |  | 2
|  |  |  | Sum of additional 5b worksheets | [10 empty] | Library - Reading Area | 1.2 |  | 3
|  | Total Budget (of all worksheets) |  |  | 0 |  | 0 |  | 0 | [5 empty] | Library -Stacks | 1.7 |  | 4
[15 empty] | Lobby - General | 1.3 |  | 5
5-5 | [14 empty] | Lobby - Hotel | 1.1 |  | 6
[15 empty] | Lobby - Motion Picture Theater | 1.1 |  | 7
[15 empty] | Lobby - Performing Arts Theater | 3.3 |  | 8
[15 empty] | Lounge/Recreation | 1.2 |  | 9
[15 empty] | Lounge/Recreation - Hospital | 0.8 |  | 10
[15 empty] | Museum - General Exhibition | 1 |  | 11
[15 empty] | Museum -Restoration | 1.7 |  | 12
[15 empty] | Office-enclosed | 1.1 |  | 13
[15 empty] | Office-open plan | 1.1 |  | 14
[15 empty] | Post Office-Sorting Area | 1.2 |  | 15
[15 empty] | Religious Buildings - Worship-pulpit, choir | 2.4 |  | 16
[15 empty] | Religious Buildings Fellowship Hall | 0.9 |  | 17
[15 empty] | Restrooms | 0.9 |  | 18
[15 empty] | Retail - Grocery Sales Area | 2 |  | 19
[15 empty] | Retail - Jewelry & Art Sales Area | 3.5 |  | 20
[15 empty] | Retail - Mall Concourse | 1.5
[15 empty] | Retail - Other Merchandise Sales Area | 2
[15 empty] | Sports Arena -Court Sports Area | 2.3
[15 empty] | Sports Arena -Indoor Plying Field Area | 1.4
[15 empty] | Sports Arena -Ring Sports Area | 2.7
[15 empty] | Stairs-active | 0.6
[15 empty] | Transportation Terminal – Ticket Counter | 1.5
[15 empty] | Warehouse - Fine Material Storage | 1.4
[15 empty] | Warehouse - Medium/Bulky Material Storage | 0.9
[15 empty] | Workshop | 1.9
For track lighting enter lineal feet in column column (g) .
Column (k), enter sum of column (j) for each room only once at first entry for the room . See example in instructions.
Other Pages
List the additional worksheets nece-ssary to catalog all luminaires in building
Each room must be identified.
Describe luminaires for each individual room in plans.

## Worksheet 5b (hidden)
Worksheet 5b-2 | Project Name: | [6 empty] | Page:
INTERIOR LIGHTING POWER | [13 empty] | TABLE 13-H — SPACE-BY-SPACE METHOD MAXIMUM ALLOWABLE LIGHTING POWER DENSITY (LPD)
|  | Space-by-Space Method Only Skip to column (f) if using the Tenant Space Method |  |  |  | (f) Lum ID from Worksheet 5a Column (a) | [8 empty] | Common Space Types | LPD (W/ft2)
| (a) | (b) | (c) | (d) | (e) |  | (g) | (h) | (i) | (j) | (k) | [6 empty] | 0
| Room ID (do not leave any blanks) | Area (ft2) | Space Type (Table 13-H) (enter space type only once per room) | Space Type LPD | Lighting Power Budget (b) x (d) |  | Quantity of Luminaires (or lineal ft. for track lighting) | Luminaire Power (Watts) | Exempt Fixtures | Lighting Power (g) x (h) | Room Total Ltg. Power |  |  |  | Active Storage | 0.8
|  |  |  | -- | -- |  |  | 0 |  | 0 | 0 | FALSE | 1 | FALSE | Active Storage - Hospitals | 0.9 | FALSE | 5
|  |  |  | -- | -- |  |  | 0 |  | 0 | -- | FALSE | 1 | FALSE | Air/Train/Bus – Baggage Area | 1 | FALSE | 49
|  |  |  | -- | -- |  |  | 0 |  | 0 | -- | FALSE | 1 | FALSE | Airport - Concourse | 0.6 | FALSE | 5
|  |  |  | -- | -- |  |  | 0 |  | 0 | -- | FALSE | 1 | FALSE | Atrium-each additional floors | 0.2 | FALSE | 6
|  |  |  | -- | -- |  |  | 0 |  | 0 | -- | FALSE | 1 | FALSE | Atrium-first three floors | 0.6 | FALSE | 3
|  |  |  | -- | -- |  |  | 0 |  | 0 | -- | FALSE | 1 | FALSE | Audience/Seating Area | 0.9 | FALSE | 1
|  |  |  | -- | -- |  |  | 0 |  | 0 | -- | FALSE | 1 |  | Audience/Seating Area - Convention Center | 0.7 | FALSE | 29
|  |  |  | -- | -- |  |  | 0 |  | 0 | -- | FALSE | 1 |  | Audience/Seating Area - Exercise Center | 0.3 | FALSE | 1
|  |  |  | -- | -- |  |  | 0 |  | 0 | -- | FALSE | 1 |  | Audience/Seating Area - Gymnasium | 0.4 | FALSE | 1
|  |  |  | -- | -- |  |  | 0 |  | 0 | -- | FALSE | 1 |  | Audience/Seating Area - Motion Picture Theater | 1.2 | FALSE | 42
|  |  |  | -- | -- |  |  | 0 |  | 0 | -- | FALSE | 1 |  | Audience/Seating Area -Performing Arts Theater | 2.6 | FALSE | 1
|  |  |  | -- | -- |  |  | 0 |  | 0 | -- | FALSE | 1 |  | Audience/Seating Area -Religious Buildings | 1.7 | FALSE | 1
|  |  |  | -- | -- |  |  | 0 |  | 0 | -- | FALSE | 1 |  | Audience/Seating Area -Sports Arenas | 0.4 | FALSE | 1
|  |  |  | -- | -- |  |  | 0 |  | 0 | -- | FALSE | 1 |  | Audience/Seating Area -Transportation | 0.5 | FALSE | 1
|  |  |  | -- | -- |  |  | 0 |  | 0 | -- | FALSE | 1 |  | Automotive – Service/Repair | 0.7 | FALSE | 1
|  |  |  | -- | -- |  |  | 0 |  | 0 | -- | FALSE | 1 |  | Bank/Office – Banking Activity Area | 1.5 | FALSE | 1
|  |  |  | -- | -- |  |  | 0 |  | 0 | -- | FALSE | 1 |  | Classroom/Lecture/Training | 1.4 | FALSE | 1
|  |  |  | -- | -- |  |  | 0 |  | 0 | -- | FALSE | 1 |  | Conference/Meeting/Multipurpose | 1.3 | FALSE | 1
|  |  |  | -- | -- |  |  | 0 |  | 0 | -- | FALSE | 1 |  | Convention Center – Exhibit Space | 1.3 | FALSE | 1
|  |  |  | -- | -- |  |  | 0 |  | 0 | -- | FALSE | 1 |  | Corridor/Transition | 0.5 | FALSE | 1
|  |  |  | -- | -- |  |  | 0 |  | 0 | -- | FALSE | 1 |  | Corridor/Transition - Hospital | 1 | FALSE | 1
|  |  |  | -- | -- |  |  | 0 |  | 0 | -- | FALSE | 1 |  | Corridor/Transition - Manufacturing Facility | 0.5 | FALSE | 2
|  |  |  | -- | -- |  |  | 0 |  | 0 | -- | FALSE | 1 |  | Courthouse/Police Station - Courtroom | 1.9 | FALSE | 1
|  |  |  | -- | -- |  |  | 0 |  | 0 | -- | FALSE | 1 |  | Courthouse/Police Station - Judges Chambers | 1.3 | FALSE | 1
|  |  |  | -- | -- |  |  | 0 |  | 0 | -- | FALSE | 1 |  | Dining Area - Bar Lounge/Leisure Dining | 1.4 | FALSE | 1
|  |  |  | -- | -- |  |  | 0 |  | 0 | -- | FALSE | 1 |  | Dining Area - Family Dining | 2.1 | FALSE | 1
|  |  |  | -- | -- |  |  | 0 |  | 0 | -- | FALSE | 1 |  | Dining Area - Hotel/Motel | 1.3 | FALSE | 1
|  |  |  | -- | -- |  |  | 0 |  | 0 | -- | FALSE | 1 |  | Dressing/Locker/Fitting Room | 0.6 | FALSE | 1
|  |  |  | -- | -- |  |  | 0 |  | 0 | -- | FALSE | 1 |  | Electrical/Mechanical | 1.5 | FALSE | 1
|  |  |  | -- | -- |  |  | 0 |  | 0 | -- | FALSE | 1 |  | Fire Station - Engine Room | 0.8 | FALSE | 1
|  |  |  | -- | -- |  |  | 0 |  | 0 | -- | FALSE | 1 |  | Fire Stations - Sleeping Quarters | 0.3 | FALSE | 1
|  |  |  | -- | -- |  |  | 0 |  | 0 | -- | FALSE | 1 |  | Food Preparation | 1.2 | FALSE | 1
|  |  |  | -- | -- |  |  | 0 |  | 0 | -- | FALSE | 1 |  | Gymnasium/Exercise Center - Exercise Area | 0.9 | FALSE | 1
|  |  |  | -- | -- |  |  | 0 |  | 0 | -- | FALSE | 1 |  | Gymnasium/Exercise Center - Playing Area | 1.4 | FALSE | 1
|  |  |  | -- | -- |  |  | 0 |  | 0 | -- | FALSE | 1 |  | Hospital - Emergency | 2.7 | FALSE | 1
|  |  |  | -- | -- |  |  | 0 |  | 0 | -- | FALSE | 1 |  | Hospital - Exam/Treatment | 1.5 | FALSE | 2
|  |  |  | -- | -- |  |  | 0 |  | 0 | -- | FALSE | 1 |  | Hospital - Laundry-Washing | 0.6 | FALSE | 1
|  |  |  | -- | -- |  |  | 0 |  | 0 | -- | FALSE | 1 |  | Hospital - Medical Supply | 1.4 | FALSE | 1
|  |  |  | -- | -- |  |  | 0 |  | 0 | -- | FALSE | 1 |  | Hospital - Nurse Station | 1 | FALSE | 1
|  |  |  | -- | -- |  |  | 0 |  | 0 | -- | FALSE | 1 |  | Hospital - Nursery | 0.6 | FALSE | 1
|  |  |  | -- | -- |  |  | 0 |  | 0 | -- | FALSE | 1 |  | Hospital - Operating Room | 2.2 | FALSE | 1
|  |  |  | -- | -- |  |  | 0 |  | 0 | -- | FALSE | 1 |  | Hospital - Patient Room | 0.7 | FALSE | 1
|  |  |  | -- | -- |  |  | 0 |  | 0 | -- | FALSE | 1 |  | Hospital - Pharmacy | 1.2 | FALSE
|  |  |  | -- | -- |  |  | 0 |  | 0 | -- | FALSE | 1 |  | Hospital - Physical Therapy | 0.9 | FALSE
|  |  |  | -- | -- |  |  | 0 |  | 0 | -- | FALSE | 1 |  | Hospital - Radiology | 0.4 | FALSE
|  |  |  | -- | -- |  |  | 0 |  | 0 | -- | FALSE | 1 |  | Hospital - Recovery | 0.8 | FALSE
|  |  |  | -- | -- |  |  | 0 |  | 0 | -- | FALSE | 1 |  | Inactive Storage | 0.3 | FALSE
|  | 0 | Worksheet 5b-2 Total Budget |  | 0 | Wrksht 5b-2 Total Lighting Power (excluding exempt/track fixtures) |  |  |  |  | 0 |  |  |  | Inactive Storage - Museum | 0.8 |  | 0
[15 empty] | Laboratory | 1.4 |  | 1
[15 empty] | Library - Card File & Cataloging | 1.1 |  | 2
5-5 | [14 empty] | Library - Reading Area | 1.2 |  | 3
[15 empty] | Library -Stacks | 1.7 |  | 4
[15 empty] | Lobby - General | 1.3 |  | 5
[15 empty] | Lobby - Hotel | 1.1 |  | 6
[15 empty] | Lobby - Motion Picture Theater | 1.1 |  | 7
[15 empty] | Lobby - Performing Arts Theater | 3.3 |  | 8
[15 empty] | Lounge/Recreation | 1.2 |  | 9
[15 empty] | Lounge/Recreation - Hospital | 0.8 |  | 10
[15 empty] | Museum - General Exhibition | 1
[15 empty] | Museum -Restoration | 1.7
[15 empty] | Office-enclosed | 1.1
[15 empty] | Office-open plan | 1.1
[15 empty] | Post Office-Sorting Area | 1.2
[15 empty] | Religious Buildings - Worship-pulpit, choir | 2.4
[15 empty] | Religious Buildings Fellowship Hall | 0.9
[15 empty] | Restrooms | 0.9
[15 empty] | Retail - Grocery Sales Area | 2
[15 empty] | Retail - Jewelry & Art Sales Area | 3.5
[15 empty] | Retail - Mall Concourse | 1.5
[15 empty] | Retail - Other Merchandise Sales Area | 2
[15 empty] | Sports Arena -Court Sports Area | 2.3
[15 empty] | Sports Arena -Indoor Plying Field Area | 1.4
[15 empty] | Sports Arena -Ring Sports Area | 2.7
[15 empty] | Stairs-active | 0.6
[15 empty] | Transportation Terminal – Ticket Counter | 1.5
[15 empty] | Warehouse - Fine Material Storage | 1.4
[15 empty] | Warehouse - Medium/Bulky Material Storage | 0.9
[15 empty] | Workshop | 1.9
For track lighting enter lineal feet in column column (g) .
Column (k), enter sum of column (j) for each room only once at first entry for the room . See example in instructions.
Each room must be identified.
Describe luminaires for each individual room in plans.

## Worksheet 5c
Worksheet 5c | Project Name: | [6 empty] | Page:
EXTERIOR CANOPY AND PARKING GARAGE LIGHTING POWER | [13 empty] | TABLE 13-H — SPACE-BY-SPACE METHOD MAXIMUM ALLOWABLE LIGHTING POWER DENSITY (LPD)
Exterior Canopy Lighting
(f) Lum ID from Worksheet 5a Column (a)
| (a) | (b) | (c) | (d) | (e) |  | (g) | (h) | (i) | (j) | (k)
| Room ID (do not leave any blanks) | Area (ft2) | Canopy | Space Type LPD | Lighting Power Budget (b) x (d) |  | Quantity of Luminaires (or lineal ft. for track lighting) | Luminaire Power (Watts) | Exempt Fixtures | Lighting Power (g) x (h) | Room Total Ltg. Power |  |  |  | Common Space Types | LPD (W/ft2)
|  |  |  | -- | -- |  |  | 0 |  | 0 | 0 | FALSE | [5 empty] | 0
|  |  |  | -- | -- |  |  | 0 |  | 0 | -- | FALSE |  |  | Canopies 15 feet and over in height | 2
|  |  |  | -- | -- |  |  | 0 |  | 0 | -- | FALSE | 3 | FALSE | Canopies Under 15 feel in height | 1.5 | FALSE | 5
|  |  |  | -- | -- |  |  | 0 |  | 0 | -- | FALSE | 2 | TRUE |  |  | TRUE | 49
|  |  |  | -- | -- |  |  | 0 |  | 0 | -- | FALSE | 1 | FALSE |  |  | FALSE | 5
|  |  |  | -- | -- |  |  | 0 |  | 0 | -- | FALSE | 1 | FALSE |  |  | FALSE | 6
|  |  |  | -- | -- |  |  | 0 |  | 0 | -- | FALSE | 1 | FALSE |  |  | FALSE | 3
|  |  |  | -- | -- |  |  | 0 |  | 0 | -- | FALSE | 1 | FALSE |  |  | FALSE | 1
|  |  |  | -- | -- |  |  | 0 |  | 0 | -- | FALSE | 1 | FALSE |  |  | FALSE | 29
|  |  |  | -- | -- |  |  | 0 |  | 0 | -- | FALSE | 1 | FALSE |  |  | FALSE | 1
|  |  |  | -- | -- |  |  | 0 |  | 0 | -- | FALSE | 1 | FALSE |  |  | FALSE | 1
|  |  |  | -- | -- |  |  | 0 |  | 0 | -- | FALSE | 1 | FALSE |  |  | FALSE | 42
|  |  |  | -- | -- |  |  | 0 |  | 0 | -- | FALSE | 1 | FALSE |  |  | FALSE | 1
|  |  |  | -- | -- |  |  | 0 |  | 0 | -- | FALSE | 1 | FALSE |  |  | FALSE | 1
|  | 0 | Total Exterior Canopy Budget |  | 0 |  |  |  |  | Total Exterior Canopy Lighting Power (excluding exempt fixtures) | 0
FALSE
Parking Garage Lighting
(f) Lum ID from Worksheet 5a Column (a)
| (a) | (b) | (c) | (d) | (e) |  | (g) | (h) | (i) | (j) | (k)
| Room ID (do not leave any blanks) | Area (ft2) | Parking Garage | Space Type LPD | Lighting Power Budget (b) x (d) |  | Quantity of Luminaires (or lineal ft. for track lighting) | Luminaire Power (Watts) | Exempt Fixtures | Lighting Power (g) x (h) | Room Total Ltg. Power
|  |  |  | -- | -- |  |  | 0 |  | 0 | 0 | FALSE | 1 | FALSE | Parking Garage – Garage Area | 0.2 | FALSE | 1
|  |  |  | -- | -- |  |  | 0 |  | 0 | -- | FALSE | 1 | FALSE |  |  | FALSE | 1
|  |  |  | -- | -- |  |  | 0 |  | 0 | -- | FALSE | 1 | FALSE |  |  | FALSE | 2
|  |  |  | -- | -- |  |  | 0 |  | 0 | -- | FALSE | 1 | FALSE |  |  | FALSE | 1
|  |  |  | -- | -- |  |  | 0 |  | 0 | -- | FALSE | 1 | FALSE |  |  | FALSE | 1
|  |  |  | -- | -- |  |  | 0 |  | 0 | -- | FALSE | 1 | FALSE |  |  | FALSE | 1
|  |  |  | -- | -- |  |  | 0 |  | 0 | -- | FALSE | 1 | FALSE |  |  | FALSE | 1
|  |  |  | -- | -- |  |  | 0 |  | 0 | -- | FALSE | 1 | FALSE |  |  | FALSE | 1
|  |  |  | -- | -- |  |  | 0 |  | 0 | -- | FALSE | 1 | FALSE |  |  | FALSE | 1
|  |  |  | -- | -- |  |  | 0 |  | 0 | -- | FALSE | 1 | FALSE |  |  | FALSE | 1
|  |  |  | -- | -- |  |  | 0 |  | 0 | -- | FALSE | 1 | FALSE |  |  | FALSE | 1
|  |  |  | -- | -- |  |  | 0 |  | 0 | -- | FALSE | 1 | FALSE |  |  | FALSE | 1
|  |  |  | -- | -- |  |  | 0 |  | 0 | -- | FALSE | 1 | FALSE |  |  | FALSE | 1
|  |  |  | -- | -- |  |  | 0 |  | 0 | -- | FALSE | 1 | FALSE |  |  | FALSE | 1
|  | 0 | Total Parking Garage Budget |  | 0 |  |  |  |  | Total Parking Garage Lighting Power (excluding exempt fixtures) | 0
| Does Canopy Lighting Power Comply? | [7 empty] | N/A
| Does Parking Garage Lighting Power Comply? | [7 empty] | N/A
5-6
For track lighting enter lineal feet in column column (g) .
Column (k), enter sum of column (j) for each room only once at first entry for the room . See example in instructions.
Each room must be identified.
Describe luminaires for each individual room in plans.

## Worksheet 5d-1 (hidden)
Worksheet 5d-1 |  | Project Name: | [5 empty] | Page:
Retail Display Lighting Power | [12 empty] | TABLE 13-H — SPACE-BY-SPACE METHOD MAXIMUM ALLOWABLE LIGHTING POWER DENSITY (LPD)
1. Room # or Space ID
2. Room Area (ft2)
|  | 3. Retail Space Type | [9 empty] | 5 | FALSE
[12 empty] | 4 | FALSE
[6 empty] | (a) Lum ID from Worksheet 5a Column (a) | [5 empty] | 4 | FALSE | Common Space Types | LPD (W/ft2)
|  |  | (c) | (d) | (e) |  | (b) | (c) | (i) | (d) |  | 4 | FALSE |  |  |  | 0
|  |  | Space Type (Table 13-H) (enter space type only once per room) | Space Type LPD | Lighting Power Budget (b) x (d) |  | Quantity of Luminaires (or lineal ft. for track lighting) | Luminaire Power (Watts) | Exempt Fixtures | Lighting Power (b) x (c) |  | 3 | FALSE | Retail - Grocery Sales Area | 2
|  |  | Airport - Concourse | #N/A | #N/A |  |  | 0 |  | 0 | #N/A | 4 | FALSE | Retail - Jewelry & Art Sales Area | 3.5 | #N/A | 5
|  |  |  | -- | -- |  |  | 0 |  | 0 | #N/A | 4 | FALSE | Retail - Mall Concourse | 1.5 | #N/A | 49
|  |  |  | -- | -- |  |  | 0 |  | 0 | #N/A | 4 | FALSE | Retail - Other Merchandise Sales Area | 2 | #N/A | 5
|  |  |  | -- | -- |  |  | 0 |  | 0 | #N/A | 1 | FALSE |  |  | #N/A | 6
|  |  |  | -- | -- |  |  | 0 |  | 0 | #N/A | 1 | FALSE |  |  | #N/A | 3
|  |  |  | -- | -- |  |  | 0 |  | 0 | #N/A | 1 | FALSE |  |  | #N/A | 1
|  |  |  | -- | -- |  |  | 0 |  | 0 | #N/A | 1 |  |  |  | #N/A | 29
|  |  |  | -- | -- |  |  | 0 |  | 0 | #N/A | 1 |  |  |  | #N/A | 1
|  |  |  | -- | -- |  |  | 0 |  | 0 | #N/A | 1 |  |  |  | #N/A | 1
|  |  |  | -- | -- |  |  | 0 |  | 0 | #N/A | 1 |  |  |  | #N/A | 42
|  |  |  | -- | -- |  |  | 0 |  | 0 | #N/A | 1 |  |  |  | #N/A | 1
|  |  |  | -- | -- |  |  | 0 |  | 0 | #N/A | 1 |  |  |  | #N/A | 1
|  |  |  | -- | -- |  |  | 0 |  | 0 | #N/A | 1 |  |  |  | #N/A | 1
|  |  |  | -- | -- |  |  | 0 |  | 0 | #N/A | 1 |  |  |  | #N/A | 1
|  |  |  | -- | -- |  |  | 0 |  | 0 | #N/A | 1 |  |  |  | #N/A | 1
|  |  |  | -- | -- |  |  | 0 |  | 0 | #N/A | 1 |  |  |  | #N/A | 1
|  |  |  | -- | -- |  |  | 0 |  | 0 | #N/A | 1 |  |  |  | #N/A | 1
|  |  |  | -- | -- |  |  | 0 |  | 0 | #N/A | 1 |  |  |  | #N/A | 1
|  |  |  | -- | -- |  |  | 0 |  | 0 | #N/A | 1 |  |  |  | #N/A | 1
|  |  |  | -- | -- |  |  | 0 |  | 0 | #N/A | 1 |  |  |  | #N/A | 1
|  |  |  | -- | -- |  |  | 0 |  | 0 | #N/A | 1 |  |  |  | #N/A | 1
|  |  |  | -- | -- |  |  | 0 |  | 0 | #N/A | 1 |  |  |  | #N/A | 2
|  |  |  | -- | -- |  |  | 0 |  | 0 | #N/A | 1 |  |  |  | #N/A | 1
|  |  |  | -- | -- |  |  | 0 |  | 0 | #N/A | 1 |  |  |  | #N/A | 1
|  |  |  | -- | -- |  |  | 0 |  | 0 | #N/A | 1 |  |  |  | #N/A | 1
|  |  |  | -- | -- |  |  | 0 |  | 0 | #N/A | 1 |  |  |  | #N/A | 1
|  |  |  | -- | -- |  |  | 0 |  | 0 | #N/A | 1 |  |  |  | #N/A | 1
|  |  |  | -- | -- |  |  | 0 |  | 0 | #N/A | 1 |  |  |  | #N/A | 1
|  |  |  | -- | -- |  |  | 0 |  | 0 | #N/A | 1 |  |  |  | #N/A | 1
[12 empty] | 1 |  |  |  | #VALUE! | 1
1. | Space Display Lighting Power (total d column excluding track fixtures) |  |  | -- | -- |  |  |  |  | 0 |  | 1 |  |  |  | #VALUE! | 1
2. | Total length of track lighting (ft) | [8 empty] | 0 | 0 | 1 |  |  |  | FALSE | 1
3. | Line 2 multiplied by 50 Watts/ft | [9 empty] | 1 | 1 |  |  |  | TRUE | 1
4. | Total amperage of circuit breaker(s) serving track lighting (amps) | [9 empty] | 2 | 1 |  |  |  | TRUE | 1
5. | Voltage of circuit breaker serving track lighting (volts) | [9 empty] | 3 | 1 |  |  |  | TRUE | 1
6. | Maximum wattage of track lighting (multiply line 4 by line 5) | [9 empty] | 4 | 1 |  |  |  | TRUE | 2
7. | VA rating of the inline current limiter or the low voltage transformers | [9 empty] | 5 | 1 |  |  |  | TRUE | 1
8. | Track Lighting Power (the lesser value of line 3, 6 or 7) | [9 empty] | 6 | 1 |  |  |  | TRUE | 1
9. | Total Space Display Lighting Power (Watts) (line 1 + line 8) | [8 empty] | 0 | 7 | 1 |  |  |  | TRUE | 1
10. | Total Space Display Lighting Power Budget (Watts) (room area x 1.75 to max of 17,500) | [8 empty] | 0 | 8 | 1 |  |  |  | TRUE | 1
11. | Does Space Retail Display Meet Space Budget (Line 9 less than line 10 and less than 17,500 W)? | [8 empty] | N/A | 9 | 1 |  |  |  | TRUE | 1
[11 empty] | 10 | 1 |  |  |  | TRUE | 1
Total Number of Additional Worksheet 5d |  |  |  | -- | -- | [5 empty] | 0 | 1 |  |  |  | #VALUE! | 0
|  |  | Worksheet 5b-2 Total Budget |  | #N/A | [6 empty] | 1 |  |  |  | #VALUE! | 1
|  |  |  | -- | -- | [6 empty] | 1 |  |  |  | #VALUE! | 2
5-6 | [11 empty] | 1 |  |  |  | #VALUE! | 3
[12 empty] | 1 |  |  |  | #VALUE! | 4
5
6
7
8
9
10
Describe luminaires for each individual room in plans.
For track lighting enter lineal feet in column (b).
Complete one worksheet for each room (space) for retail display lighting that is specifically directed to highlight merchandise, and is controlled separately from the general lighting system within the room. General lighting should be included on Worksheet 5b.

## Worksheet 5d (hidden)
Worksheet 5d |  | Project Name: | [5 empty] | Page:
Retail Display Lighting Power | [12 empty] | TABLE 13-H — SPACE-BY-SPACE METHOD MAXIMUM ALLOWABLE LIGHTING POWER DENSITY (LPD)
1. Room # or Space ID
2. Room Area (ft2)
|  | 3. Retail Space Type | [5 empty] | Retail - Jewelry & Art Sales Area |  |  |  | 5 | FALSE
[12 empty] | 4 | FALSE
[6 empty] | (a) Lum ID from Worksheet 5a Column (a) | [5 empty] | 4 | FALSE | Common Space Types | LPD (W/ft2)
|  |  | (c) | (d) | (e) |  | (b) | (c) | (i) | (d) |  | 4 | FALSE |  |  |  | 0
|  |  | Space Type (Table 13-H) (enter space type only once per room) | Space Type LPD | Lighting Power Budget (b) x (d) |  | Quantity of Luminaires (or lineal ft. for track lighting) | Luminaire Power (Watts) | Exempt Fixtures | Lighting Power (b) x (c) |  | 3 | FALSE | Retail - Grocery Sales Area | 2
|  |  | Airport - Concourse | #N/A | #N/A |  |  | 0 |  | 0 | #N/A | 4 | FALSE | Retail - Jewelry & Art Sales Area | 3.5 | #N/A | 5
|  |  |  | -- | -- |  |  | 0 |  | 0 | #N/A | 4 | FALSE | Retail - Mall Concourse | 1.5 | #N/A | 49
|  |  |  | -- | -- |  |  | 0 |  | 0 | #N/A | 4 | FALSE | Retail - Other Merchandise Sales Area | 2 | #N/A | 5
|  |  |  | -- | -- |  |  | 0 |  | 0 | #N/A | 1 | FALSE |  |  | #N/A | 6
|  |  |  | -- | -- |  |  | 0 |  | 0 | #N/A | 1 | FALSE |  |  | #N/A | 3
|  |  |  | -- | -- |  |  | 0 |  | 0 | #N/A | 1 | FALSE |  |  | #N/A | 1
|  |  |  | -- | -- |  |  | 0 |  | 0 | #N/A | 1 |  |  |  | #N/A | 29
|  |  |  | -- | -- |  |  | 0 |  | 0 | #N/A | 1 |  |  |  | #N/A | 1
|  |  |  | -- | -- |  |  | 0 |  | 0 | #N/A | 1 |  |  |  | #N/A | 1
|  |  |  | -- | -- |  |  | 0 |  | 0 | #N/A | 1 |  |  |  | #N/A | 42
|  |  |  | -- | -- |  |  | 0 |  | 0 | #N/A | 1 |  |  |  | #N/A | 1
|  |  |  | -- | -- |  |  | 0 |  | 0 | #N/A | 1 |  |  |  | #N/A | 1
|  |  |  | -- | -- |  |  | 0 |  | 0 | #N/A | 1 |  |  |  | #N/A | 1
|  |  |  | -- | -- |  |  | 0 |  | 0 | #N/A | 1 |  |  |  | #N/A | 1
|  |  |  | -- | -- |  |  | 0 |  | 0 | #N/A | 1 |  |  |  | #N/A | 1
|  |  |  | -- | -- |  |  | 0 |  | 0 | #N/A | 1 |  |  |  | #N/A | 1
|  |  |  | -- | -- |  |  | 0 |  | 0 | #N/A | 1 |  |  |  | #N/A | 1
|  |  |  | -- | -- |  |  | 0 |  | 0 | #N/A | 1 |  |  |  | #N/A | 1
|  |  |  | -- | -- |  |  | 0 |  | 0 | #N/A | 1 |  |  |  | #N/A | 1
|  |  |  | -- | -- |  |  | 0 |  | 0 | #N/A | 1 |  |  |  | #N/A | 1
|  |  |  | -- | -- |  |  | 0 |  | 0 | #N/A | 1 |  |  |  | #N/A | 1
|  |  |  | -- | -- |  |  | 0 |  | 0 | #N/A | 1 |  |  |  | #N/A | 2
|  |  |  | -- | -- |  |  | 0 |  | 0 | #N/A | 1 |  |  |  | #N/A | 1
|  |  |  | -- | -- |  |  | 0 |  | 0 | #N/A | 1 |  |  |  | #N/A | 1
|  |  |  | -- | -- |  |  | 0 |  | 0 | #N/A | 1 |  |  |  | #N/A | 1
|  |  |  | -- | -- |  |  | 0 |  | 0 | #N/A | 1 |  |  |  | #N/A | 1
|  |  |  | -- | -- |  |  | 0 |  | 0 | #N/A | 1 |  |  |  | #N/A | 1
|  |  |  | -- | -- |  |  | 0 |  | 0 | #N/A | 1 |  |  |  | #N/A | 1
|  |  |  | -- | -- |  |  | 0 |  | 0 | #N/A | 1 |  |  |  | #N/A | 1
[12 empty] | 1 |  |  |  | #VALUE! | 1
1. | Space Display Lighting Power (total d column excluding track fixtures) |  |  | -- | -- |  |  |  |  | 0 |  | 1 |  |  |  | #VALUE! | 1
2. | Total length of track lighting (ft) | [8 empty] | 0 | 0 | 1 |  |  |  | FALSE | 1
3. | Line 2 multiplied by 50 Watts/ft | [9 empty] | 1 | 1 |  |  |  | TRUE | 1
4. | Total amperage of circuit breaker(s) serving track lighting (amps) | [9 empty] | 2 | 1 |  |  |  | TRUE | 1
5. | Voltage of circuit breaker serving track lighting (volts) | [9 empty] | 3 | 1 |  |  |  | TRUE | 1
6. | Maximum wattage of track lighting (multiply line 4 by line 5) | [9 empty] | 4 | 1 |  |  |  | TRUE | 2
7. | VA rating of the inline current limiter or the low voltage transformers | [9 empty] | 5 | 1 |  |  |  | TRUE | 1
8. | Track Lighting Power (the lesser value of line 3, 6 or 7) | [9 empty] | 6 | 1 |  |  |  | TRUE | 1
9. | Total Space Display Lighting Power (Watts) (line 1 + line 8) | [8 empty] | 0 | 7 | 1 |  |  |  | TRUE | 1
10. | Total Space Display Lighting Power Budget (Watts) (room area x 1.75 to max of 17,500) | [8 empty] | 0 | 8 | 1 |  |  |  | TRUE | 1
11. | Does Space Retail Display Meet Space Budget (Line 9 less than line 10 and less than 17,500 W)? | [8 empty] | N/A | 9 | 1 |  |  |  | TRUE | 1
[11 empty] | 10 | 1 |  |  |  | TRUE | 1
|  |  |  | -- | -- | [5 empty] | 0 | 1 |  |  |  | #VALUE! | 0
|  |  | Worksheet 5b-2 Total Budget |  | #N/A | [6 empty] | 1 |  |  |  | #VALUE! | 1
|  |  |  | -- | -- | [6 empty] | 1 |  |  |  | #VALUE! | 2
5-6 | [11 empty] | 1 |  |  |  | #VALUE! | 3
[12 empty] | 1 |  |  |  | #VALUE! | 4
5
6
7
8
9
10
Describe luminaires for each individual room in plans.
For track lighting enter lineal feet in column (b).
Complete one worksheet for each room (space) for retail display lighting that is specifically directed to highlight merchandise, and is controlled separately from the general lighting system within the room. General lighting should be included on Worksheet 5b.