Statement of Work (SOW)

DESSP New Cumberland- Post 4 Canopy Shelter and Lighting

- Scope of Work to be Performed:

The project consist of furnishing and installing a turn-key system of inspection shelters and associated interior lighting systems at Guard Post 4 (Truck Gate) at DDSP new Cumberland, PA. Project task includes, but is not limited to F.O.B. delivery and set-up of two (2) temporary canopies, interior lighting fixtures, underground and aboveground electric service to canopy site from an existing building 2011, located approximately 130 feet away.

Furnish and install one each canopies for inbound traffic lane and outbound traffic lane.

The following is the canopy requirements:

a. Furnish and install on the inbound side of traffic shall be a 54-foot wide by 120-foot long canopy with 12-400 watt metal halide lights. This will have two inbound lane coverage.

b. Furnish and install on the outbound side of traffic shall be a 36-foot wide by 40-foot long canopy with 6-400 watt metal halide lights.  This will have a one lane outbound coverage.

c. Canopy frame, including all weld joints, shall be constructed of heavy-wall galvanized tubular steel members.

d. Canopy fabric shall be flame-retardant PVC with polyester scrim.  Color-White.

e. Both canopies shall provide a minimum 30-foot center and minimum 22-foot sidewall height.

f. Canopies shall be installed using sufficient anchors to existing earth or pavement surfaces to prevent wind uplift when subjected to wind load design standards for York County, Pennsylvania.

g. Canopy installation shall be turn-key by the canopy provider, F.O.B. New Cumberland, PA.

h. All existing surfaces disturbed by canopy installation activities shall be restored in-kind.

i. Canopies include side panels with clear viewing windows.

j.  The inbound structure will include roof mounted viewing mirrors, centered over each of the traffic lanes, to assist in the inspection process.  Mirrors will be placed at intervals to provide adequate viewing of the tops of vehicles from different angles and should be approximately 4’ wide by 5’ long.

k.   The outbound structure will include roof mounted viewing mirrors, centered over the traffic lane, to assist in the inspection process.  Mirrors will be placed at intervals to provide adequate viewing of the tops of vehicles from different angles and should be approximately 4’ wide by 5’ long.

l.  The North side of the larger (inbound traffic lane) structure will include an opening at least 40’ wide to allow access to the four parking spaces between the inbound and outbound traffic lanes.

m.  The South side of the larger (inbound traffic lane) structure shall include two (2) personnel ingress/egress openings to allow Police Officers suitable locations to depart the structure.  The personnel openings (2) on the South side would need to be at least 4-feet wide.

The following is the electrical service requirements:

a. Furnish and install a 2-pole, 50 amp circuit breaker in the existing power panel located in building 2011 to feed the new electric service to the new canopies.  The existing panel is a GE panel; catalog number AQF3301AB, 120/208 volt.

b. Furnish and install a new underground electric service from the existing power panel located in building 2011, consisting of three (3) #6 AWG copper conductors and one (1) #6 AWG copper ground in 1-inch diameter conduit.  Depth of conduit shall be minimum 24 inches and shall have red electrical marker tape at 12-inch depth. Conduit shall be galvanized rigid steel where exposed above grade.

c. Furnish and install two (2) 20-amp branch circuits from the new power panel to feed the inbound canopy lighting circuits and to feed the outbound canopy lighting circuits.  Branch circuits shall consist of two (2) #12 AWG copper conductors and one (1) #12 AWG copper ground in ¾-inch diameter galvanized rigid steel conduit.  Mount conduit to eave of existing building 2007.

d. Electrical lighting installation shall include wiring, hangers, switches, and cover boxes to provide a complete and usable system.

e. All existing surfaces disturbed by electric service trenching activities shall be restored in-kind.

2.  Description of Contractor’s Tasks:

The contractor shall be responsible for any damage to the grounds, shrubbery, underground utilities, asphalt, and concrete due to normal construction process.  The contractor will be responsible for protecting and restoration if damage occurs.

3.   Government Furnished Property/Equipment:

Government shall be responsible for removing existing metal light pole as indicated on the drawing.

4.  Certification and Acceptance:

Final acceptance Post-4 Canopies will be provided by the Contracting Officer Representative (COR) assigned to this project.

- Suggested Canopy Sources:

Below is a list of possible canopy sources.  This list is by no means conclusive and is only provided for reference.

Big Top Shelters

3255 N. US 19
            Perry, Florida 32347 USA

Phone: 1-800-277-8677

Fax: 1-850-584-7713

sales@bigtopshelters.com

Universal Fabric Structures

2200 Kumry Road
            Quakertown, PA 18951
            TEL: +1 215-529-9921        
            TOLL FREE: +1 800-634-8368
            FAX: +1 215-529-9936  
            EMAIL: sales@ufsinc.com

Fabric Structures-USA., LLC

24 South O Street

Lake Worth, Florida 3346

Phone: 561-586-7023

Fax: 561-586-7024

Email: info@fabricstructures-usa.com

6.  Definitions of Terms and Abbreviations:

a.	DDC		Defense Distribution Center

b.	DES		DLA Enterprise Support

c.	DESSP            Defense Enterprise Support Susquehanna PA.

d.	SOW		Statement of Work

e.   	AWG               American Wire Gauge

f.    	PVC                Polyvinyl Chloride

g.  	COR		Contracting Officer Representative