UNITED STATES DEPARTMENT OF AGRICULTURE

Rural Utilities Service

BULLETIN 1751F-635

SUBJECT:  Aerial Plant Construction

TO:  All Telecommunications Borrowers

RUS Telecommunications Staff

EFFECTIVE DATE:  Date of Approval

EXPIRATION DATE:  Seven years from effective date

OFFICE OF PRIMARY INTEREST:  Outside Plant Branch, Telecommunications Standards Division

PREVIOUS INSTRUCTIONS:  This bulletin replaces RUS Telecommunications Engineering & Construction Manual (TE&CM) Section 635, Construction of Aerial Cable Plant, Issue 3, dated February 1962; Addenda 2, 3, and 4, dated October 1966, March 1979, and August 1979; respectively.

FILING INSTRUCTIONS:  Discard RUS TE&CM Section 635, Construction of Aerial Cable Plant, Issue 3, dated February 1962; Addenda 2, 3, and 4, dated October 1966, March 1979, and August 1979, respectively; and replace them with this bulletin.  File with 7 CFR 1751 and is available to the RUS staff on RUSNET.

PURPOSE:  This bulletin provides RUS borrowers, consulting engineers, contractors and other interested parties with information on the construction of aerial plant facilities.

Wally Beyer                        6-12-96

Administrator                         Date

TABLE OF CONTENTS

Abbreviations ............................................ 6

Definitions .............................................. 7

1.  General ................................................. 10

2.  Inspection of Construction .............................. 12

3.  Suspension Strand Stringing ............................. 16

4.  Suspension Strand Splices ............................... 18

5.  Suspension Strand Tensioning ............................ 18

6.  Cable Installation and Lashing .......................... 23

7.  Self-Supporting, Filled, Fiber Optic

Cable Installation ...................................... 26

8.  Sag and Tension of Installed Filled Cables .............. 27

9.  Railroad Crossing ....................................... 57

10.  Pole Stepping ........................................... 57

11.  Mechanical Protection of Cable and Prevention of

Cable Dancing ........................................... 58

12.  Handling and Care of Materials During Construction ...... 59

13.  Repair of Cables Damaged During Construction ............ 59

14.  Preparation for Splicing or Termination ................. 60

15.  Installation Procedures for Filled Cables in

Cold Weather ............................................ 60

16.  Assembly Units .......................................... 61

17.  Numbering and Acceptance Testing ........................ 61

TABLES & FIGURES

Table  1  6M EHS Suspension Strand - Initial Installation

Tensions and Sags ................................ 19

Table  2  10M EHS Suspension Strand - Initial Installation

Tensions and Sags ................................ 20

Table  3  16M EHS Suspension Strand - Initial Installation

Tensions and Sags ................................ 21

Table  4  Maximum Span Lengths by Loading Districts -

6M EHS Stand with Aerial Cable Lashed to Strand .. 21

Table  5  Maximum Span Lengths by Loading Districts -

10M EHS Stand with Aerial Cable Lashed to Strand . 22

Table  6  Maximum Span Lengths by Loading Districts -

16M EHS Stand with Aerial Cable Lashed to Strand . 22

Table  7  Roller Spacing Versus Cable Weight ............... 24

Table  8  Initial Sag and Tension - 6M EHS Suspension

Strand Supporting Cable Weighing 0.2 lb/ft for

Heavy, Medium, and Light Loading Districts ....... 28

Table  9  Initial Sag and Tension - 6M EHS Suspension

Strand Supporting Cable Weighing 0.4 lb/ft for

Heavy, Medium, and Light Loading Districts ....... 29

Table 10  Initial Sag and Tension - 6M EHS Suspension

Strand Supporting Cable Weighing 0.6 lb/ft for

Heavy, Medium, and Light Loading Districts ....... 30

Table 11  Initial Sag and Tension - 6M EHS Suspension

Strand Supporting Cable Weighing 0.8 lb/ft for

Heavy, Medium, and Light Loading Districts ....... 31

Table 12  Initial Sag and Tension - 6M EHS Suspension

Strand Supporting Cable Weighing 1.0 lb/ft for

Heavy, Medium, and Light Loading Districts ....... 31

Table 13  Initial Sag and Tension - 6M EHS Suspension

Strand Supporting Cable Weighing 1.2 lb/ft for

Heavy, Medium, and Light Loading Districts ....... 32

Table 14  Initial Sag and Tension - 6M EHS Suspension

Strand Supporting Cable Weighing 1.4 lb/ft for

Heavy, Medium, and Light Loading Districts ....... 32

Table 15  Initial Sag and Tension - 6M EHS Suspension

Strand Supporting Cable Weighing 1.6 lb/ft for

Heavy, Medium, and Light Loading Districts ....... 33

Table 16  Initial Sag and Tension - 6M EHS Suspension

Strand Supporting Cable Weighing 1.8 lb/ft for

Heavy, Medium, and Light Loading Districts ....... 33

Table 17  Initial Sag and Tension - 6M EHS Suspension

Strand Supporting Cable Weighing 2.0 lb/ft for

Heavy, Medium, and Light Loading Districts ....... 34

Table 18  Initial Sag and Tension - 10M EHS Suspension

Strand Supporting Cable Weighing 0.4 lb/ft for

Heavy, Medium, and Light Loading Districts ....... 35

Table 19  Initial Sag and Tension - 10M EHS Suspension

Strand Supporting Cable Weighing 0.6 lb/ft for

Heavy, Medium, and Light Loading Districts ....... 36

Table 20  Initial Sag and Tension - 10M EHS Suspension

Strand Supporting Cable Weighing 0.8 lb/ft for

Heavy, Medium, and Light Loading Districts ....... 37

Table 21  Initial Sag and Tension - 10M EHS Suspension

Strand Supporting Cable Weighing 1.0 lb/ft for

Heavy, Medium, and Light Loading Districts ....... 38

Table 22  Initial Sag and Tension - 10M EHS Suspension

Strand Supporting Cable Weighing 1.2 lb/ft for

Heavy, Medium, and Light Loading Districts ....... 39

Table 23  Initial Sag and Tension - 10M EHS Suspension

Strand Supporting Cable Weighing 1.4 lb/ft for

Heavy, Medium, and Light Loading Districts ....... 40

Table 24  Initial Sag and Tension - 10M EHS Suspension

Strand Supporting Cable Weighing 1.6 lb/ft for

Heavy, Medium, and Light Loading Districts ....... 41

Table 25  Initial Sag and Tension - 10M EHS Suspension

Strand Supporting Cable Weighing 1.8 lb/ft for

Heavy, Medium, and Light Loading Districts ....... 42

Table 26  Initial Sag and Tension - 10M EHS Suspension

Strand Supporting Cable Weighing 2.0 lb/ft for

Heavy, Medium, and Light Loading Districts ....... 42

Table 27  Initial Sag and Tension - 10M EHS Suspension

Strand Supporting Cable Weighing 2.2 lb/ft for

Heavy, Medium, and Light Loading Districts ....... 43

Table 28  Initial Sag and Tension - 10M EHS Suspension

Strand Supporting Cable Weighing 2.4 lb/ft for

Heavy, Medium, and Light Loading Districts ....... 43

Table 29  Initial Sag and Tension - 10M EHS Suspension

Strand Supporting Cable Weighing 2.6 lb/ft for

Heavy, Medium, and Light Loading Districts ....... 44

Table 30  Initial Sag and Tension - 10M EHS Suspension

Strand Supporting Cable Weighing 2.8 lb/ft for

Heavy, Medium, and Light Loading Districts ....... 44

Table 31  Initial Sag and Tension - 10M EHS Suspension

Strand Supporting Cable Weighing 3.0 lb/ft for

Heavy, Medium, and Light Loading Districts ....... 45

Table 32  Initial Sag and Tension - 10M EHS Suspension

Strand Supporting Cable Weighing 3.2 lb/ft for

Heavy, Medium, and Light Loading Districts ....... 45

Table 33  Initial Sag and Tension - 10M EHS Suspension

Strand Supporting Cable Weighing 3.4 lb/ft for

Heavy, Medium, and Light Loading Districts ....... 46

Table 34  Initial Sag and Tension - 10M EHS Suspension

Strand Supporting Cable Weighing 3.6 lb/ft for

Heavy, Medium, and Light Loading Districts ....... 46

Table 35  Initial Sag and Tension - 10M EHS Suspension

Strand Supporting Cable Weighing 3.8 lb/ft for

Heavy, Medium, and Light Loading Districts ....... 47

Table 36  Initial Sag and Tension - 10M EHS Suspension

Strand Supporting Cable Weighing 4.0 lb/ft for

Heavy, Medium, and Light Loading Districts ....... 47

Table 37  Initial Sag and Tension - 10M EHS Suspension

Strand Supporting Cable Weighing 4.2 lb/ft for

Heavy, Medium, and Light Loading Districts ....... 47

Table 38  Initial Sag and Tension - 10M EHS Suspension

Strand Supporting Cable Weighing 4.4 lb/ft for

Heavy, Medium, and Light Loading Districts ....... 48

Table 39  Initial Sag and Tension - 10M EHS Suspension

Strand Supporting Cable Weighing 4.6 lb/ft for

## Heavy, Medium, and Light Loading Districts ....... 48

Table 40  Initial Sag and Tension - 10M EHS Suspension

Strand Supporting Cable Weighing 4.8 lb/ft for

Heavy, Medium, and Light Loading Districts ....... 48

Table 41  Initial Sag and Tension - 10M EHS Suspension

Strand Supporting Cable Weighing 5.0 lb/ft for

Heavy, Medium, and Light Loading Districts ....... 49

Table 42  Initial Sag and Tension - 16M EHS Suspension

Strand Supporting Cable Weighing 1.0 lb/ft for

Heavy, Medium, and Light Loading Districts ....... 50

Table 43  Initial Sag and Tension - 16M EHS Suspension

Strand Supporting Cable Weighing 1.5 lb/ft for

Heavy, Medium, and Light Loading Districts ....... 51

Table 44  Initial Sag and Tension - 16M EHS Suspension

Strand Supporting Cable Weighing 2.0 lb/ft for

Heavy, Medium, and Light Loading Districts ....... 52

Table 45  Initial Sag and Tension - 16M EHS Suspension

Strand Supporting Cable Weighing 2.5 lb/ft for

Heavy, Medium, and Light Loading Districts ....... 53

Table 46  Initial Sag and Tension - 16M EHS Suspension

Strand Supporting Cable Weighing 3.0 lb/ft for

Heavy, Medium, and Light Loading Districts ....... 54

Table 47  Initial Sag and Tension - 16M EHS Suspension

Strand Supporting Cable Weighing 3.5 lb/ft for

Heavy, Medium, and Light Loading Districts ....... 55

Table 48  Initial Sag and Tension - 16M EHS Suspension

Strand Supporting Cable Weighing 4.0 lb/ft for

Heavy, Medium, and Light Loading Districts ....... 56

Table 49  Initial Sag and Tension - 16M EHS Suspension

Strand Supporting Cable Weighing 4.5 lb/ft for

Heavy, Medium, and Light Loading Districts ....... 56

Table 50  Initial Sag and Tension - 16M EHS Suspension

Strand Supporting Cable Weighing 5.0 lb/ft for

Heavy, Medium, and Light Loading Districts ....... 57

Figure 1  Selection of Points for Reading and

Equalizing Strand Tensions ....................... 62

Figure 2  Moving Reel Method of Lashing

Cable to Suspension Strand ....................... 63

Figure 3  Stationary Reel Method of Lashing

Cable to Suspension Strand ....................... 64

INDEX:

Outside Plant

Construction

Telecommunications

ABBREVIATIONS

°C	Degrees Celsius

CFO	Aerial Filled Self-Supporting Fiber Optic Cable

Assembly Unit

CFR	Code of Federal Regulations

CO	Aerial Filled Fiber Optic Cable Assembly Unit

CW	Aerial Filled Cable Assembly Unit

EHS	Extra High Strength Galvanized Steel

°F	Degrees Fahrenheit

ft	Feet

in.	Inches

kg/m	Kilograms per meter

lbf	Pounds-force

lb/ft	Pounds per foot

m	Meter

mm	Millimeter

N	Newton

NESC	National Electrical Safety Code

R/W	Right-of-way

RUS	Rural Utilities Service

TE&CM	Telecommunications Engineering and Construction Manual

DEFINITIONS

Anchor:  A device that serves as a reliable support to hold an object firmly in place.  The term anchor is normally associated with cone, plate, screw, or concrete anchors, but the terms snub, deadman and anchor log are usually associated with pole stubs or logs set or buried in the ground to serve as temporary anchors.  The latter are often used at pull and tension sites.

CFO:  An aerial filled self-supporting fiber optic cable assembly unit which includes all the material and labor costs to install 1000 feet (304.8 meters) of self-supporting filled fiber optic cable.  The units also includes the material and labor costs for installing all supporting hardware, cable guards, insulating tapes, and bonding of the shield and supporting member.  This unit is presently a “nonstandard” assembly unit.

CO:  An aerial filled fiber optic cable assembly unit which includes all the material and labor costs to install 1000 feet (304.8 meters) of filled aerial fiber optic cable.  The unit also includes the material and labor costs for installing the suspension strand, lashing wire, attachments to strand, and bonding of the cable shield and suspension strand.

Construction Drawings:  The drawings developed through the staking process and used to guide the construction of outside plant facilities.

Contractor:  A provider of goods or services for the Project, other than the Engineer.

CW:  An aerial filled cable assembly unit which includes all the material and labor costs to install 1000 feet (304.8 meters) of filled aerial copper cable.  The unit also includes the material and labor costs for installing the suspension strand, lashing wire, attachments to strand, and bonding of the cable shield and suspension strand.

Figure Eighting:  A method of removing cable or wire from a reel and forming the removed cable or wire in the shape of the numeral eight.

Guy:  A tension member having one end secured to a fixed object and the other end attached to a pole or other structural part that it supports.

Guy Strand:  A stranded group of wires used as a semiflexible tension support between a pole or structure and the anchor rod, or between structures.

Heavy Loading District:  Horizontal wind pressure, at a right angle to the line, of 4 pounds per square foot (190 pascals) upon the projected area of the cylindrical surfaces of all supported wires (including suspension strand and cables) when coated with a radial thickness of 0.50 inch (12.5 millimeters) of ice at a temperature of 0°F (-20°C).

Inspect:  To monitor and examine the work of the Contractor, compare the work to the contract, and note the details and quantities of construction on records and progress reports.

Inspector:  A representative of the Engineer who Inspects construction and reports compliance or noncompliance to the Resident Engineer.

Lashed Aerial Cable:  Cable that is attached to the separate suspension strand by lashing wire to support the cable.

Lashing Wire:  A wire that is used to support the cable to the suspension strand by wrapping it around the cable and suspension strand.

Light Loading District:  Horizontal wind pressure, at a right angle to the line, of 9 pounds per square foot (430 pascals) upon the projected area of the cylindrical surfaces of all supported wires (including suspension strand and cables) at a temperature of 30°F (-1°C).

Medium Loading District:  Horizontal wind pressure, at a right angle to the line, of 4 pounds per square foot (190 pascals) upon the projected area of the cylindrical surfaces of all supported wires (including suspension strand and cables) when coated with a radial thickness of 0.25 inch (6.5 millimeters) of ice at a temperature of 15°F (-10°C).

Pole:  A column of wood supporting overhead cables usually by means of brackets.

Pole Line:  A series of poles arranged to support cables above the surface of the ground: and the structures and cables supported thereon.

Project:  The telecommunications construction and procurements financed by a particular RUS loan.

Resident Engineer:  The representative of the Engineer who is delegated full-time “on-site” engineering responsibilities for construction administration.

Right-of-Way:  The strip of land over which facilities such as highways, railroads, power lines, other utilities, or telecommunication lines are constructed.

RUS Accepted (Material and Equipment):  Material and equipment which RUS has reviewed and determined that:

a.  Final assembly is conducted within the United States, Mexico, or Canada or any of their respective territories and the cost of United States, Mexican, or Canadian, manufactured components, in any combination, is more than 50 percent of the total cost of all components utilized in the material or equipment, and

b.  The material or equipment complies with pertinent RUS or industry standards and field experience has demonstrated that the material or equipment is suitable for use on systems of RUS telecommunications borrowers.

RUS Technically Accepted (Material and Equipment):  Material and equipment which RUS has reviewed and determined that:

a.  Final assembly is not conducted within the United States, Mexico, or Canada, or any of their territories, or the cost of components within the material or equipment which are manufactured within the United States, Mexico, or Canada, or any of their territories, cost 50 percent or less than the total cost of all components utilized in the material or equipment, and

b.  The material or equipment complies with pertinent RUS or industry standards and field experience has demonstrated that the material or equipment is suitable for use on systems of RUS telecommunications borrowers.

Sag:  The distance measured vertically from a cable to the straight line joining its two points of support.  Unless otherwise stated in the National Electrical Safety Code (NESC), the sag referred to is the sag at the midpoint of the span.

Self-Supporting Aerial Fiber Optic Cable:  A cable consisting of one or more buffered optical fibers factory assembled with a messenger that supports the cable.

Span Length:  The horizontal distance between two adjacent supporting points of a cable.

Suspension Strand:  A stranded group of wires supported above the ground at intervals by poles or other structures and employed to furnish within these intervals frequent points of support for cables.

1.  GENERAL

1.1  This bulletin discusses in particular the construction of aerial plant using filled copper cables and filled fiber optic cables.  The information and recommendations in this bulletin are advisory.

1.2  Aerial plant for both filled copper cables and filled fiber optic cables should be constructed by attaching cables to utility poles at varying span lengths by lashing cables to separate suspension strands.  Filled fiber optic cables may also be constructed using cables containing an integrated suspension strand.  Filled fiber optic aerial cables containing integrated suspension strands are referred to as a self-supporting fiber optic cables.

1.3  Some of the work items associated with aerial plant construction are as follows:

a.  Pre-installation inspection of copper cables and fiber

optic cables;

b.  Pre-installation inspection of self-supporting fiber

optic cables;

c.  Pre-installation inspection of suspension and guy

strands and lashing wires;

d.  Installation and tensioning of the suspension strand;

e.  Installation of guy strands and pole anchors;

f.  Installation of aerial splice and ready-access cases

for copper cables;

g.  Installation of aerial filled splice cases for fiber

optic cables;

h.  Installation of aerial filled splice cases for

self-supporting fiber optic cables;

i.  Installation of cable slack loops at utility poles for

fiber optic cables;

j.  Splicing of copper cables and connection of shield

bonds and related grounding;

k.  Splicing of fiber optic cables;

l.  Connection of armor bonds and related grounding for

aerial, armored fiber optic cables;

m.  Terminating aerial service wire to filled terminal

blocks in ready-access cases, fixed count and pole

mount terminals;

n.  Placement of load coils [When loaded lines are

determined by RUS to be economically feasible and the	overall system design complies with the Modernization

Plan (7 CFR 1751, Subpart B)];

o.  Placement of digital carrier repeater housings and

lightwave repeater housings; and

p.  Conducting acceptance tests.

1.4  Additional information for the use in the construction of aerial plant facilities can be found in the following Rural Utilities Service (RUS) documents:

a.  RUS Form 515, RUS Telephone System Construction Contract

(Labor and Materials);

b.  RUS Bulletin 345-153, Specifications and Drawings for

Construction of Pole Lines, Aerial Cables and Wires

(RUS Form 515f);

c.  RUS Bulletin 345-63, RUS Standard for Acceptance Tests

and Measurements of Telephone Plant (PC-4);

d.  RUS Bulletin 1728F-700, RUS Specification for Wood

Poles, Stubs and Anchor Logs;

e.  RUS Bulletin 1751F-626, Staking of Aerial Plant;

f.  RUS Bulletin 1751F-630, Design of Aerial Plant;

g.  RUS Bulletin 1753F-401(PC-2), REA Standard for Splicing

Copper and Fiber Optic Cables (codified under 7 Code of

Federal Regulations [CFR] 1755.200);

h.  Telecommunication Engineering and Construction Manual

(TE&CM) Section 650, Guy and Anchors on Wire and Cable

Lines; and

i.  Latest edition of the National Electrical Safety

Code (NESC).

1.5  To convert the English Units to Metric Units for Tables 1 through 3 of Paragraph 5.2 and Tables 8 through 50 of Paragraph 8.2 use the following formulae:

a.  Millimeters (mm) = Inches (in.) x 25.4;

b.  Meters (m) = Feet (ft) x 0.3048;

c.  Newtons (N) = Pound-force (lbf) x 4.448;

d.  °C = 5/9 x (°F - 32); and

e.  Kilograms per meter (kg/m) =

Pounds per foot (lb/ft) x 1.488.

2.  INSPECTION OF CONSTRUCTION

2.1  The construction of aerial plant facilities should be inspected.  This inspection should be accomplished after the construction operation has been completed by the resident engineer or resident engineer’s assigned inspector.  The resident engineer or resident engineer’s assigned inspector also has the responsibility to verify that the correct class and length of pole; correct strand size; correct pair sizes, gauges, and type of copper cables; and the correct number of optical fibers, type of optical fibers, and types of fiber optic cables have been installed and free of damage after construction has been completed.

2.2  When more than one aerial plant construction operation is being performed at the same time, each construction operation after completion should be inspected.  During construction of cables, construction may be stopped pending the resident engineer’s decision concerning proposed changes in the construction route from that shown on the construction drawings.  Undue delays in making such decisions are costly to the borrower and should be avoided.

2.3  All reels of filled copper and fiber optic cables; reels of filled, self-supporting fiber optic cables; reels of suspension strands; and spools of lashing wires should be inspected by the contractor before installation for visual signs of damage.  In addition, filled copper, filled fiber optic, and filled, self-supporting fiber optic cable ends should be sealed to prevent moisture entry into the cores of copper and fiber optic cables during transportation, in storage, and during placement.

2.4  The aerial plant construction route should be inspected before beginning construction.  When selecting the aerial plant construction route, the convenience and ease of installation should be considered providing the quality of construction, which would affect future operation and maintenance of the telecommunications system, is not decreased and construction costs to the borrower are not substantially increased.

2.5  Cables, suspension stands, lashing wires, etc. should be inspected after installation to ensure that cables, suspension strands, lashing wires, etc. have not be damaged and to verify that proper cable sags and tensions have been maintained

throughout the line.  Cables should be checked for damage at severe changes in grade, corners, and corner angles after installation.

2.6  Installation of reel-end splices which may change proposed digital carrier or lightwave repeater locations should be considered for re-routing.  Because of the limited deviations allowed in digital carrier or lightwave repeater spacings, all repeatered lines should be constructed first, starting at the central office and advancing in the direction of the repeatered line in a continuous operation to the last repeater point on each repeatered section unless otherwise specified in the contract.  Deviations from this procedure should be approved in lieu of holding up the construction project in the event of late cable deliveries, or right-of-way (R/W) difficulties, etc.

2.7  Installation of reel-end splices on loaded lines [When loaded lines are determined by RUS to be economically feasible and the overall system design complies with the Modernization Plan (7 CFR 1751, Subpart B)] which may change proposed load coil locations should be considered for re-routing.  Because of the limited deviations allowed in load coil spacings, all loaded lines should be constructed first, starting at the central office and advancing in the direction of the loaded line in a continuous operation to the last load point on each loaded section unless otherwise specified in the contract.  Deviations from this procedure should be approved in lieu of holding up the construction project in the event of late cable deliveries,  or R/W difficulties, etc.

2.8  Sequential markings on the outer jackets of cables are provided to facilitate proper spacing of digital carrier or lightwave repeater housings, load coils [When loaded lines are determined by RUS to be economically feasible and the overall system design complies with the Modernization Plan (7 CFR 1751, Subpart B)], but should not be used for the inventory of cable units.  The inventory of aerial cable units should be based on span length measurements.  The resident engineer and the contractor should agree on the inventory of aerial plant units as they are installed.  Construction drawings should be appropriately marked so they can be used as permanent records of all plant items.

2.9  Aerial splices and cases for filled copper cables should be inspected to verify that:

a.  Jackets have been properly prepared;

b.  Conductors have been properly spliced;

c.  Shields have been bonded and grounded; and

d.  Aerial splice cases have been properly installed.

2.10  Aerial splices and filled aerial cases for filled fiber optic and filled, self-supporting fiber optic cables should be inspected to verify that:

a.  Jackets have been properly prepared;

b.  Optical fibers have been properly spliced;

c.  Buffer tubes containing the optical fibers have a

sufficient amount of slack;

d.  Armors of armored, filled fiber optic cables have been

bonded and grounded;

e.  Encapsulating compounds have been properly mixed and

applied; and

f.  Aerial filled splice cases have been properly installed.

2.11  Ready-access cases and fixed count and pole mounted terminals for filled copper cables should be inspected to verify that:

a.  Jackets have been properly prepared;

b.  Cable conductors have been properly spliced;

c.  Cable shields have been bonded and grounded;

d.  Aerial service wires have been properly terminated; and

e.  Ready-access cases and fixed count and pole mounted

terminals have been properly installed.

2.12  Construction drawings should be accurately marked to indicate the following:

a.  Routing of cables;

b.  Class and length of each pole;

c.  Location of each pole and anchor;

d.  Pole numbers;

e.  Span lengths;

f.  Suspension strand size for each copper or fiber

optic cable;

g.  Lengths, pair sizes, gauges, and types of copper cables;

h.  Lengths, number and types of optical fibers, and types

of fiber optic cables;

i.  Locations of aerial splice cases, fixed count or pole

mounted terminals;

j.  Locations of slack splicing loops and aerial filled

splice cases for fiber optic cables;

k.  Final sag and tension of copper or fiber optic cables;

l.  Separation in feet or meters between telecommunications

cables and foreign cables (such power, coax, etc.) on

joint occupancy construction;

m.  Locations of load coils [When loaded lines are

determined by RUS to be economically feasible and the

overall system design complies with the Modernization

Plan (7 CFR 1751, Subpart B)];

n.  Locations of digital carrier or lightwave repeater

housings; and

o.  Locations of other aerial utilities or obstacles.

This should facilitate future reinforcements which may be required on the project.

2.13  For copper cable aerial construction projects, aerial splice cases, labor, and other materials associated with the installation of reel-end splices are included in the CW assembly unit.  Therefore, such splice cases are not covered in the final inventory for compensation purposes.  Although the splice cases are not inventoried, all splice cases and cable lengths should be shown on the construction drawings for future reference.  Construction drawings should also indicate the location of all aerial splice cases that were installed for the purpose of repairing cable damage that occurred during construction.

2.14  For fiber optic cable aerial construction projects, the CO and CFO assembly units do not include filled, aerial splice cases, labor, and other materials associated with the installation of reel-end splices.  Therefore, such splice cases should be covered in the final inventory for compensation purposes.  All aerial filled splice cases and cable lengths should be shown on the construction drawings for future reference.  Construction drawings should also indicate the location of all filled, aerial splice cases that were installed for the purpose of repairing cable damage that occurred during construction.

2.15  The aerial construction route should be cleared to a width that will allow for passage of the cable and placing equipment.  The responsibilities in regards to obtaining, operating on, clearing obstructions (trees, bush, etc.), disposal of debris and restoration of public and private R/W, including any compensations are defined in RUS Bulletin 345-153, Specifications and Drawings for Construction of Pole Lines, Aerial Cables and Wires (RUS Form 515f).

2.16  In addition to the recommendations given in this bulletin, installation of the aerial plant telecommunications cables should also be performed in accordance with the requirements of the latest edition of the NESC or Federal, State, or local codes.  Where Federal, State, or local codes are more stringent than the NESC, the installation of the aerial telecommunications cables should be performed in accordance with the more stringent codes.

3.  SUSPENSION STRAND STRINGING

3.1  The suspension strand usually will be supplied on a reel.  To allow removal of the suspension strand from the reel, the reel should be supported using one of the following methods:

a.  Pay-out frames;

b.  Strand reel jacks;

c.  Strand reel hangers; or

d.  Cable reel jacks.

3.2  The suspension strand’s maximum practicable length should be payed-out in one pull.  The length of the strand payed-out using the one pull method will depend on the following items:

a.  Changes in grade;

b.  Interference from trees, other cables, etc.; or

c.  The number of corners and the corner angles.

3.3  When cutting of the suspension strand is required for placement of the strand, first wrap a double layer of friction tape around the strand for a length of 3.0 in. (76 mm) to prevent the spreading of individual strand wires and/or flying of metal particles.  Then cut the stand at the mid-point along the tape.  The strand should be cut using either a strand cutter or a hacksaw.  Other methods and safety precautions for cutting the suspension strand may be used provided agreement is obtained between the contractor and resident engineer.

3.4  Factory splices in the strand from the manufacturer are be marked with a band of paint in accordance with 7 CFR 1755.370, RUS Specification for Seven Wire Galvanized Steel Strand.  Such splices should not be bent around strand connectors, eye bolts, or at small radius bends.

3.5  Stringing of suspension strands for lashed filled copper or fiber optic cables should begin only after the guying of utility poles has been completed in a section of line.

3.6  The suspension strands should be placed on utility poles using one of the following methods:

a.  Raising the strand from ground level up to the

suspension clamps on the poles.  This method should be

used when no obstructions exist such as cables, guys,

trees, etc.;

b.  Placement of strand through the strand grooves of the

suspension clamps.  The clamp nuts should be tightened

only enough to hold the strand in the clamp groove.

This is to avoid binding of the strand during the

pull-in or tensioning operation;

c.  Placement of strand over the nut which is between the

suspension clamp and the pole.  The strand should be

placed in the clamp groove at every fifth or sixth pole

in straight sections of line and also where there is a

high point or a dip.  The clamps where the strand is

placed in the grooves should have the clamp nuts

tightened as stated in Item b of Paragraph 3.6; or

d.  Placement of strand over drive hooks or nails driven

into the poles at or below the expected height of the

cable through bolts.  If hooks are used, the hooks

should be driven into the poles leaving only space

enough between the hooks and the poles to permit

slipping the strand in the hooks.  As stated in Item

c of Paragraph 3.6, the strand should be placed in

the clamps at every fifth or sixth pole.  The hooks

should be removed after the through bolts have been

placed and the strand has been placed in the clamps.

3.7  Where it is necessary to place the suspension strand above secondary power wires (not primaries), above guy wires to a power line on separate poles, or over highways, the strand should be installed between the poles using the rope method.  This method consists of installing a rope containing rope loops or cable rings between the poles.  The suspension strand is then placed in loops or rings to support the strand between the poles.  The diameter of the rope should not be less than 0.5 in. (13.0 mm).  The rope between the poles should remain in place until the strand has been tensioned and deadended.

3.8  Where there is a possibility of the strand coming in contact with the power wires during stringing or tensioning, the strand should be held in place with ropes having diameters equal to or greater than 0.37 in. (9.4 mm).

3.9  Where a cable diminishes in size and a smaller size of suspension strand could be used for the smaller cable it is more practical to continue to string the larger size strand rather than make a strand connection to the smaller size strand, if the extension beyond the diminishing point is equal to or less than 1,000 ft (305 m).  A false deadend should be placed on the larger strand size and guyed as shown on Guide Drawing 211 of RUS Bulletin 345-153 (RUS Form 515f).

3.10  The stringing of the suspension strand on joint occupancy poles should be performed in accordance with the latest edition of the NESC.

4.  SUSPENSION STRAND SPLICES

4.1  Two methods are available for splicing suspension strands.  The first method uses guy clamps and strand connectors.  The guy clamp method is shown on Guide Drawing 204 of RUS Bulletin

345-153 (RUS Form 515f).

4.2  The second method uses terminating devices that are rated to develop the strength of the appropriate suspension strand being used in the construction project.  These devices are available in sizes for splicing two strands of the same size and for splicing 6M to 10M strands or 10M to 16M strands.  These terminating devices should be used over the clamp method because the devices eliminate the cutting and clamping of lashing wires at strand splices.  These devices are also more economical from the standpoint of material and labor costs.

4.3  Splicing of support strands of filled, self-supporting fiber optic cables should be made using insulated automatic type splicing sleeves.  It is important that only enough insulation be removed from the support member to properly install the splicing sleeves.

5.  SUSPENSION STRAND TENSIONING

5.1  The ambient air temperature at the time of strand tensioning should not be taken in direct sunlight because the hot sunlight will increase the strand temperature above that in an adjacent shaded area.  The tension required for the shade temperature, if applied to the strand at the hotter temperature, will result in some tension increase when the strand cools.  However, this has been taken into consideration in the sag and tension tables.

5.2  The initial strand tension required depends on the suspension strand size, the temperature at which the strand is tensioned, and on the average span length.  There is a definite tension for each strand size for each average span length at each temperature. The initial tension and sag data for the installation of only the 6M, 10M, and 16M Extra High Strength Galvanized Steel (EHS) suspension strands at various temperatures and average span lengths are given in Tables 1, 2, and 3.

| TABLE 1 6M EHS Suspension Strand Initial Installation Tensions and Sags |
| --- |
| Installation Temperature °F |
|  | 0 | 20 | 40 | 60 | 80 | 100 |
| Span Length Ft | Tension Sag lbf in. | Tension Sag lbf in. | Tension Sag lbf in. | Tension Sag lbf in. | Tension Sag lbf in. | Tension Sag lbf in. |
| 100 150 | 1390 1 1388 3 | 1290 1 1292 3 | 1197 2 1196 3 | 1100 2 1100 4 | 999 2 1001 4 | 898 2 902 4 |
| 200 250 | 1385 5 1380 8 | 1290 5 1288 9 | 1195 6 1194 9 | 1100 6 1100 10 | 1002 7 1004 11 | 905 8 910 12 |
| 300 350 | 1375 11 1369 16 | 1285 13 1281 17 | 1192 14 1190 19 | 1100 14 1100 20 | 1006 16 1008 22 | 915 18 920 24 |
| 400 450 | 1364 21 1357 27 | 1277 23 1271 29 | 1188 24 1186 31 | 1100 26 1100 33 | 1012 21 1015 36 | 925 32 931 39 |
| 500 550 | 1349 34 1342 41 | 1265 36 1260 43 | 1182 39 1179 46 | 1100 42 1100 50 | 1018 45 1020 53 | 936 48 942 58 |
| 600 650 | 1334 49 1328 57 | 1253 52 1248 61 | 1175 55 1172 65 | 1100 59 1100 69 | 1024 63 1028 73 | 947 67 954 71 |
| 700 750 | 1322 67 1316 78 | 1245 71 1242 83 | 1171 76 1170 88 | 1100 80 1100 93 | 1031 86 1033 99 | 961 92 969 105 |

| TABLE 2 10M EHS Suspension Strand Initial Installation Tensions and Sags |
| --- |
| Installation Temperature °F |
|  | 0 | 20 | 40 | 60 | 80 | 100 |
| Span Length Ft | Tension Sag lbf in. | Tension Sag lbf in. | Tension Sag lbf in. | Tension Sag lbf in. | Tension Sag lbf in. | Tension Sag lbf in. |
| 100 150 | 2476 1 2471 3 | 2320 1 2316 3 | 2163 1 2161 3 | 2000 1 2000 3 | 1833 2 1836 4 | 1665 2 1671 4 |
| 200 250 | 2466 5 2461 8 | 2312 5 2308 8 | 2159 6 2156 9 | 2000 6 2000 10 | 1839 7 1842 10 | 1683 7 1683 11 |
| 300 350 | 2456 11 2450 15 | 2303 12 2298 16 | 2153 13 2149 17 | 2000 14 2000 19 | 1845 15 1848 20 | 1689 16 1696 22 |
| 400 450 | 2442 20 2432 26 | 2293 21 2287 27 | 2145 23 2142 29 | 2000 25 2000 31 | 1851 27 1854 34 | 1703 28 1710 36 |
| 500 550 | 2422 32 2412 38 | 2281 33 2274 41 | 2139 36 2136 43 | 2000 38 2000 46 | 1858 41 1862 50 | 1717 45 1724 53 |
| 600 650 | 2402 46 2392 54 | 2267 48 2260 57 | 2133 51 2130 62 | 2000 55 2000 65 | 1866 59 1870 69 | 1732 64 1740 74 |
| 700 750 | 2382 63 2372 72 | 2253 67 2246 77 | 2127 71 2123 81 | 2000 75 2000 86 | 1874 80 1879 92 | 1749 86 1759 98 |
| 800 850 900 | 2362 83 2351 94 2340 107 | 2239 88 2232 99 2225 112 | 2119 93 2115 105 2111 110 | 2000 98 2000 111 2000 125 | 1884 105 1889 117 1894 131 | 1769 111 1779 124 1790 139 |

| TABLE 3 16M EHS Suspension Strand Initial Installation Tensions and Sags |
| --- |
| Installation Temperature °F |
|  | 0 | 20 | 40 | 60 | 80 | 100 |
| Span Length ft | Tension Sag lbf in. | Tension Sag lbf in. | Tension Sag lbf in. | Tension Sag lbf in. | Tension Sag lbf in. | Tension Sag lbf in. |
| 100 150 | 4666 1 4661 3 | 4380 1 4376 3 | 4093 1 4091 3 | 3800 2 3800 3 | 3494 2 3497 4 | 3181 2 3186 4 |
| 200 250 | 4655 5 4648 8 | 4372 5 4367 8 | 4089 6 4087 9 | 3800 6 3800 10 | 3500 7 3504 11 | 3192 7 3199 11 |
| 300 350 | 4639 12 4629 16 | 4361 12 4354 17 | 4084 13 4080 18 | 3800 14 3800 19 | 3508 15 3513 21 | 3207 17 3217 23 |
| 400 450 | 4617 21 4603 26 | 4346 22 4337 28 | 4076 23 4071 30 | 3800 25 3800 32 | 3518 27 3524 34 | 3229 29 3242 37 |
| 500 550 | 4588 33 4572 39 | 4327 35 4317 41 | 4066 37 4060 44 | 3800 39 3800 47 | 3530 42 3536 51 | 3256 46 3271 54 |
| 600 650 | 4555 47 4537 56 | 4303 50 4291 59 | 4054 53 4047 63 | 3800 57 3800 67 | 3544 60 3552 71 | 3287 65 3304 76 |
| 700 750 | 4518 65 4498 74 | 4278 68 4264 78 | 4040 72 4032 82 | 3800 77 3800 87 | 3560 82 3569 93 | 3321 88 3339 99 |
| 800 850 | 4477 85 4455 97 | 4249 90 4233 102 | 4024 95 4015 108 | 3800 100 3800 114 | 3578 106 3588 120 | 3358 113 3379 127 |
| 900 950 1000 | 4432 109 4408 122 4383 137 | 4216 115 4199 129 4181 143 | 4006 121 3996 135 3986 150 | 3800 127 3800 142 3800 158 | 3598 134 3609 149 3621 165 | 3401 142 3424 157 3448 173 |

5.3  Tables 4, 5, and 6 indicate the maximum span length for 6M, 10M, and 16M EHS suspension strands with aerial cable lashed to the suspension strands for each storm loading district as defined in the latest edition of the NESC.

| TABLE 4 Maximum Span Lengths by Loading Districts 6M EHS Strand with Aerial Cable Lashed to Strand |
| --- |
| Cable Weight Lb/ft (kg/m) | Maximum Span Lengths ft (m) Heavy Medium Light |
| 0.2 (0.3) 0.4 (0.6) 0.6 (0.9) 0.8 (1.2) 1.0 (1.5) | 500 (152) 400 (122) 325 (99) 300 (91) 250 (76) | 750 (229) 600 (183) 475 (145) 425 (129) 375 (114) | 750 (229) 725 (221) 575 (175) 500 (152) 425 (129) |
| 1.2 (1.8) 1.4 (2.1) 1.6 (2.4) 1.8 (2.7) 2.0 (3.0) | 225 (68) 225 (68) 200 (61) 200 (61) 175 (53) | 325 (99) 300 (91) 275 (84) 250 (76) 225 (68) | 375 (114) 350 (107) 300 (91) 300 (91) 275 (84) |

| TABLE 5 Maximum Span Lengths by Loading Districts 10M EHS Strand with Aerial Cable Lashed to Strand |
| --- |
| Cable Weight Lb/ft (kg/m) | Maximum Span Lengths ft (m) Heavy Medium Light |
| 0.4 (0.6) 0.6 (0.9) 0.8 (1.2) 1.0 (1.5) | 625 (190) 550 (168) 475 (145) 425 (129) | 800 (244) 750 (229) 675 (206) 600 (183) | 900 (274) 875 (267) 775 (236) 700 (213) |
| 1.2 (1.8) 1.4 (2.1) 1.6 (2.4) 1.8 (2.7) 2.0 (3.0) | 400 (122) 350 (107) 325 (99) 300 (91) 300 (91) | 550 (168) 500 (152) 450 (137) 425 (129) 400 (122) | 625 (190) 575 (175) 525 (160) 475 (145) 450 (137) |
| 2.2 (3.3) 2.4 (3.6) 2.6 (3.9) 2.8 (4.2) 3.0 (4.5) | 275 (84) 275 (84) 250 (76) 250 (76) 225 (68) | 375 (114) 350 (107) 325 (99) 300 (91) 300 (91) | 425 (129) 400 (122) 375 (114) 350 (107) 325 (99) |
| 3.2 (4.8) 3.4 (5.0) 3.6 (5.3) 3.8 (5.6) 4.0 (5.9) | 225 (68) 200 (61) 200 (61) 200 (61) 175 (53) | 275 (84) 275 (84) 250 (76) 250 (76) 225 (68) | 325 (99) 325 (99) 275 (84) 275 (84) 250 (76) |
| 4.2 (6.2) 4.4 (6.5) 4.6 (6.8) 4.8 (7.1) 5.0 (7.4) | 175 (53) 175 (53) 175 (53) 175 (53) 150 (46) | 225 (68) 225 (68) 200 (61) 200 (61) 200 (61) | 250 (76) 250 (76) 225 (68) 225 (68) 225 (68) |

| TABLE 6 Maximum Span Lengths by Loading Districts 16M EHS Strand with Aerial Cable Lashed to Strand |
| --- |
| Cable Weight lb/ft (kg/m) | Maximum Span Lengths ft (m) Heavy Medium Light |
| 1.0 (1.5) 1.5 (2.2) 2.0 (3.0) 2.5 (3.7) | 750 (229) 625 (190) 575 (175) 475 (145) | 1000 (305) 825 (251) 700 (213) 600 (183) | 1000 (305) 925 (282) 775 (236) 675 (206) |
| 3.0 (4.5) 3.5 (5.2) 4.0 (5.9) 4.5 (6.7) 5.0 (7.4) | 425 (129) 375 (114) 350 (107) 325 (99) 300 (91) | 525 (160) 450 (137) 425 (129) 375 (114) 350 (107) | 575 (175) 525 (160) 475 (145) 425 (129) 375 (114) |

5.4  A dynamometer should be used rather than sag measurements in suspension strand tensioning because strand sag is difficult to accurately measure.  Shunt type dynamometers are more useful than tension type dynamometers because the shunt type dynamometers can also be used to test the tension of the strand after the strand as been installed.  Dynamometer measurements should be made in accordance with the manufacturer’s instructions.  Tension readings should made as indicated in Figure 1.  The oscillation method for determining the strand tension should not be used.

5.5  The suspension strand should be tensioned using either a strand puller attached to a winch line or by a block and tackle.  The tension should be slowly applied while the entire length of the strand being installed is observed for evidence of snagging or failure to slip through its temporary attachments at poles.  The strand puller jaws should be kept free of oil, grease, etc. to prevent slippage.

5.6  The strand should be anchored at a deadend pole before the first section of strand is tensioned and terminated by the use of boltless guy clamps.  Successive pulls should be made from the end of the first pull.  If there is a possibility that the strand and cable may be extended beyond a deadend pole, a 3 ft (1 m) tail of suspension strand should be left beyond the deadend pole to allow for extension of the strand using a strand sleeve. A 6.0 in. (152 mm) suspension strand tail should be left at all other locations.  The ends of the suspension strand tails should be secured using either stainless lashing wire wrapped around the strand or by guy wire clips.  Guy wire clips are available in sizes to fit 6M, 10M, and 16M EHS suspension strands.

5.7  Dampers to protect the suspension strand from fatigue failure should be used when the cable is not immediately installed.  For this purpose a piece of bridle wire may be installed along the top of the suspension clamp and wrapped around the strand extending 2 ft (607 mm) in both directions with the ends of the bridle wire sealed.  Other methods of protecting the strand from fatigue failure may be used if allowed by the borrower.

6.  CABLE INSTALLATION AND LASHING

6.1  Direct lashing of filled copper or fiber optic cables to suspension strands should be accomplished by either the moving reel or stationary reel method.

6.2  The moving reel method consists of a cable reel trailer and a towing vehicle.  This method is preferred over the stationary reel method because of its faster installation time.  This method should be used when the terrain along the side of the pole line on which the cable is to be installed is free of obstructions such as trees, guys, etc., which would prevent raising the cable to the strand.  When using this method the pulling tension and bending radius of filled fiber optic cables should be in accordance with the manufacturer’s recommendations.  If not specified by the fiber optic cable manufacturer, the maximum pulling tension should not exceed 600 lbf (2,669 N) and minimum bending radius should not be less than 20 times the outside diameter of the cable.  Also when using this method, the bending radius of filled copper cables should be in accordance with the manufacturer’s recommendations.  If not specified by the copper cable manufacturer, the minimum bending radius should not be less than 10 times the outside cable diameter.  Figure 2 depicts the moving reel method of installation.

6.3  The stationary reel method, which is depicted in Figure 3, consists of a cable reel, a suitable device for supporting the cable reel, and rollers attached to the strand to support the cable during the installation.  When using the stationary reel method the pulling tension and bending radius of filled fiber optic cables and the bending radius of filled copper cables should be in accordance with Paragraph 6.2.  Rollers used in the stationary reel method should be installed on the strand at various spacings depending on the weight of the cable.  The roller spacing versus the cable weight that should be used with the stationary reel method is given in Table 7.  Rollers should also be installed at all bends in excess of 45 degrees from normal.

| TABLE 7 Roller Spacing Versus Cable Weight |
| --- |
| Cable Weight lb/ft (kg/m) | Maximum Spacing ft (m) |
| 1.0 (1.5) or less 1.5 (2.2) 2.0 (3.0) 2.5 (3.7) 3.0 (4.5) 3.5 (5.2) 4.0 (5.9) 4.5 (6.7) 5.0 (7.4) and greater | 35 (10.7) 33 (10.0) 25 (7.6) 20 (6.1) 16 (4.9) 14 (4.3) 12 (3.6) 10 (3.0) 8 (2.5) |

6.4  The cable should be pulled over the rollers in the stationary reel method using either a winch line, wire rope approximately 0.25 in. (6.4 mm) in diameter, or manila rope approximately 0.5 in. (12.7 mm) in diameter.

6.5  Because filled fiber optic cables are typically manufactured and installed in longer lengths than filled copper cables, special consideration should be given to reel placement to eliminate the need of figure-eighting the cable and a series of mid-assist pulls for both the moving and stationary reel installation methods.

6.6  Lashing machines are manufactured in several sizes.  The size of the lashing machine used on the construction project should be based on the outside diameter of the cable to be installed on the project.  The lashing machine should wrap the lashing wire around the cable and suspension strand in the counterclockwise direction.  Where grades in construction are encountered, the lashing of the cable to the strand should be performed in the downhill direction.

6.7  Stainless steel lashing wire should be used to lash cables to the suspension strand on aerial plant construction projects.  The diameter of the lashing wire used on the construction project should be based on the outside diameter and weight of the cable to be installed and the size of the lashing machine.

6.8  Two types of lashing wire clamps are necessary in lashing cables to strands.  The first type is a temporary clamp having a handle for opening and closing the clamp jaws.  The second type is known as the permanent clamp.  Temporary clamps are removed after the permanent clamps are installed.  Guide drawings in RUS Bulletin 345-153 (RUS Form 515f) show how lashing wires are clamped in various situations.  Lashing wire should be clamped at each side of each utility pole.

6.9  Lashing wires should be spliced using stainless steel compression sleeves for the appropriate sizes.

6.10  When filled copper or fiber optic cables are lashed at temperatures below 30°F (-1.1°C), the cables should be tensioned more than is usual at higher temperatures.  This should prevent bowing in hot weather by causing cables to be lashed snugly against the strand.

6.11  When required because of construction constraints, etc., two filled copper or fiber optic cables may be lashed to the same suspension strand or a new filled copper or fiber optic cable may be lashed over an existing cable to the same strand.  The combined diameters of the two cables can not exceed the diameter for which the lashing machine was designed.

6.12  In order to promote firm lashing when lashing two filled copper or fiber optic cables to the same strand, the diameter of first cable should not be more than twice the diameter of the second cable.

6.13  If the diameter of a filled copper cable or of two filled copper cables exceeds 2.0 in. (51 mm), two nuts should be placed between the suspension clamp and washer to provide clearance between the pole and cables.

6.14  Before lashing new filled copper or fiber optic cable to an existing cable on the same strand, the existing lashing wire should be examined for corrosion, pitting, breakage, sharp points or edges, etc. which could damage the new cable during installation.  If the existing lashing wire is found to be severely corroded or pitted, broken, or containing sharp points

or edges, the existing lashing wire should be removed before installation of the new cable.  However, it is generally not necessary to remove the existing lashing wire.

7.  SELF-SUPPORTING, FILLED, FIBER OPTIC CABLE INSTALLATION

7.1  Installation of self-supporting, filled, fiber optic cables should begin only after the guying of utility poles has been completed in a section of line.

7.2  Self-supporting, filled, fiber optic cables should be installed using the moving reel method whenever possible.  The cable should be placed in stringing rollers on the poles where it should remain during the remainder of the placing and tensioning operations.  When using this installation method the maximum pulling tension and minimum bend radius of the self-supporting, filled, fiber optic cable should not exceed the manufacturer’s recommendations.

7.3  Where it is necessary, because of physical obstructions, to install self-supporting, filled, fiber optic cables using the stationary reel method, cables should be strung through rollers under a sufficient amount of tension to avoid excessive bending and to prevent cables from contacting the ground or obstructions between poles.  The rollers should be spaced as indicated in Table 7 of Paragraph 6.3.  When using this installation method the maximum pulling tension and minimum bend radius of the self-supporting, filled fiber optic cable should not exceed the manufacturer’s recommendations.  Care should be exercised to prevent continuous spiraling occurring in self-supporting, filled fiber optic cables when installed using the stationary reel method.  Since the cable is spiraled by hand from alternate poles after the cable has been tensioned, any existing spirals in the cable would be increased in one span and removed in the adjacent span.  It would then be very difficult to obtain a uniform number of spirals in every span.

7.4  Self-supporting, filled, fiber optic cables should be tensioned with the aid of series dynamometers.  The cable should be temporarily supported at each pole in rollers until after the cable has been tensioned and the tensioned equalized in all spans of the section being tensioned.  Tension should be applied slowly while the entire length of cable being installed is observed for evidence of snagging or failure to move freely through its temporary supports at the poles.

7.5  The initial stringing tension for self-supporting, filled, fiber optic cables will depend on the size of its support strand, the size of cable core, the NESC storm loading district for the construction project, the maximum permissible span length, temperature at the time of tensioning, and the cable manufacturer’s recommendations.

7.6  When tensioning self-supporting, filled, fiber optic cables, the insulation over the support strand should not be damaged.  Tensioning by means of grips placed over the insulated support strand is the preferred method, provided that the tensioning can be accomplished without rupturing the insulation.

7.7  The initial sags and tensions for self-supporting, filled, fiber optic cables installed at various span lengths and temperatures in the three NESC storm loading districts should be obtained from the fiber optic cable manufacturer.

8.  SAG AND TENSION OF INSTALLED FILLED CABLES

8.1  The sag and tension in a strand and a filled copper or fiber optic cable after their installation depends on the installation temperature, strand size, cable weight on a per foot basis, and the span length.  The above information is known as the “initial” cable sag and tension.

8.2  The initial sags and tensions for filled copper cables installed on 6M, 10M, and 16M EHS suspension strands at various span lengths and temperatures are given in Tables 8 through 50.

| TABLE 8 Initial Sag and Tension 6M EHS Suspension Strand Supporting Cable Weighing 0.2 lb/ft for Heavy, Medium, and Light Loading Districts |
| --- |
| Installation Temperature °F |
|  | 0 | 20 | 40 | 60 | 80 | 100 |
| Span Length ft | Tension Sag lbf in. | Tension Sag lbf in. | Tension Sag lbf in. | Tension Sag lbf in. | Tension Sag lbf in. | Tension Sag lbf in. |
| 100 125 150 175 | 1409 3 1415 5 1423 8 1435 11 | 1317 4 1326 6 1337 8 1352 12 | 1222 4 1232 6 1246 9 1263 12 | 1127 4 1138 7 1154 10 1175 13 | 1032 5 1046 7 1064 10 1088 14 | 936 5 956 8 980 11 1005 15 |
| 200 225 250 275 | 1448 14 1462 18 1476 22 1490 26 | 1366 15 1382 18 1382 22 1414 27 | 1280 16 1298 20 1317 24 1336 28 | 1196 17 1217 21 1239 26 1261 30 | 1113 19 1137 23 1161 27 1184 32 | 1030 20 1056 24 1082 30 1107 34 |
| 300 325 350 375 | 1505 30 1521 34 1536 39 1553 45 | 1431 31 1447 36 1466 41 1484 47 | 1355 33 1374 38 1393 43 1413 49 | 1282 35 1303 40 1325 46 1347 51 | 1207 37 1230 43 1253 48 1276 54 | 1132 39 1157 45 1184 51 1209 57 |
| 400 425 450 475 | 1569 50 1586 56 1604 62 1621 69 | 1503 52 1522 58 1541 65 1559 71 | 1432 55 1453 61 1472 68 1493 74 | 1467 58 1388 64 1410 71 1431 78 | 1299 60 1323 67 1346 74 1369 81 | 1235 63 1261 70 1286 77 1311 85 |
| 500 525 550 575 | 1639 75 1657 82 1677 88 1695 95 | 1578 78 1597 85 1615 92 1634 99 | 1513 81 1533 88 1554 95 1574 103 | 1453 85 1474 92 1495 99 1515 107 | 1392 88 1414 96 1437 103 1459 111 | 1336 92 1360 100 1384 107 1407 115 |
| 600 625 650 675 | 1713 103 1730 111 1746 119 1763 127 | 1653 107 1671 115 1689 123 1707 131 | 1594 111 1614 119 1633 127 1653 135 | 1536 115 1556 123 1576 132 1596 140 | 1482 119 1504 128 1525 136 1546 145 | 1430 124 1453 132 1475 141 1497 150 |
| 700 725 750 | 1779 135 1795 144 1811 152 | 1725 140 1743 148 1759 157 | 1672 144 1690 153 1708 162 | 1616 149 1636 158 1656 167 | 1567 154 1586 163 1605 172 | 1518 159 1539 168 1559 178 |

| TABLE 9 Initial Sag and Tension 6M EHS Suspension Strand Supporting Cable Weighing 0.4 lb/ft for Heavy, Medium, and Light Loading Districts |
| --- |
| Installation Temperature °F |
|  | 0 | 20 | 40 | 60 | 80 | 100 |
| Span Length ft | Tension Sag lbf in. | Tension Sag lbf in. | Tension Sag lbf in. | Tension Sag lbf in. | Tension Sag lbf in. | Tension Sag lbf in. |
| 100 125 150 175 | 1430 5 1455 8 1482 12 1510 16 | 1344 6 1372 9 1402 12 1432 17 | 1258 6 1288 9 1319 13 1352 18 | 1169 7 1203 10 1239 14 1275 19 | 1080 7 1119 11 1160 15 1201 20 | 994 8 1037 12 1082 16 1127 21 |
| 200 225 250 275 | 1540 20 1570 25 1602 31 1635 37 | 1464 21 1497 26 1531 32 1566 38 | 1386 23 1423 28 1461 33 1499 40 | 1313 24 1353 29 1393 35 1434 41 | 1243 25 1285 31 1328 37 1371 43 | 1172 27 1218 32 1264 38 1309 45 |
| 300 325 350 375 | 1668 43 1703 49 1737 56 1773 63 | 1602 44 1638 51 1675 58 1712 65 | 1537 46 1576 53 1614 60 1652 67 | 1474 48 1515 55 1555 62 1594 70 | 1413 50 1455 57 1496 65 1537 72 | 1353 52 1397 60 1441 67 1483 75 |
| 400 425 450 475 | 1809 70 1843 77 1875 85 1909 93 | 1751 72 1786 80 1821 88 1855 96 | 1692 75 1728 83 1764 91 1799 99 | 1635 77 1672 85 1709 94 1745 102 | 1578 80 1617 88 1655 97 1692 105 | 1525 83 1565 91 1604 100 1643 109 |
| 500 525 550 575 | 1943 101 1975 110 2007 119 2039 128 | 1889 104 1922 113 1955 122 1988 132 | 1834 108 1868 116 1903 126 1936 135 | 1782 111 1817 120 1852 129 1886 139 | 1729 114 1766 123 1802 133 1837 143 | 1680 118 1717 127 1754 137 1790 146 |
| 600 625 650 675 | 2071 138 2102 147 2133 157 2163 167 | 2020 141 2053 151 2084 161 2116 171 | 1970 145 2003 154 2035 164 2067 175 | 1921 149 1955 159 1988 169 2021 179 | 1873 153 1907 163 1941 173 1975 183 | 1825 156 1860 168 1895 177 1929 188 |
| 700 725 | 2194 177 2224 187 | 2147 181 2177 191 | 2099 185 2131 195 | 2053 189 2086 200 | 2008 194 2041 205 | 1963 198 1997 209 |

| TABLE 10 Initial Sag and Tension 6M EHS Suspension Strand Supporting Cable Weighing 0.6 lb/ft for Heavy, Medium, and Light Loading Districts |
| --- |
| Installation Temperature °F |
|  | 0 | 20 | 40 | 60 | 80 | 100 |
| Span Length ft | Tension Sag lbf in. | Tension Sag lbf in. | Tension Sag lbf in. | Tension Sag lbf in. | Tension Sag lbf in. | Tension Sag lbf in. |
| 100 125 150 175 | 1473 7 1520 12 1567 17 1615 23 | 1386 8 1437 13 1489 18 1540 24 | 1306 8 1359 13 1414 19 1467 25 | 1225 9 1283 14 1341 20 1398 26 | 1142 10 1205 15 1267 21 1327 27 | 1062 10 1128 16 1194 22 1257 28 |
| 200 225 250 275 | 1663 28 1711 34 1758 40 1806 46 | 1592 29 1643 35 1694 41 1744 48 | 1521 30 1574 36 1629 43 1681 49 | 1454 32 1511 38 1566 44 1621 51 | 1387 33 1447 40 1504 46 1563 53 | 1321 35 1383 41 1444 48 1506 55 |
| 300 325 350 375 | 1853 53 1901 61 1948 69 1996 77 | 1794 55 1844 63 1892 71 1943 79 | 1676 59 1728 67 1782 75 1833 83 | 1648 68 1701 69 1756 76 1808 85 | 1619 61 1674 71 1729 77 1782 86 | 1566 63 1621 73 1676 80 1732 88 |
| 400 425 450 475 | 2044 85 2091 94 2138 103 2186 112 | 1992 88 2039 96 2087 106 2135 115 | 1939 90 1986 99 2035 108 2084 118 | 1886 92 1935 102 1986 111 2036 121 | 1835 95 1886 104 1938 114 1988 124 | 1785 98 1837 107 1890 117 1941 127 |
| 500 525 550 575 | 2233 122 2278 132 2323 142 2367 153 | 2182 125 2228 135 2275 145 2320 156 | 2132 128 2179 138 2227 149 2273 159 | 2085 131 2133 141 2182 152 2228 162 | 2039 134 2087 144 2136 155 2184 166 | 1993 137 2041 147 2090 158 2140 170 |

| TABLE 11 Initial Sag and Tension 6M EHS Suspension Strand Supporting Cable Weighing 0.8 lb/ft for Heavy, Medium, and Light Loading Districts |
| --- |
| Installation Temperature °F |
|  | 0 | 20 | 40 | 60 | 80 | 100 |
| Span Length ft | Tension Sag lbf in. | Tension Sag lbf in. | Tension Sag lbf in. | Tension Sag lbf in. | Tension Sag lbf in. | Tension Sag lbf in. |
| 100 125 150 175 | 1520 9 1585 13 1648 19 1712 24 | 1442 10 1510 14 1577 19 1643 26 | 1362 10 1434 15 1505 20 1575 27 | 1284 11 1360 16 1435 21 1509 28 | 1207 11 1287 16 1365 22 1443 29 | 1133 12 1218 17 1302 23 1380 30 |
| 200 225 250 275 | 1775 31 1837 38 1899 46 1963 54 | 1709 32 1775 39 1842 47 1907 55 | 1644 33 1713 41 1782 49 1849 57 | 1582 35 1653 42 1725 50 1793 59 | 1518 36 1594 44 1668 52 1741 60 | 1455 37 1540 45 1618 54 1692 62 |
| 300 325 350 375 | 2026 62 2089 71 2151 79 2213 88 | 1973 64 2038 72 2102 81 2164 91 | 1917 66 1983 74 2049 83 2113 93 | 1863 67 1931 76 1999 86 2065 95 | 1811 69 1882 78 1950 88 2017 97 | 1761 71 1834 81 1903 90 1970 100 |
| 400 425 450 475 500 | 2275 98 2334 107 2394 117 2453 128 2512 139 | 2227 100 2288 110 2347 120 2407 131 2466 141 | 2178 103 2241 112 2300 123 2360 133 2419 144 | 2131 105 2194 115 2225 125 2322 136 2375 147 | 2083 107 2147 117 2210 128 2271 139 2331 150 | 2036 110 2100 120 2163 131 2225 142 2287 153 |

| TABLE 12 Initial Sag and Tension 6M EHS Suspension Strand Supporting Cable Weighing 1.0 lb/ft for Heavy, Medium, and Light Loading Districts |
| --- |
| Installation Temperature °F |
|  | 0 | 20 | 40 | 60 | 80 | 100 |
| Span Length ft | Tension Sag lbf in. | Tension Sag lbf in. | Tension Sag lbf in. | Tension Sag lbf in. | Tension Sag lbf in. | Tension Sag lbf in. |
| 100 125 150 175 | 1567 11 1650 16 1733 21 1814 28 | 1492 11 1579 16 1664 22 1747 29 | 1419 12 1510 17 1598 23 1685 30 | 1351 12 1443 18 1534 24 1623 31 | 1278 13 1375 19 1470 25 1564 33 | 1211 14 1310 20 1408 26 1504 34 |
| 200 225 250 275 | 1895 35 1974 43 2052 51 2128 60 | 1831 36 1912 44 1992 53 2070 62 | 1770 38 1854 46 1937 54 2018 64 | 1712 39 1800 47 1889 56 1967 65 | 1656 40 1745 49 1832 58 1915 67 | 1599 42 1691 50 1781 59 1867 69 |
| 300 325 350 375 | 2204 70 2277 79 2351 89 2424 99 | 2148 71 2225 81 2301 91 2375 101 | 2098 73 2176 83 2253 93 2328 103 | 2048 75 2132 85 2205 95 2281 105 | 1998 77 2079 87 2158 97 2235 108 | 1951 79 2033 89 2113 99 2191 110 |
| 400 425 | 2495 109 2566 120 | 2449 112 2521 122 | 2402 114 2476 125 | 2356 116 2431 127 | 2311 118 2386 129 | 2267 121 2343 132 |

| TABLE 13 Initial Sag and Tension 6M EHS Suspension Strand Supporting Cable Weighing 1.2 lb/ft for Heavy, Medium, and Light Loading Districts |
| --- |
| Installation Temperature °F |
|  | 0 | 20 | 40 | 60 | 80 | 100 |
| Span Length ft | Tension Sag lbf in. | Tension Sag lbf in. | Tension Sag lbf in. | Tension Sag lbf in. | Tension Sag lbf in. | Tension Sag lbf in. |
| 100 125 150 175 | 1625 12 1722 18 1818 24 1912 32 | 1554 13 1654 18 1754 25 1852 33 | 1492 13 1588 19 1692 26 1793 34 | 1415 14 1525 20 1632 27 1735 35 | 1348 15 1461 21 1570 28 1678 36 | 1283 16 1398 22 1511 29 1621 37 |
| 200 225 250 275 | 2005 40 2097 48 2189 57 2279 66 | 1949 41 2043 49 2137 58 2229 68 | 1892 42 1988 51 2085 60 2179 69 | 1837 43 1934 52 2033 61 2130 71 | 1782 44 1882 53 1982 63 2080 73 | 1731 46 1833 55 1934 65 2033 74 |
| 300 325 350 375 | 2369 76 2457 86 2545 96 2629 107 | 2321 77 2410 88 2498 98 2583 109 | 2273 79 2363 89 2452 100 2536 111 | 2224 81 2315 91 2406 102 2492 113 | 2175 83 2268 93 2359 104 2446 115 | 2128 85 2221 95 2312 106 2400 117 |

| TABLE 14 Initial Sag and Tension 6M EHS Suspension Strand Supporting Cable Weighing 1.4 lb/ft for Heavy, Medium, and Light Loading Districts |
| --- |
| Installation Temperature °F |
|  | 0 | 20 | 40 | 60 | 80 | 100 |
| Span Length ft | Tension Sag lbf in. | Tension Sag lbf in. | Tension Sag lbf in. | Tension Sag lbf in. | Tension Sag lbf in. | Tension Sag lbf in. |
| 100 125 150 175 | 1682 14 1793 20 1903 27 2012 35 | 1613 14 1727 20 1841 28 1953 36 | 1547 15 1665 21 1782 29 1897 37 | 1483 15 1605 22 1725 30 1844 38 | 1418 16 1544 23 1669 31 1789 39 | 1353 17 1483 24 1611 32 1735 40 |
| 200 225 250 275 | 2120 43 2225 52 2329 62 2431 72 | 2064 44 2171 53 2277 63 2381 73 | 2010 46 2120 55 2227 65 2333 75 | 1960 47 2071 56 2180 66 2286 76 | 1907 48 2020 57 2130 67 2239 78 | 1854 49 1970 59 2082 69 2192 79 |
| 300 325 350 | 2532 82 2630 93 2727 103 | 2483 84 2583 94 2681 105 | 2436 85 2537 96 2636 107 | 2390 87 2494 98 2592 109 | 2344 88 2447 99 2547 111 | 2299 90 2402 101 2502 113 |

| TABLE 15 Initial Sag and Tension 6M EHS Suspension Strand Supporting Cable Weighing 1.6 lb/ft for Heavy, Medium, and Light Loading Districts |
| --- |
| Installation Temperature °F |
|  | 0 | 20 | 40 | 60 | 80 | 100 |
| Span Length ft | Tension Sag lbf in. | Tension Sag lbf in. | Tension Sag lbf in. | Tension Sag lbf in. | Tension Sag lbf in. | Tension Sag lbf in. |
| 100 125 150 175 | 1742 15 1867 21 1992 29 2114 37 | 1676 15 1804 22 1933 30 2058 38 | 1610 16 1742 23 1874 31 2002 39 | 1547 17 1684 24 1818 32 1950 40 | 1484 17 1628 25 1766 33 1900 42 | 1425 18 1572 26 1711 34 1848 43 |
| 200 225 250 275 300 | 2235 46 2353 56 2470 66 2582 76 2692 87 | 2183 47 2302 57 2419 67 2533 78 2644 89 | 2130 49 2252 58 2371 68 2487 79 2600 90 | 2080 50 2202 59 2323 70 2440 81 2555 92 | 2030 51 2153 61 2275 71 2394 82 2510 94 | 1982 53 2109 63 2231 73 2348 84 2465 95 |

| TABLE 16 Initial Sag and Tension 6M EHS Suspension Strand Supporting Cable Weighing 1.8 lb/ft for Heavy, Medium, and Light Loading Districts |
| --- |
| Installation Temperature °F |
|  | 0 | 20 | 40 | 60 | 80 | 100 |
| Span Length ft | Tension Sag lbf in. | Tension Sag lbf in. | Tension Sag lbf in. | Tension Sag lbf in. | Tension Sag lbf in. | Tension Sag lbf in. |
| 100 125 150 175 | 1800 16 1944 23 2085 31 2221 40 | 1737 17 1884 24 2027 32 2166 41 | 1678 17 1826 24 1971 33 2114 42 | 1616 18 1768 25 1914 34 2060 43 | 1556 19 1710 26 1860 35 2008 44 | 1497 19 1654 27 1808 36 1857 45 |
| 200 225 250 275 300 | 2352 49 2479 59 2604 70 2724 81 2843 92 | 2302 50 2433 60 2559 71 2680 82 2800 94 | 2251 51 2384 61 2512 72 2635 83 2755 95 | 2199 52 2334 63 2464 74 2590 85 2711 96 | 2150 54 2287 64 2419 75 2545 86 2668 98 | 2101 55 2241 66 2375 77 2501 88 2626 100 |

| TABLE 17 Initial Sag and Tension 6M EHS Suspension Strand Supporting Cable Weighing 2.0 lb/ft for Heavy, Medium, and Light Loading Districts |
| --- |
| Installation Temperature °F |
|  | 0 | 20 | 40 | 60 | 80 | 100 |
| Span Length ft | Tension Sag lbf in. | Tension Sag lbf in. | Tension Sag lbf in. | Tension Sag lbf in. | Tension Sag lbf in. | Tension Sag lbf in. |
| 100 125 150 175 | 1861 17 2011 24 2160 33 2307 42 | 1799 18 1954 25 2108 34 2257 43 | 1738 18 1897 26 2054 35 2207 44 | 1680 19 1843 27 2002 36 2158 45 | 1622 20 1789 28 1952 37 2110 46 | 1566 20 1736 29 1902 38 2062 47 |
| 200 225 250 275 | 2452 52 2593 63 2730 74 2862 84 | 2406 53 2549 64 2686 75 2820 86 | 2358 54 2504 65 2642 76 2776 88 | 2311 55 2457 66 2596 77 2732 89 | 2264 57 2411 67 2551 79 2688 91 | 2218 58 2365 69 2506 80 2645 92 |

| TABLE 18 Initial Sag and Tension 10M EHS Suspension Strand Supporting Cable Weighing 0.4 lb/ft for Heavy, Medium, and Light Loading Districts |
| --- |
| Installation Temperature °F |
|  | 0 | 20 | 40 | 60 | 80 | 100 |
| Span Length ft | Tension Sag lbf in. | Tension Sag lbf in. | Tension Sag lbf in. | Tension Sag lbf in. | Tension Sag lbf in. | Tension Sag lbf in. |
| 100 125 150 175 | 2503 4 2524 6 2547 9 2571 12 | 2355 4 2379 7 2405 10 2433 13 | 2200 4 2229 7 2260 10 2293 14 | 2046 4 2079 8 2115 11 2151 15 | 1891 5 1929 8 1968 12 2088 16 | 1733 5 1776 9 1819 13 1863 17 |
| 200 225 250 275 | 2596 16 2622 19 2648 23 2674 27 | 2461 17 2489 20 2518 24 2547 28 | 2323 18 2355 21 2386 26 2419 30 | 2185 19 2221 23 2256 27 2291 32 | 2047 20 2087 24 2125 29 2163 33 | 1907 21 1951 25 1995 30 2038 35 |
| 300 325 350 375 | 2700 31 2727 36 2758 40 2787 45 | 2578 33 2607 38 2640 42 2674 48 | 2453 35 2486 39 2520 44 2558 50 | 2327 37 2365 42 2401 47 2443 52 | 2203 38 2244 44 2283 49 2329 55 | 2082 41 2126 46 2170 52 2215 57 |
| 400 425 450 475 | 2820 51 2853 57 2885 64 2918 70 | 2709 54 2743 60 2776 66 2810 73 | 2596 56 2633 62 2664 69 2705 75 | 2484 58 2524 65 2563 72 2602 79 | 2372 61 2414 68 2455 74 2493 82 | 2260 64 2305 71 2350 78 2394 85 |
| 500 525 550 575 | 2951 77 2983 84 3016 92 3049 99 | 2844 80 2879 87 2913 95 2947 102 | 2740 83 2778 90 2814 98 2849 106 | 2639 86 2678 94 2716 101 2754 110 | 2537 89 2578 97 2618 105 2659 113 | 2437 93 2479 101 2522 109 2565 117 |
| 600 625 650 675 | 3082 107 3115 114 3149 122 3179 130 | 2982 110 3016 118 3051 126 3084 134 | 2886 114 2918 122 2955 130 2988 139 | 2791 118 2827 126 2865 134 2901 143 | 2697 122 2736 130 2776 139 2815 147 | 2608 126 2651 135 2692 143 2731 152 |
| 700 725 750 775 | 3210 139 3241 147 3272 156 3303 165 | 3117 143 3150 151 3183 161 3217 170 | 3023 147 3058 156 3093 165 3128 175 | 2937 151 2974 160 3011 170 3047 180 | 2853 156 2891 165 2929 175 2966 184 | 2771 161 2809 170 2847 180 2885 190 |
| 800 825 850 875 900 | 3335 175 3366 185 3397 195 3429 205 3461 215 | 3251 180 3284 190 3317 200 3351 210 3382 220 | 3167 185 3201 195 3235 205 3265 215 3302 226 | 3085 189 3120 200 3154 210 3189 221 3223 231 | 3004 195 3040 205 3076 215 3115 226 3147 237 | 2923 200 2961 210 2998 221 3035 232 3071 243 |

| TABLE 19 Initial Sag and Tension 10M EHS Suspension Strand Supporting Cable Weighing 0.6 lb/ft for Heavy, Medium, and Light Loading Districts |
| --- |
| Installation Temperature °F |
|  | 0 | 20 | 40 | 60 | 80 | 100 |
| Span Length ft | Tension Sag lbf in. | Tension Sag lbf in. | Tension Sag lbf in. | Tension Sag lbf in. | Tension Sag lbf in. | Tension Sag lbf in. |
| 100 125 150 175 | 2533 5 2571 8 2610 11 2648 15 | 2390 5 2432 8 2475 12 2520 15 | 2240 5 2287 9 2336 12 2386 15 | 2089 6 2142 9 2197 13 2250 16 | 1941 6 1999 10 2057 14 2116 17 | 1790 7 1853 11 1916 15 1980 17 |
| 200 225 250 275 | 2691 19 2734 23 2776 28 2818 33 | 2565 20 2609 24 2655 29 2700 34 | 2434 21 2483 25 2531 31 2581 36 | 2303 22 2356 27 2409 32 2461 38 | 2173 23 2231 28 2286 34 2342 39 | 2042 25 2105 30 2166 35 2226 41 |
| 300 325 350 375 | 2861 38 2905 43 2952 48 2998 55 | 2747 40 2793 45 2842 51 2891 57 | 2631 41 2680 47 2730 53 2783 59 | 2514 43 2567 49 2619 55 2676 62 | 2398 45 2455 51 2510 58 2570 64 | 2287 47 2347 54 2406 60 2466 67 |
| 400 425 450 475 | 3046 62 3094 69 3141 76 3188 83 | 2941 64 2990 71 3038 78 3087 86 | 2835 66 2887 73 2934 81 2989 89 | 2731 69 2785 76 2839 84 2892 92 | 2657 71 2684 79 2739 86 2791 95 | 2524 74 2583 82 2641 90 2698 98 |
| 500 525 550 575 | 3236 91 3283 99 3331 107 3378 116 | 3136 94 3186 102 3234 110 3282 119 | 3039 97 3091 105 3141 114 3190 122 | 2944 100 2997 108 3049 117 3101 126 | 2848 103 2903 112 2957 120 3012 130 | 2755 106 2811 115 2867 124 2923 133 |
| 600 625 650 675 | 3424 124 3470 133 3517 142 3559 151 | 3331 128 3378 137 3425 146 3470 155 | 3240 131 3287 140 3336 150 3381 159 | 3151 135 3201 144 3251 154 3299 163 | 3063 139 3115 148 3167 158 3217 167 | 2979 143 3034 152 3087 162 3137 172 |
| 700 725 750 775 | 3602 160 3645 170 3687 180 3729 190 | 3515 164 3560 174 3604 184 3648 194 | 3426 168 3474 178 3519 188 3564 199 | 3346 173 3394 182 3441 192 3487 203 | 3266 177 3315 187 3363 197 3410 208 | 3188 181 3237 192 3286 202 3333 213 |
| 800 825 850 875 | 3775 201 3813 211 3855 222 3898 233 | 3692 205 3735 216 3779 227 3824 238 | 3612 209 3656 220 3701 231 3743 243 | 3534 214 3580 225 3624 236 3670 248 | 3458 219 3504 230 3550 241 3598 253 | 3381 224 3429 235 3475 247 3522 258 |

| TABLE 20 Initial Sag and Tension 10M EHS Suspension Strand Supporting Cable Weighing 0.8 lb/ft for Heavy, Medium, and Light Loading Districts |
| --- |
| Installation Temperature °F |
|  | 0 | 20 | 40 | 60 | 80 | 100 |
| Span Length ft | Tension Sag lbf in. | Tension Sag lbf in. | Tension Sag lbf in. | Tension Sag lbf in. | Tension Sag lbf in. | Tension Sag lbf in. |
| 100 125 150 175 | 2563 6 2618 9 2673 13 2727 17 | 2425 6 2485 9 2545 13 2607 18 | 2280 6 2345 10 2412 14 2479 20 | 2132 7 2205 11 2279 15 2349 20 | 1991 8 2069 12 2146 16 2224 21 | 1847 8 1930 12 2013 17 2097 23 |
| 200 225 250 275 | 2786 21 2846 27 2904 32 2962 38 | 2669 23 2729 28 2792 34 2853 40 | 2545 24 2611 29 2676 35 2743 41 | 2421 25 2491 31 2562 37 2631 43 | 2299 27 2375 33 2447 39 2521 45 | 2177 28 2259 34 2337 40 2414 47 |
| 300 325 350 375 | 3022 44 3083 51 3136 58 3209 65 | 2916 46 2979 53 3044 60 3108 67 | 2809 48 2874 55 2940 62 3008 69 | 2701 50 2769 57 2837 64 2909 72 | 2593 52 2666 59 2737 66 2811 74 | 2492 54 2568 61 2642 69 2717 76 |
| 400 425 450 475 | 3272 72 3335 80 3397 88 3458 96 | 3173 74 3237 82 3300 90 3364 99 | 3074 77 3141 85 3204 93 3273 102 | 2978 79 3046 87 3115 96 3182 105 | 2912 82 2954 90 3023 98 3089 107 | 2788 84 2861 93 2932 101 3002 110 |
| 500 525 550 575 | 3521 105 3583 114 3646 123 3707 133 | 3428 108 3493 117 3555 126 3617 136 | 3338 111 3404 120 3468 129 3531 139 | 3248 114 3316 123 3382 132 3448 142 | 3159 117 3228 126 3296 136 3365 146 | 3073 120 3143 129 3212 139 3281 149 |
| 600 625 650 675 | 3766 142 3825 152 3885 162 3939 172 | 3680 145 3740 155 3799 165 3856 175 | 3594 149 3656 159 3717 169 3774 179 | 3511 152 3575 162 3637 173 3697 183 | 3429 156 3494 166 3558 177 3619 187 | 3350 160 3417 170 3482 181 3443 191 |
| 700 725 750 775 | 3994 182 4049 192 4102 203 4155 214 | 3913 186 3970 196 4025 207 4079 218 | 3829 190 3890 200 3945 211 4000 223 | 3755 194 3814 204 3874 216 3927 227 | 3679 198 3739 209 3797 220 3854 231 | 3605 202 3665 213 3725 225 3781 236 |

| TABLE 21 Initial Sag and Tension 10M EHS Suspension Strand Supporting Cable Weighing 1.0 lb/ft for Heavy, Medium, and Light Loading Districts |
| --- |
| Installation Temperature °F |
|  | 0 | 20 | 40 | 60 | 80 | 100 |
| Span Length ft | Tension Sag lbf in. | Tension Sag lbf in. | Tension Sag lbf in. | Tension Sag lbf in. | Tension Sag lbf in. | Tension Sag lbf in. |
| 100 125 150 175 | 2593 7 2664 10 2736 14 2809 19 | 2459 7 2537 11 2615 15 2694 20 | 2319 8 2404 11 2488 16 2572 21 | 2176 8 2268 12 2360 17 2449 23 | 2040 9 2138 13 2236 19 2331 24 | 1903 10 2008 14 2111 20 2213 25 |
| 200 225 250 275 | 2882 24 2957 30 3031 37 3107 44 | 2772 26 2850 32 2928 39 3007 45 | 2655 27 2739 33 2822 40 2904 47 | 2538 29 2627 35 2714 42 2801 49 | 2425 30 2518 37 2609 44 2699 51 | 2313 32 2412 39 2509 46 2602 53 |
| 300 325 350 375 | 3183 51 3261 58 3340 66 3419 74 | 3086 53 3166 60 3246 68 3326 77 | 2987 55 3069 62 3151 70 3232 79 | 2887 57 2971 64 3056 73 3141 81 | 2789 59 2877 67 2965 75 3052 83 | 2698 61 2789 69 2878 77 2967 86 |
| 400 425 450 475 | 3497 83 3575 91 3652 100 3729 109 | 3405 85 3484 94 3563 103 3641 112 | 3313 87 3394 96 3475 105 3556 115 | 3225 90 3308 97 3390 108 3471 117 | 3138 92 3223 101 3307 111 3388 120 | 3053 95 3139 104 3224 113 3306 123 |
| 500 525 550 575 | 3807 119 3883 129 3960 139 4035 149 | 3720 122 3799 132 3877 142 3953 152 | 3636 124 3716 135 3795 145 3873 156 | 3553 127 3634 138 3715 148 3794 159 | 3471 130 3554 141 3636 151 3717 162 | 3391 133 3475 144 3558 154 3640 165 |
| 600 625 650 675 700 | 4108 160 4180 170 4252 181 4319 192 4387 203 | 4029 163 4101 174 4174 185 4243 196 4312 207 | 3949 166 4024 177 4099 188 4168 199 4237 211 | 3872 170 3948 181 4024 192 4094 203 4164 215 | 3795 173 3873 184 3950 196 4021 207 4093 218 | 3720 176 3799 188 3876 199 3949 211 4022 223 |

| TABLE 22 Initial Sag and Tension 10M EHS Suspension Strand Supporting Cable Weighing 1.2 lb/ft for Heavy, Medium, and Light Loading Districts |
| --- |
| Installation Temperature °F |
|  | 0 | 20 | 40 | 60 | 80 | 100 |
| Span Length ft | Tension Sag lbf in. | Tension Sag lbf in. | Tension Sag lbf in. | Tension Sag lbf in. | Tension Sag lbf in. | Tension Sag lbf in. |
| 100 125 150 175 | 2639 8 2727 11 2816 16 2905 21 | 2508 8 2603 12 2698 17 2793 22 | 2372 9 2474 13 2576 18 2675 23 | 2234 9 2343 14 2452 19 2555 25 | 2102 10 2217 15 2332 20 2442 26 | 1970 11 2093 16 2212 21 2328 27 |
| 200 225 250 275 | 2993 27 3082 34 3170 41 3259 48 | 2886 28 2978 35 3070 42 3163 50 | 2773 30 2872 36 2968 44 3064 51 | 2661 31 2764 38 2865 46 2965 53 | 2551 33 2659 40 2764 47 2867 55 | 2443 34 2556 41 2667 49 2773 57 |
| 300 325 350 375 | 3349 56 3440 64 3531 72 3622 81 | 3255 57 3348 65 3440 74 3532 83 | 3160 59 3254 68 3349 76 3442 85 | 3064 61 3160 69 3257 78 3354 87 | 2969 63 3069 72 3169 80 3367 89 | 2880 65 2983 73 3084 82 3184 92 |
| 400 425 450 475 | 3712 89 3801 98 3889 108 3977 118 | 3623 92 3714 101 3803 110 3892 120 | 3534 94 3627 103 3719 113 3809 123 | 3449 96 3542 106 3636 115 3727 125 | 3364 99 3460 108 3555 118 3646 128 | 3282 101 3379 111 3475 121 3567 131 |
| 500 525 550 575 | 4064 128 4149 138 4235 149 4318 160 | 3980 130 4069 141 4155 152 4239 163 | 3899 133 3988 144 4076 155 4161 166 | 3818 136 3908 147 3998 158 4085 169 | 3739 139 3831 150 3921 161 4009 172 | 3661 142 3753 153 3845 164 3934 176 |
| 600 625 | 4399 171 4479 182 | 4322 174 4403 186 | 4245 177 4328 189 | 4170 181 4255 192 | 4095 184 4181 196 | 4022 187 4109 199 |

| TABLE 23 Initial Sag and Tension 10M EHS Suspension Strand Supporting Cable Weighing 1.4 lb/ft for Heavy, Medium, and Light Loading Districts |
| --- |
| Installation Temperature °F |
|  | 0 | 20 | 40 | 60 | 80 | 100 |
| Span Length ft | Tension Sag lbf in. | Tension Sag lbf in. | Tension Sag lbf in. | Tension Sag lbf in. | Tension Sag lbf in. | Tension Sag lbf in. |
| 100 125 150 175 | 2685 9 2791 13 2896 18 3001 23 | 2557 9 2670 13 2782 19 2892 24 | 2425 10 2545 14 2664 19 2779 25 | 2292 10 2418 15 2544 21 2661 27 | 2164 11 2296 16 2428 22 2553 28 | 2038 12 2178 17 2313 23 2444 29 |
| 200 225 250 275 | 3104 30 3207 37 3309 44 3412 52 | 3000 31 3107 38 3213 46 3319 54 | 2892 32 3005 39 3115 47 3224 55 | 2784 34 2901 41 3016 49 3129 57 | 2677 35 2800 43 2919 51 3035 59 | 2573 37 2700 44 2825 52 2944 61 |
| 300 325 350 375 | 3515 60 3619 69 3722 78 3825 88 | 3424 62 3530 71 3634 80 3739 89 | 3333 64 3439 73 3547 82 3652 91 | 3241 66 3349 75 3458 84 3567 93 | 3149 68 3261 77 3373 86 3482 95 | 3062 69 3178 78 3290 88 3401 97 |
| 400 425 450 475 | 3927 96 4027 106 4126 116 4225 126 | 3841 98 3944 108 4043 118 4143 129 | 3755 101 3861 110 3963 121 4062 131 | 3673 103 3777 113 3882 123 3983 134 | 3590 105 3697 115 3803 126 3905 136 | 3511 107 3619 118 3725 128 3828 139 |
| 500 525 550 575 | 4321 137 4416 148 4510 159 4601 171 | 4211 139 4339 150 4433 162 4525 174 | 4162 142 4260 153 4357 165 4449 177 | 4084 144 4183 156 4281 167 4376 180 | 4007 147 4108 159 4206 170 4302 182 | 3931 150 4032 161 4132 173 4229 186 |

| TABLE 24 Initial Sag and Tension 10M EHS Suspension Strand Supporting Cable Weighing 1.6 lb/ft for Heavy, Medium, and Light Loading Districts |
| --- |
| Installation Temperature °F |
|  | 0 | 20 | 40 | 60 | 80 | 100 |
| Span Length ft | Tension Sag lbf in. | Tension Sag lbf in. | Tension Sag lbf in. | Tension Sag lbf in. | Tension Sag lbf in. | Tension Sag lbf in. |
| 100 125 150 175 | 2731 9 2855 14 2976 19 3097 25 | 2606 10 2737 15 2866 20 2991 27 | 2479 11 2616 15 2752 21 2883 27 | 2350 11 2493 16 2636 22 2768 29 | 2227 12 2375 17 2524 23 2664 30 | 2106 13 2263 18 2414 24 2560 31 |
| 200 225 250 275 | 3215 32 3332 40 3448 48 3565 56 | 3114 34 3236 41 3356 49 3475 58 | 3011 35 3138 42 3262 51 3384 60 | 2907 36 3038 44 3167 53 3293 61 | 2803 38 2941 46 3074 54 3203 63 | 2703 39 2844 47 2983 56 3115 65 |
| 300 325 350 375 | 3681 65 3798 74 3914 83 4028 93 | 3594 67 3712 76 3828 85 3946 95 | 3506 68 3625 78 3745 87 3862 97 | 3418 70 3538 80 3659 89 3780 99 | 3330 72 3454 82 3577 91 3697 101 | 3245 74 3373 83 3496 93 3619 103 |
| 400 425 450 475 | 4142 103 4253 113 4364 124 4473 135 | 4059 105 4174 115 4284 126 4394 137 | 3976 107 4095 118 4207 128 4315 139 | 3897 109 4012 120 4128 131 4239 142 | 3817 112 3935 122 4051 133 4164 144 | 3740 114 3859 125 3977 136 4090 147 |
| 500 525 | 4579 146 4683 157 | 4502 148 4609 160 | 4425 150 4533 162 | 4350 153 4458 165 | 4275 156 4385 168 | 4201 158 4311 170 |

| TABLE 25 Initial Sag and Tension 10M EHS Suspension Strand Supporting Cable Weighing 1.8 lb/ft for Heavy, Medium, and Light Loading Districts |
| --- |
| Installation Temperature °F |
|  | 0 | 20 | 40 | 60 | 80 | 100 |
| Span Length ft | Tension Sag lbf in. | Tension Sag lbf in. | Tension Sag lbf in. | Tension Sag lbf in. | Tension Sag lbf in. | Tension Sag lbf in. |
| 100 125 150 175 | 2778 10 2919 15 3057 21 3193 28 | 2656 11 2804 16 2950 22 3090 29 | 2533 12 2687 17 2840 23 2987 30 | 2409 12 2569 18 2729 24 2875 31 | 2290 13 2454 19 2621 25 2775 32 | 2174 14 2349 19 2515 26 2676 33 |
| 200 225 250 275 | 3326 35 3457 43 3588 52 3718 61 | 3228 36 3365 44 3499 53 3631 62 | 3130 37 3271 46 3409 55 3545 64 | 3030 39 3176 47 3319 56 3458 65 | 2930 40 3082 49 3229 58 3371 67 | 2833 41 2989 50 3141 59 3286 69 |
| 300 325 350 375 | 3848 70 3977 79 4106 89 4232 99 | 3764 71 3894 81 4023 91 4153 101 | 3679 73 3811 83 3943 93 4072 103 | 3595 75 3728 85 3861 95 3993 105 | 3511 77 3647 87 3781 97 3913 107 | 3428 78 3568 88 3703 99 3837 109 |
| 400 425 450 475 | 4357 110 4480 121 4602 132 4721 143 | 4278 112 4404 123 4525 134 4645 145 | 4198 114 4329 125 4451 136 4569 147 | 4121 116 4247 127 4374 139 4495 150 | 4044 118 4173 130 4300 141 4423 152 | 3969 120 4099 132 4229 143 4351 155 |

| TABLE 26 Initial Sag and Tension 10M EHS Suspension Strand Supporting Cable Weighing 2.0 lb/ft for Heavy, Medium, and Light Loading Districts |
| --- |
| Installation Temperature °F |
|  | 0 | 20 | 40 | 60 | 80 | 100 |
| Span Length ft | Tension Sag lbf in. | Tension Sag lbf in. | Tension Sag lbf in. | Tension Sag lbf in. | Tension Sag lbf in. | Tension Sag lbf in. |
| 100 125 150 175 | 2825 11 2983 17 3138 23 3289 30 | 2706 12 2871 17 3034 24 3190 31 | 2587 13 2758 18 2928 24 3091 32 | 2468 13 2645 19 2822 25 2982 33 | 2353 14 2534 20 2718 26 2887 34 | 2242 15 2435 21 2617 28 2792 35 |
| 200 225 250 275 | 3437 38 3583 46 3728 55 3871 65 | 3343 39 3494 47 3642 57 3788 66 | 3249 40 3404 49 3556 58 3706 68 | 3153 41 3314 50 3471 60 3623 69 | 3057 43 3224 52 3385 61 3540 71 | 2963 44 3134 53 3300 63 3457 73 |
| 300 325 350 375 | 4015 75 4157 85 4298 95 4436 106 | 3934 76 4076 86 4218 97 4360 107 | 3853 78 3997 88 4141 98 4283 109 | 3773 79 3918 90 4063 100 4206 111 | 3692 81 3840 92 3986 102 4129 113 | 3611 83 3763 93 3910 104 4055 115 |
| 400 425 450 | 4573 117 4707 128 4840 140 | 4497 119 4635 130 4766 142 | 4420 121 4563 132 4695 144 | 4345 123 4482 134 4620 146 | 4271 125 4411 137 4549 149 | 4199 127 4340 139 4481 151 |

| TABLE 27 Initial Sag and Tension 10M EHS Suspension Strand Supporting Cable Weighing 2.2 lb/ft for Heavy, Medium, and Light Loading Districts |
| --- |
| Installation Temperature °F |
|  | 0 | 20 | 40 | 60 | 80 | 100 |
| Span Length ft | Tension Sag lbf in. | Tension Sag lbf in. | Tension Sag lbf in. | Tension Sag lbf in. | Tension Sag lbf in. | Tension Sag lbf in. |
| 100 125 150 175 | 2879 12 3052 18 3221 24 3385 32 | 2763 13 2942 18 3119 25 3288 33 | 2646 13 2832 19 3014 26 3190 34 | 2530 14 2721 20 2910 27 3085 35 | 2418 15 2613 21 2808 28 2991 36 | 2309 15 2514 22 2709 29 2897 37 |
| 200 225 250 275 | 3546 40 3704 49 3861 58 4015 68 | 3454 41 3617 50 3776 59 3934 69 | 3361 42 3528 51 3692 61 3853 71 | 3267 43 3440 52 3608 62 3772 72 | 3173 45 3352 54 3524 64 3690 74 | 3082 46 3264 55 3441 65 3608 75 |
| 300 325 350 375 | 4169 78 4322 88 4473 99 4620 110 | 4090 79 4243 90 4395 101 4546 112 | 4011 81 4166 91 4319 102 4469 114 | 3933 83 4088 93 4242 104 4394 116 | 3852 84 4011 95 4167 106 4319 118 | 3773 86 3935 97 4092 108 4246 120 |
| 400 425 | 4765 121 4908 133 | 4692 123 4837 135 | 4616 125 4765 137 | 4543 127 4687 139 | 4470 129 4617 142 | 4399 131 4547 144 |

| TABLE 28 Initial Sag and Tension 10M EHS Suspension Strand Supporting Cable Weighing 2.4 lb/ft for Heavy, Medium, and Light Loading Districts |
| --- |
| Installation Temperature °F |
|  | 0 | 20 | 40 | 60 | 80 | 100 |
| Span Length ft | Tension Sag lbf in. | Tension Sag lbf in. | Tension Sag lbf in. | Tension Sag lbf in. | Tension Sag lbf in. | Tension Sag lbf in. |
| 100 125 150 175 | 2933 13 3121 19 3304 26 3482 33 | 2820 14 3013 20 3204 26 3386 34 | 2705 14 2906 20 3101 27 3290 35 | 2592 15 2797 21 2999 28 3188 36 | 2483 15 2692 22 2899 29 3095 38 | 2377 16 2594 23 2801 30 3003 39 |
| 200 225 250 275 | 3655 42 3826 51 3994 61 4159 71 | 3565 43 3740 52 3911 62 4080 72 | 3473 44 3652 53 3828 63 4000 73 | 3381 45 3566 55 3745 65 3921 75 | 3289 47 3480 56 3663 66 3840 77 | 3201 48 3395 57 3582 68 3759 78 |
| 300 325 350 375 400 | 4324 81 4487 92 4648 103 4804 114 4958 126 | 4247 83 4411 93 4573 104 4732 116 4887 128 | 4169 84 4335 95 4498 106 4655 118 4812 130 | 4093 86 4258 97 4423 108 4582 120 4741 132 | 4012 87 4182 98 4348 110 4509 122 4669 134 | 3935 89 4107 100 4274 112 4438 124 4599 136 |

| TABLE 29 Initial Sag and Tension 10M EHS Suspension Strand Supporting Cable Weighing 2.6 lb/ft for Heavy, Medium, and Light Loading Districts |
| --- |
| Installation Temperature °F |
|  | 0 | 20 | 40 | 60 | 80 | 100 |
| Span Length ft | Tension Sag lbf in. | Tension Sag lbf in. | Tension Sag lbf in. | Tension Sag lbf in. | Tension Sag lbf in. | Tension Sag lbf in. |
| 100 125 150 175 | 2987 14 3190 20 3387 27 3579 35 | 2877 14 3085 21 3289 28 3484 36 | 2764 15 2980 21 3188 29 3390 37 | 2654 16 2873 22 3088 30 3291 38 | 2548 16 2771 23 2990 31 3199 39 | 2445 17 2674 24 2894 32 3109 40 |
| 200 225 250 275 | 3765 44 3948 53 4127 63 4304 74 | 3676 45 3863 55 4046 65 4226 75 | 3585 46 3776 56 3964 66 4147 77 | 3495 47 3693 57 3883 67 4070 78 | 3406 49 3609 58 3802 69 3990 79 | 3320 50 3526 60 3723 70 3911 82 |
| 300 325 350 375 | 4479 84 4652 95 4823 107 4988 119 | 4404 86 4579 97 4751 108 4918 120 | 4328 87 4504 99 4677 110 4842 122 | 4253 89 4428 100 4603 112 4770 124 | 4173 91 4353 102 4530 114 4699 126 | 4097 92 4279 104 4456 116 4630 128 |

| TABLE 30 Initial Sag and Tension 10M EHS Suspension Strand Supporting Cable Weighing 2.8 lb/ft for Heavy, Medium, and Light Loading Districts |
| --- |
| Installation Temperature °F |
|  | 0 | 20 | 40 | 60 | 80 | 100 |
| Span Length ft | Tension Sag lbf in. | Tension Sag lbf in. | Tension Sag lbf in. | Tension Sag lbf in. | Tension Sag lbf in. | Tension Sag lbf in. |
| 100 125 150 175 | 3042 15 3259 21 3471 29 3676 37 | 2935 15 3157 22 3374 29 3588 38 | 2824 16 3054 23 3275 30 3490 39 | 2717 16 2950 23 3177 31 3394 40 | 2613 17 2850 24 3081 32 3303 41 | 2513 18 2754 25 2987 33 3215 42 |
| 200 225 250 275 | 3875 46 4070 56 4260 66 4449 77 | 3787 47 3986 57 4181 67 4372 78 | 3697 48 3901 58 4100 69 4295 79 | 3610 49 3820 59 4021 70 4219 81 | 3523 51 3738 61 3942 71 4140 82 | 3439 52 3657 62 3864 73 4062 84 |
| 300 325 350 | 4634 88 4817 99 4999 111 | 4561 89 4747 101 4929 112 | 4487 91 4673 102 4856 114 | 4413 92 4599 104 4783 116 | 4334 94 4524 105 4712 118 | 4259 95 4451 107 4638 119 |

| TABLE 31 Initial Sag and Tension 10M EHS Suspension Strand Supporting Cable Weighing 3.0 lb/ft for Heavy, Medium, and Light Loading Districts |
| --- |
| Installation Temperature °F |
|  | 0 | 20 | 40 | 60 | 80 | 100 |
| Span Length ft | Tension Sag lbf in. | Tension Sag lbf in. | Tension Sag lbf in. | Tension Sag lbf in. | Tension Sag lbf in. | Tension Sag lbf in. |
| 100 125 150 175 | 3097 15 3329 22 3555 30 3773 39 | 2993 16 3229 23 3459 31 3682 40 | 2884 17 3128 24 3362 32 3590 41 | 2780 17 3027 24 3266 33 3497 42 | 2679 18 2930 25 3172 34 3408 43 | 2581 19 2834 26 3080 35 3321 44 |
| 200 225 250 275 | 3985 48 4192 58 4393 69 4594 80 | 3898 49 4109 59 4316 70 4519 81 | 3810 50 4026 61 4237 71 4443 82 | 3725 51 3947 62 4159 73 4368 84 | 3640 53 3867 63 4082 74 4290 85 | 3558 54 3788 64 4005 75 4215 87 |
| 300 325 | 4789 91 4983 103 | 4718 92 4915 104 | 4646 94 4843 106 | 4573 95 4770 107 | 4495 97 4696 109 | 4421 98 4623 110 |

| TABLE 32 Initial Sag and Tension 10M EHS Suspension Strand Supporting Cable Weighing 3.2 lb/ft for Heavy, Medium, and Light Loading Districts |
| --- |
| Installation Temperature °F |
|  | 0 | 20 | 40 | 60 | 80 | 100 |
| Span Length ft | Tension Sag lbf in. | Tension Sag lbf in. | Tension Sag lbf in. | Tension Sag lbf in. | Tension Sag lbf in. | Tension Sag lbf in. |
| 100 125 150 175 | 3154 16 3398 23 3636 31 3864 40 | 3051 17 3300 24 3542 32 3776 41 | 2944 17 3202 25 3448 33 3687 42 | 2842 18 3103 25 3354 34 3596 43 | 2743 18 3008 26 3262 35 3509 44 | 2646 19 2914 27 3172 36 3423 45 |
| 200 225 250 275 | 4088 50 4304 60 4516 71 4727 82 | 4003 51 4224 61 4440 72 4653 83 | 3918 52 4143 62 4363 73 4578 85 | 3834 53 4065 63 4287 75 4505 86 | 3751 54 3986 65 4210 76 4428 87 | 3670 55 3907 66 4134 77 4354 89 |
| 300 325 | 4932 94 5133 105 | 4862 95 5066 107 | 4791 96 4995 109 | 4719 98 4924 110 | 4642 99 4851 112 | 4569 101 4779 113 |

| TABLE 33 Initial Sag and Tension 10M EHS Suspension Strand Supporting Cable Weighing 3.4 lb/ft for Heavy, Medium, and Light Loading Districts |
| --- |
| Installation Temperature °F |
|  | 0 | 20 | 40 | 60 | 80 | 100 |
| Span Length ft | Tension Sag lbf in. | Tension Sag lbf in. | Tension Sag lbf in. | Tension Sag lbf in. | Tension Sag lbf in. | Tension Sag lbf in. |
| 100 125 150 175 | 3211 17 3468 24 3717 32 3956 41 | 3109 17 3372 25 3626 33 3870 42 | 3004 18 3276 25 3534 34 3784 43 | 2905 18 3179 26 3442 35 3695 44 | 2807 19 3086 27 3352 36 3610 45 | 2711 20 2994 28 3264 37 3526 46 |
| 200 225 250 275 | 4191 51 4417 62 4639 73 4860 84 | 4109 52 4339 63 4565 74 4787 86 | 4026 54 4260 64 4489 75 4714 87 | 3943 55 4183 65 4415 77 4642 88 | 3862 56 4105 66 4338 78 4566 90 | 3782 57 4027 68 4263 79 4493 91 |
| 300 325 | 5075 96 5283 108 | 5006 98 5217 110 | 4936 99 5147 111 | 4865 100 5078 113 | 4789 102 5006 114 | 4718 103 4935 116 |

| TABLE 34 Initial Sag and Tension 10M EHS Suspension Strand Supporting Cable Weighing 3.6 lb/ft for Heavy, Medium, and Light Loading Districts |
| --- |
| Installation Temperature °F |
|  | 0 | 20 | 40 | 60 | 80 | 100 |
| Span Length ft | Tension Sag lbf in. | Tension Sag lbf in. | Tension Sag lbf in. | Tension Sag lbf in. | Tension Sag lbf in. | Tension Sag lbf in. |
| 100 125 150 175 | 3269 17 3538 25 3798 33 4048 43 | 3167 18 3444 26 3710 34 3964 44 | 3065 18 3350 26 3620 35 3881 45 | 2968 19 3255 27 3530 36 3795 46 | 2871 20 3164 28 3442 37 3711 47 | 2776 20 3074 29 3357 38 3629 48 |
| 200 225 250 275 | 4294 53 4530 64 4762 75 4993 87 | 4215 54 4454 65 4690 76 4922 88 | 4134 55 4377 66 4615 77 4850 89 | 4052 56 4301 67 4543 79 4779 91 | 3973 57 4224 68 4467 80 4704 92 | 3895 58 4147 69 4392 81 4632 93 |

| TABLE 35 Initial Sag and Tension 10M EHS Suspension Strand Supporting Cable Weighing 3.8 lb/ft for Heavy, Medium, and Light Loading Districts |
| --- |
| Installation Temperature °F |
|  | 0 | 20 | 40 | 60 | 80 | 100 |
| Span Length ft | Tension Sag lbf in. | Tension Sag lbf in. | Tension Sag lbf in. | Tension Sag lbf in. | Tension Sag lbf in. | Tension Sag lbf in. |
| 100 125 150 175 | 3327 18 3608 26 3879 35 4140 44 | 3226 18 3516 27 3794 35 4059 45 | 3126 19 3424 27 3706 36 3978 46 | 3031 20 3332 28 3618 37 3895 47 | 2935 20 3243 29 3533 38 3813 48 | 2842 21 3155 29 3450 39 3732 49 |
| 200 225 250 275 | 4397 55 4643 65 4886 77 5126 89 | 4321 56 4569 67 4815 78 5057 90 | 4242 57 4494 68 4742 79 4986 92 | 4162 58 4420 69 4671 81 4916 93 | 4084 59 4343 70 4596 82 4843 94 | 4008 60 4267 71 4521 83 4771 95 |

| TABLE 36 Initial Sag and Tension 10M EHS Suspension Strand Supporting Cable Weighing 4.0 lb/ft for Heavy, Medium, and Light Loading Districts |
| --- |
| Installation Temperature °F |
|  | 0 | 20 | 40 | 60 | 80 | 100 |
| Span Length ft | Tension Sag lbf in. | Tension Sag lbf in. | Tension Sag lbf in. | Tension Sag lbf in. | Tension Sag lbf in. | Tension Sag lbf in. |
| 100 125 150 175 | 3385 19 3678 27 3960 36 4232 46 | 3285 19 3588 27 3878 37 4154 47 | 3187 20 3498 28 3793 37 4075 47 | 3093 20 3409 29 3707 38 3995 48 | 3000 21 3322 30 3624 39 3915 49 | 2908 22 3236 30 3543 40 3835 50 |
| 200 225 250 | 4500 56 4756 67 5010 79 | 4427 57 4684 68 4940 80 | 4350 58 4612 70 4869 81 | 4272 59 4539 71 4799 83 | 4195 61 4463 72 4725 84 | 4121 62 4387 73 4651 85 |

| TABLE 37 Initial Sag and Tension 10M EHS Suspension Strand Supporting Cable Weighing 4.2 lb/ft for Heavy, Medium, and Light Loading Districts |
| --- |
| Installation Temperature °F |
|  | 0 | 20 | 40 | 60 | 80 | 100 |
| Span Length ft | Tension Sag lbf in. | Tension Sag lbf in. | Tension Sag lbf in. | Tension Sag lbf in. | Tension Sag lbf in. | Tension Sag lbf in. |
| 100 125 150 175 | 3441 19 3746 27 4039 37 4322 47 | 3342 20 3656 28 3958 38 4245 48 | 3245 20 3567 29 3873 38 4166 49 | 3153 21 3479 30 3789 39 4087 49 | 3060 21 3392 30 3706 40 4008 50 | 2969 22 3306 31 3624 41 3928 51 |
| 200 225 250 | 4599 57 4865 69 5127 81 | 4526 59 4793 70 5058 82 | 4450 60 4722 71 4988 83 | 4373 61 4649 72 4919 84 | 4296 62 4574 73 4846 86 | 4222 63 4499 74 4773 87 |
| TABLE 38 Initial Sag and Tension 10M EHS Suspension Strand Supporting Cable Weighing 4.4 lb/ft for Heavy, Medium, and Light Loading Districts |
| Installation Temperature °F |
|  | 0 | 20 | 40 | 60 | 80 | 100 |
| Span Length ft | Tension Sag lbf in. | Tension Sag lbf in. | Tension Sag lbf in. | Tension Sag lbf in. | Tension Sag lbf in. | Tension Sag lbf in. |
| 100 125 150 175 | 3497 20 3814 28 4118 38 4412 48 | 3399 20 3724 29 4038 38 4336 49 | 3303 21 3636 30 3954 39 4257 50 | 3212 21 3549 30 3871 40 4179 51 | 3120 22 3462 31 3788 41 4101 51 | 3030 23 3377 32 3706 42 4022 52 |
| 200 225 250 | 4698 59 4974 70 5245 82 | 4625 60 4903 71 5176 84 | 4550 61 4832 72 5107 85 | 4474 62 4759 73 5039 86 | 4397 63 4685 75 4967 87 | 4232 64 4611 76 4895 88 |

| TABLE 39 Initial Sag and Tension 10M EHS Suspension Strand Supporting Cable Weighing 4.6 lb/ft for Heavy, Medium, and Light Loading Districts |
| --- |
| Installation Temperature °F |
|  | 0 | 20 | 40 | 60 | 80 | 100 |
| Span Length ft | Tension Sag lbf in. | Tension Sag lbf in. | Tension Sag lbf in. | Tension Sag lbf in. | Tension Sag lbf in. | Tension Sag lbf in. |
| 100 125 150 | 3553 20 3882 29 4197 38 | 3456 21 3792 30 4118 39 | 3362 21 3705 30 4035 40 | 3271 22 3619 31 3953 41 | 3181 23 3532 32 3870 42 | 3091 23 3448 32 3788 43 |
| 175 200 225 | 4502 49 4797 60 5083 72 | 4427 50 4725 61 5013 73 | 4348 51 4650 62 4942 74 | 4271 52 4575 63 4870 75 | 4194 53 4498 64 4796 76 | 4116 54 4424 65 4723 77 |

| TABLE 40 Initial Sag and Tension 10M EHS Suspension Strand Supporting Cable Weighing 4.8 lb/ft for Heavy, Medium, and Light Loading Districts |
| --- |
| Installation Temperature °F |
|  | 0 | 20 | 40 | 60 | 80 | 100 |
| Span Length ft | Tension Sag lbf in. | Tension Sag lbf in. | Tension Sag lbf in. | Tension Sag lbf in. | Tension Sag lbf in. | Tension Sag lbf in. |
| 100 125 150 | 3609 21 3950 30 4281 39 | 3514 21 3861 30 4198 40 | 3421 22 3775 31 4116 41 | 3331 23 3687 32 4038 42 | 3242 23 3603 32 3952 43 | 3152 24 3519 33 3870 43 |
| 175 200 225 | 4592 50 4897 61 5193 73 | 4518 51 4825 62 5123 74 | 4439 52 4750 63 5052 75 | 4364 53 4676 64 4981 76 | 4287 54 4600 65 4908 78 | 4210 55 4526 66 4836 79 |

| TABLE 41 Initial Sag and Tension 10M EHS Suspension Strand Supporting Cable Weighing 5.0 lb/ft for Heavy, Medium, and Light Loading Districts |
| --- |
| Installation Temperature °F |
|  | 0 | 20 | 40 | 60 | 80 | 100 |
| Span Length ft | Tension Sag lbf in. | Tension Sag lbf in. | Tension Sag lbf in. | Tension Sag lbf in. | Tension Sag lbf in. | Tension Sag lbf in. |
| 100 125 150 | 3665 21 4019 30 4357 40 | 3572 22 3930 31 4279 41 | 3480 23 3845 32 4197 42 | 3391 23 3760 32 4118 43 | 3303 24 3674 33 4034 43 | 3214 24 3590 34 3952 44 |
| 175 200 225 | 4683 51 4997 63 5303 75 | 4609 52 4925 64 5233 76 | 4531 53 4850 65 5163 77 | 4457 54 4777 66 5092 78 | 4380 55 4702 67 5020 79 | 4304 56 4628 68 4949 80 |

| TABLE 42 Initial Sag and Tension 16M EHS Suspension Strand Supporting Cable Weighing 1.0 lb/ft for Heavy, Medium, and Light Loading Districts |
| --- |
| Installation Temperature °F |
|  | 0 | 20 | 40 | 60 | 80 | 100 |
| Span Length ft | Tension Sag lbf in. | Tension Sag lbf in. | Tension Sag lbf in. | Tension Sag lbf in. | Tension Sag lbf in. | Tension Sag lbf in. |
| 200 225 250 275 | 4973 17 5051 20 5129 24 5207 28 | 4728 18 4813 21 4898 25 4984 30 | 4479 19 4570 22 4660 26 4750 31 | 4231 20 4331 23 4431 28 4529 33 | 3985 21 4093 25 4200 29 4305 35 | 3751 22 3865 26 3979 31 4091 37 |
| 300 325 350 375 | 5286 33 5365 39 5443 45 5521 52 | 5069 35 5154 41 5238 48 5322 54 | 4840 37 4930 43 5019 50 5108 57 | 4627 39 4724 45 4820 52 4915 59 | 4410 41 4513 47 4614 54 4714 62 | 4201 43 4310 50 4417 57 4523 64 |
| 400 425 450 475 | 5600 59 5679 67 5757 74 5836 81 | 5406 62 5490 69 5573 76 5656 84 | 5196 64 5284 72 5372 79 5460 87 | 5010 67 5104 74 5197 82 5290 90 | 4813 69 4910 77 5007 85 5104 93 | 4627 72 4729 80 4831 88 4931 96 |
| 500 525 550 575 | 5915 89 5993 97 6072 105 6151 113 | 5739 92 5823 100 5907 108 5990 117 | 5548 95 5635 103 5723 111 5810 120 | 5378 98 5470 106 5561 115 5650 124 | 5199 101 5295 110 5388 119 5481 128 | 5031 105 5128 113 5225 122 5320 131 |
| 600 625 650 675 | 6229 122 6307 131 6385 140 6463 149 | 6073 125 6155 134 6236 144 6316 153 | 5897 129 5983 138 6068 147 6153 157 | 5738 133 5826 142 5913 152 5998 161 | 5574 137 5665 146 5755 156 5843 165 | 5413 141 5505 150 5597 160 5688 170 |
| 700 725 750 775 | 6541 158 6618 168 6695 178 6772 187 | 6395 162 6474 172 6552 182 6628 192 | 6235 167 6317 176 6399 186 6480 196 | 6083 171 6167 181 6250 191 6333 201 | 5931 175 6018 185 6105 195 6190 206 | 5778 180 5867 190 5955 200 6043 210 |
| 800 825 850 875 | 6849 197 6923 208 6997 218 7069 228 | 6704 202 6779 212 6854 222 6928 233 | 6560 206 6638 217 6715 227 6790 238 | 6415 211 6495 221 6573 232 6651 243 | 6274 216 6355 226 6435 237 6514 248 | 6129 221 6212 231 6295 242 6375 254 |
| 900 925 950 975 1000 | 7141 239 7211 250 7281 262 7349 273 7415 285 | 7001 244 7074 255 7145 267 7214 279 7282 290 | 6864 249 6937 261 7009 272 7079 284 7149 296 | 6727 254 6801 266 6875 278 6947 290 7019 302 | 6591 260 6667 272 6742 283 6816 295 6889 308 | 6454 265 6532 277 6609 289 6685 301 6762 314 |

| TABLE 43 Initial Sag and Tension 16M EHS Suspension Strand Supporting Cable Weighing 1.5 lb/ft for Heavy, Medium, and Light Loading Districts |
| --- |
| Installation Temperature °F |
|  | 0 | 20 | 40 | 60 | 80 | 100 |
| Span Length ft | Tension Sag lbf in. | Tension Sag lbf in. | Tension Sag lbf in. | Tension Sag lbf in. | Tension Sag lbf in. | Tension Sag lbf in. |
| 200 225 250 275 | 5202 22 5330 26 5456 32 5579 38 | 4973 23 5101 28 5230 33 5357 40 | 4745 24 4878 29 5010 35 5142 41 | 4525 25 4662 31 4799 37 4936 43 | 4309 27 4450 32 4592 38 4731 45 | 4104 28 4246 34 4392 40 4537 47 |
| 300 325 350 375 | 5700 45 5821 52 5939 59 6056 67 | 5482 46 5607 54 5733 61 5856 69 | 5273 48 5404 56 5534 64 5664 72 | 5072 50 5206 58 5342 66 5477 74 | 4872 52 5012 60 5153 68 5293 76 | 4682 54 4828 62 4972 70 5115 79 |
| 400 425 450 475 | 6174 75 6290 83 6405 91 6520 100 | 5979 77 6101 85 6224 94 6347 102 | 5794 80 5922 88 6050 96 6147 105 | 5612 82 5746 90 5879 99 6012 108 | 5432 85 5569 93 5707 102 5845 110 | 5258 87 5403 96 5543 105 5683 114 |
| 500 525 550 575 | 6635 108 6746 117 6858 126 6970 135 | 6470 111 6584 120 6697 129 6812 138 | 6305 114 6420 123 6536 132 6652 141 | 6144 116 6262 126 6381 135 6498 145 | 5982 119 6101 129 6222 138 6342 148 | 5826 123 5946 132 6069 142 6193 151 |
| 600 625 650 675 | 7080 144 7191 154 7300 164 7409 175 | 6925 148 7038 158 7151 168 7262 179 | 6768 151 6885 161 7000 172 7114 182 | 6615 154 6732 165 6848 175 6964 186 | 6462 158 6582 168 6700 179 6821 190 | 6313 162 6435 172 6556 183 6677 194 |
| 700 725 750 775 | 7517 186 7626 197 7733 208 7841 219 | 7374 190 7485 201 7595 212 7704 224 | 7227 193 7341 205 7451 216 7564 228 | 7079 197 7194 209 7308 220 7422 232 | 6938 201 7055 213 7172 225 7288 236 | 6797 206 6916 217 7033 229 7152 241 |
| 800 825 850 875 | 7947 231 8053 243 8159 255 8261 267 | 7814 235 7922 247 8029 259 8132 271 | 7675 239 7785 251 7894 263 8000 276 | 7536 244 7645 256 7753 268 7860 280 | 7406 248 7515 260 7625 273 7732 285 | 7271 253 7383 265 7493 278 7600 290 |
| 900 925 | 8359 279 8453 292 | 8232 284 8330 296 | 8103 288 8204 301 | 7964 293 8062 306 | 7835 298 7936 311 | 7706 303 7807 316 |

| TABLE 44 Initial Sag and Tension 16M EHS Suspension Strand Supporting Cable Weighing 2.0 lb/ft for Heavy, Medium, and Light Loading Districts |
| --- |
| Installation Temperature °F |
|  | 0 | 20 | 40 | 60 | 80 | 100 |
| Span Length ft | Tension Sag lbf in. | Tension Sag lbf in. | Tension Sag lbf in. | Tension Sag lbf in. | Tension Sag lbf in. | Tension Sag lbf in. |
| 200 225 250 275 | 5473 26 5627 31 5783 38 5940 45 | 5259 27 5422 33 5584 39 5745 46 | 5051 29 5218 34 5386 41 5552 48 | 4846 30 5026 36 5202 42 5378 50 | 4638 31 4820 37 5002 44 5184 51 | 4433 33 4623 39 4812 46 4998 53 |
| 300 325 350 375 | 6094 52 6251 60 6404 68 6559 77 | 5906 54 6066 62 6227 70 6386 79 | 5720 56 5886 64 6051 73 6215 81 | 5550 57 5722 66 5892 75 6060 84 | 5363 59 5540 68 5715 77 5889 86 | 5182 61 5365 70 5545 79 5725 88 |
| 400 425 450 475 | 6712 86 6866 95 7019 105 7170 114 | 6544 88 6702 97 6860 107 7016 116 | 6379 91 6542 100 6704 109 6864 119 | 6225 93 6390 102 6552 112 6712 122 | 6060 95 6230 105 6397 115 6562 125 | 5900 98 6075 108 6245 118 6413 128 |
| 500 525 550 575 | 7320 124 7469 134 7615 144 7760 155 | 7172 126 7324 136 7473 147 7620 158 | 7022 129 7176 139 7326 150 7473 161 | 6872 132 7027 142 7179 153 7329 164 | 6722 135 6881 145 7036 156 7190 167 | 6577 138 6737 148 6894 159 7047 171 |
| 600 625 650 675 | 7902 166 8042 177 8179 188 8310 199 | 7762 169 7903 180 8040 191 8172 203 | 7616 172 7757 183 7896 194 8034 206 | 7474 175 7617 186 7757 197 7896 209 | 7336 178 7481 190 7625 201 7765 213 | 7197 182 7344 193 7488 205 7629 217 |
| 700 725 750 775 | 8441 211 8568 223 8694 235 8820 247 | 8302 214 8432 226 8561 238 8687 251 | 8169 217 8298 229 8427 242 8555 254 | 8034 221 8166 233 8296 246 8426 258 | 7903 225 8035 237 8167 250 8298 263 | 7768 229 7901 241 8033 254 8165 267 |

| TABLE 45 Initial Sag and Tension 16M EHS Suspension Strand Supporting Cable Weighing 2.5 lb/ft for Heavy, Medium, and Light Loading Districts |
| --- |
| Installation Temperature °F |
|  | 0 | 20 | 40 | 60 | 80 | 100 |
| Span Length ft | Tension Sag lbf in. | Tension Sag lbf in. | Tension Sag lbf in. | Tension Sag lbf in. | Tension Sag lbf in. | Tension Sag lbf in. |
| 100 125 150 175 | 5028 9 5220 13 5412 17 5600 23 | 4785 9 4989 13 5190 18 5390 24 | 4537 10 4751 14 4962 19 5172 25 | 4291 10 4513 14 4734 20 4952 26 | 4049 11 4279 15 4508 21 4735 27 | 3814 11 4058 16 4298 22 4536 28 |
| 200 225 250 275 | 5790 30 5977 36 6167 44 6356 52 | 5587 31 5784 38 5979 45 6172 54 | 5378 32 5585 39 5788 47 5990 55 | 5168 33 5383 40 5595 48 5805 57 | 4958 34 5181 42 5401 50 5620 58 | 4772 35 5001 43 5230 51 5453 60 |
| 300 325 350 375 | 6542 61 6730 69 6916 78 7100 87 | 6363 62 6553 71 6743 80 6932 89 | 6190 64 6386 73 6580 82 6773 91 | 6014 66 6213 74 6412 84 6610 93 | 5837 67 6043 76 6247 86 6450 95 | 5673 69 5886 78 6095 88 6300 97 |
| 400 425 450 475 | 7283 96 7465 106 7644 116 7820 126 | 7120 98 7305 108 7487 118 7668 129 | 6963 101 7151 111 7337 121 7521 131 | 6805 103 6997 113 7188 123 7376 134 | 6651 105 6848 115 7042 126 7231 136 | 6505 107 6704 118 6900 128 7092 139 |
| 500 525 550 575 | 7996 137 8165 148 8334 159 8500 170 | 7849 139 8024 150 8193 162 8364 173 | 7704 142 7880 153 8053 165 8225 176 | 7560 145 7736 156 7912 168 8085 179 | 7418 148 7597 159 7776 171 7952 183 | 7282 150 7462 162 7640 174 7816 186 |
| 600 625 650 675 | 8666 182 8829 194 8990 206 9149 218 | 8534 185 8699 197 8862 209 9024 221 | 8396 188 8565 200 8732 213 8894 225 | 8256 191 8427 204 8594 216 8760 228 | 8126 195 8298 207 8466 219 8632 232 | 7991 198 8165 210 8336 223 8503 235 |

| TABLE 46 Initial Sag and Tension 16M EHS Suspension Strand Supporting Cable Weighing 3.0 lb/ft for Heavy, Medium, and Light Loading Districts |
| --- |
| Installation Temperature °F |
|  | 0 | 20 | 40 | 60 | 80 | 100 |
| Span Length ft | Tension Sag lbf in. | Tension Sag lbf in. | Tension Sag lbf in. | Tension Sag lbf in. | Tension Sag lbf in. | Tension Sag lbf in. |
| 100 125 150 175 | 5129 10 5361 14 5593 20 5822 26 | 4904 10 5145 15 5383 21 5620 27 | 4664 11 4913 16 5164 22 5412 28 | 4433 11 4691 17 4984 22 5204 29 | 4205 12 4475 17 4743 23 5007 30 | 3976 13 4258 18 4541 24 4817 32 |
| 200 225 250 275 | 6051 33 6276 41 6499 49 6721 58 | 5856 34 6090 42 6322 50 6550 59 | 5657 36 5900 43 6142 52 6380 61 | 5459 37 5711 45 5959 53 6206 62 | 5268 38 5526 46 5781 55 6036 64 | 5090 39 5358 48 5624 56 5885 66 |
| 300 325 350 375 | 6941 67 7162 76 7382 85 7597 95 | 6776 68 7003 77 7228 87 7447 97 | 6618 70 6846 79 7072 89 7296 99 | 6450 71 6684 81 6915 91 7142 101 | 6288 73 6529 83 6765 93 6996 103 | 6141 75 6386 85 6625 95 6855 105 |
| 400 425 450 475 | 7811 105 8020 116 8225 127 8428 138 | 7665 107 7877 118 8086 129 8292 140 | 7512 109 7727 120 7941 131 8147 142 | 7365 111 7585 122 7802 134 8015 145 | 7221 114 7445 125 7664 136 7880 147 | 7082 116 7301 127 7519 138 7738 150 |
| 500 525 550 575 | 8628 149 8827 161 9024 173 9218 185 | 8494 151 8695 163 8896 175 9091 188 | 8354 154 8557 166 8758 178 8956 190 | 8225 157 8431 169 8632 181 8831 193 | 8090 159 8297 171 8500 184 8700 196 | 7946 162 8154 174 8362 187 8565 199 |

| TABLE 47 Initial Sag and Tension 16M EHS Suspension Strand Supporting Cable Weighing 3.5 lb/ft for Heavy, Medium, and Light Loading Districts |
| --- |
| Installation Temperature °F |
|  | 0 | 20 | 40 | 60 | 80 | 100 |
| Span Length ft | Tension Sag lbf in. | Tension Sag lbf in. | Tension Sag lbf in. | Tension Sag lbf in. | Tension Sag lbf in. | Tension Sag lbf in. |
| 100 125 150 175 | 5265 11 5525 16 5787 22 6049 28 | 5028 11 5303 17 5577 23 5850 30 | 4806 12 5098 17 5387 24 5669 31 | 4586 13 4888 18 5187 25 5481 32 | 4366 13 4685 19 4996 26 5298 33 | 4150 14 4484 20 4807 27 5122 34 |
| 200 225 250 275 | 6310 36 6572 44 6832 53 7089 62 | 6123 37 6392 45 6658 54 6920 64 | 5947 38 6222 47 6494 56 6762 65 | 5771 40 6050 48 6327 58 6597 67 | 5595 41 5876 50 6155 59 6433 69 | 5427 42 5719 51 6006 61 6289 70 |
| 300 325 350 375 | 7343 72 7595 82 7843 92 8087 102 | 7180 73 7437 83 7691 94 7940 104 | 7025 75 7284 85 7540 95 7791 106 | 6866 77 7130 87 7390 97 7644 108 | 6706 79 6975 89 7242 99 7494 110 | 6567 81 6842 91 7112 101 7368 112 |
| 400 425 450 475 | 8328 113 8565 124 8797 135 9026 147 | 8184 115 8424 126 8658 137 8890 149 | 8037 117 8279 128 8517 139 8751 151 | 7893 119 8138 130 8378 142 8615 154 | 7745 121 7992 133 8236 144 8475 157 | 7620 123 7868 135 8110 147 8348 159 |
| 500 525 | 9250 159 9470 171 | 9117 161 9341 174 | 8980 164 9207 176 | 8847 166 9075 179 | 8709 169 8940 182 | 8552 171 8812 184 |

| TABLE 48 Initial Sag and Tension 16M EHS Suspension Strand Supporting Cable Weighing 4.0 lb/ft for Heavy, Medium, and Light Loading Districts |
| --- |
| Installation Temperature °F |
|  | 0 | 20 | 40 | 60 | 80 | 100 |
| Span Length ft | Tension Sag lbf in. | Tension Sag lbf in. | Tension Sag lbf in. | Tension Sag lbf in. | Tension Sag lbf in. | Tension Sag lbf in. |
| 100 125 150 175 | 5384 12 5709 17 6027 24 6334 31 | 5161 13 5492 18 5820 25 6138 32 | 4941 13 5278 19 5611 26 5939 33 | 4733 14 5076 20 5414 27 5746 34 | 4525 15 4876 21 5220 27 5559 35 | 4320 15 4680 21 5033 28 5380 36 |
| 200 225 250 275 | 6633 39 6926 48 7209 57 7487 67 | 6449 40 6749 49 7043 59 7325 68 | 6260 41 6573 50 6876 60 7170 70 | 6072 43 6392 52 6704 61 7006 72 | 5893 44 6221 53 6540 63 6849 73 | 5721 45 6054 54 6385 64 6699 75 |
| 300 325 350 375 | 7762 77 8038 88 8312 98 8580 109 | 7606 79 7885 89 8162 100 8435 111 | 7456 80 7740 91 8019 102 8292 113 | 7300 82 7585 93 7867 104 8144 115 | 7152 84 7439 94 7724 106 8044 117 | 7011 85 7301 96 7586 108 7868 119 |
| 400 425 450 475 | 8843 121 9104 132 9361 144 9612 157 | 8702 122 8966 134 9224 146 9479 159 | 8562 124 8828 136 9089 148 9347 161 | 8417 127 8685 139 8950 151 9211 163 | 8279 129 8550 141 8817 153 9082 166 | 8144 131 8417 143 8684 155 8948 168 |

| TABLE 49 Initial Sag and Tension 16M EHS Suspension Strand Supporting Cable Weighing 4.5 lb/ft for Heavy, Medium, and Light Loading Districts |
| --- |
| Installation Temperature °F |
|  | 0 | 20 | 40 | 60 | 80 | 100 |
| Span Length ft | Tension Sag lbf in. | Tension Sag lbf in. | Tension Sag lbf in. | Tension Sag lbf in. | Tension Sag lbf in. | Tension Sag lbf in. |
| 100 125 150 175 | 5511 13 5869 19 6214 26 6554 34 | 5306 14 5673 20 6029 27 6374 35 | 5098 14 5472 21 5839 28 6197 36 | 4892 15 5271 21 5644 29 6011 37 | 4687 16 5072 22 5451 30 5825 38 | 4496 16 4890 23 5273 31 5654 39 |
| 200 225 250 275 | 6880 42 7201 52 7516 61 7825 71 | 6712 44 7039 53 7360 63 7673 73 | 6545 45 6882 54 7210 64 7530 75 | 6370 46 6716 55 7054 65 7381 76 | 6192 47 6551 57 6901 67 7231 77 | 6029 48 6396 58 6753 68 7090 79 |
| 300 325 350 375 | 8133 82 8438 93 8738 104 9034 115 | 7984 84 8292 95 8594 106 8893 117 | 7845 85 8155 96 8461 108 8761 119 | 7702 87 8019 98 8331 109 8636 121 | 7557 88 7878 100 8192 111 8498 123 | 7421 90 7746 101 8062 113 8370 125 |
| 400 425 | 9322 127 9612 139 | 9187 129 9477 141 | 9057 131 9347 144 | 8933 133 9220 146 | 8797 135 9085 148 | 8669 137 8961 150 |

| TABLE 50 Initial Sag and Tension 16M EHS Suspension Strand Supporting Cable Weighing 5.0 lb/ft for Heavy, Medium, and Light Loading Districts |
| --- |
| Installation Temperature °F |
|  | 0 | 20 | 40 | 60 | 80 | 100 |
| Span Length ft | Tension Sag lbf in. | Tension Sag lbf in. | Tension Sag lbf in. | Tension Sag lbf in. | Tension Sag lbf in. | Tension Sag lbf in. |
| 100 125 150 175 | 5664 14 6049 20 6427 28 6793 36 | 5453 15 5848 21 6236 29 6616 37 | 5248 15 5648 22 6044 29 6434 38 | 5048 16 5456 23 5858 30 6252 39 | 4855 17 5283 23 5699 31 6100 40 | 4661 17 5094 24 5520 32 5936 41 |
| 200 225 250 275 | 7149 45 7498 54 7843 65 8184 75 | 6985 46 7344 56 7695 66 8040 77 | 6815 47 7187 57 7548 67 7895 78 | 6642 48 7024 58 7398 69 7751 80 | 6490 49 6876 59 7250 70 7612 81 | 6340 51 6727 61 7109 72 7473 83 |
| 300 325 350 375 | 8524 86 8858 98 9184 109 9503 121 | 8381 88 8717 99 9044 111 9367 123 | 8237 89 8576 101 8907 112 9233 125 | 8097 91 8439 102 8774 114 9100 126 | 7965 93 8305 104 8636 116 8960 128 | 7832 94 8182 106 8518 118 8843 130 |

8.3  The initial sags and tensions for filled fiber optic cables installed on 6M EHS suspension strands at various span lengths and temperatures in the three NESC storm loading districts should be obtained from the fiber optic cable manufacturer.

9.  RAILROAD CROSSING

9.1  Aerial construction involving the crossing of railroads should be performed in accordance with Section 24 of the latest edition of the NESC.

9.2 Aerial construction involving the crossing of railroads also should be performed in accordance with the latest edition of the “Specification For Communication Lines Crossing the Tracks of Railroads” issued by the Association of American Railroads.

10.  POLE STEPPING

10.1 Poles should be stepped where indicated on the construction drawings.

10.2  The steps should be placed on poles as shown on Assembly Unit Drawing PM-5 in RUS Bulletin 345-153 (RUS Form 515f).

11.  MECHANICAL PROTECTION OF CABLE AND PREVENTION

OF CABLE DANCING

11.1  Aerial cables that could be damaged by chafing from trees or poles should be protected from damage by placing RUS accepted or technically accepted plastic split or spirally cut cable guards over the cable at those locations.  Cable guards should also be placed on aerial cables at locations where the required clearance between the telecommunications cable and power cable can not maintained.

11.2  In areas where lashed aerial filled copper or fiber optic cables are subjected to high winds, cables should be spiraled around the suspension strand to minimize cable dancing.  The spiraling of the cable around the suspension strand represents an irregular configuration of cable and strand to the wind pressure thereby tending to break up movement of cable and reduce dancing.

11.3  In areas where self-supporting, filled fiber optic cables are subjected to high winds, cables should be spiraled around the integrated suspension strand to minimize cable dancing.  The spiraling of the cable around the integrated suspension strand represents an irregular configuration of cable and strand to the wind pressure thereby tending to break up movement of cable and reduce dancing.

11.4  The spiraling of the cable around the suspension strand to minimize cable dancing should be performed as indicated on Guide Drawing 250 for lashed filled copper and fiber optic cables and Guide Drawing 250-1 for self-supporting, filled fiber optic cable of RUS Bulletin 345-153 (RUS Form 515f).

11.5  The spiraling operation should be performed at alternate poles throughout the length of the affected section of the cable lead.  Performing the spiraling operation at alternate pole locations results in the spiraling of two adjacent spans at the same time.  The presence of a straight splice in the affected section of cable lead should not affect the spiraling operation.

11.6  Prior to spiraling of lashed cable, the lashing wire clamps should be temporarily loosened to eliminate tightening of the lashing wire during the spiraling operation.  After spiraling, the lashing wire should be readjusted and reclamped.

11.7  The spiraling operation may be performed at poles where strand mounted terminals are installed provided that care is exercised to prevent damage to the terminal stub and splice.

11.8  In areas where high winds prevail and light weight cable is constructed on unusually long spans, addition spiraling of the cable may be required to obtain satisfactory results.  The number of additional twists at these locations should be indicated on the construction drawings.

12.  HANDLING AND CARE OF MATERIALS DURING CONSTRUCTION

12.1  Extreme care should be exercised in handling materials during the construction process.  The suspension strand should be handled and stored in such a manner as to prevent accelerated corrosion or physical damaged to the suspension strand.

12.2  Care should be exercised to prevent damage to exposed cables during the construction period.  Construction work should be scheduled to keep such exposure to minimum.

12.3  Cables should be installed in aerial splice cases, ready-access cases, and pole mounted terminals as soon as practicable.  The installation work should be completed as soon as practicable after the cables have been installed.

13.  REPAIR OF CABLES DAMAGED DURING CONSTRUCTION

13.1  Minor damage to the outer jackets, where the shields or armors of the cables have not been bent, abraded, or penetrated should be repaired in accordance with Bulletin 1753F-401(PC-2), RUS Standard for Splicing Copper and Fiber Optic Cables.

13.2  Where shields or armors have penetrated the outer jackets of cables, the damaged sections should be enclosed in aerial splice cases.  The outer jackets, shields, or armors of the damaged sections should be removed as though preparing for splicing.  The shields or armors should then be bonded together.  Damage to the copper conductors or their insulations or optical fibers or their buffer tubes should be repaired in accordance with Bulletin 1753F-401(PC-2), RUS Standard for Splicing Copper and Fiber Optic Cables.

13.3  Cables found to be damaged after installation should be repaired.  If the damage is considered minor, the damage should be repaired in accordance with Bulletin 1753F-401(PC-2), RUS Standard for Splicing Copper and Fiber Optic Cables.  If the damage is considered major, the damage should be repaired either by replacing the damaged sections with new cables spliced to the undamaged sections of the cable or repaired in accordance with the method specified in the contract.

13.4  All aerial splice cases added because of repairs should be shown on the construction drawings.  However, they should not be included in the final inventory for compensation purposes as specified by the RUS 515 Contract and RUS Bulletin 345-153 (RUS Form 515f).

14.  PREPARATION FOR SPLICING OR TERMINATION

14.1  Aerial filled copper cables should be spliced in accordance with Bulletin 1753F-401(PC-2), RUS Standard for Splicing Copper and Fiber Optic Cables and enclosed in RUS accepted or technically accepted aerial splice cases, ready-access cases, or pole mount terminals.

14.2  Aerial filled fiber optic or self-supporting fiber optic cables should be spliced in accordance with Bulletin 1753F-401(PC-2), RUS Standard for Splicing Copper and Fiber Optic Cables and enclosed in RUS accepted or technically accepted filled fiber optic splice cases.

14.3  RUS accepted or technically accepted filled terminal blocks should only be used in ready-access cases and pole mount terminals.

15.  INSTALLATION PROCEDURES FOR FILLED CABLES IN COLD WEATHER

15.1  Flexibility of filled copper or fiber optic cables should not be a problem at normal operating temperatures.  However, flexibility may be affected when cables are exposed to lower temperatures.  The flexibility of filled copper or fiber optic cables could be sharply reduced at temperatures below 40°F (4.4°C).  At temperatures below 40°F (4.4°C), almost twice the force may be needed to bend the filled copper or fiber optic cables.  Filled copper or fiber optic cables should be inspected each morning to determine if the cables are flexible enough for aerial placement when night time temperatures drop below 30°F

(-1.1°C).  When filled copper or fiber optic cables have been stored outdoors and subjected to cold nights, considerable time may be lost each morning waiting for the cables to warm up even though the daytime temperature may be above 40°F (4.4°C).  During the spring and fall of the year, the filled copper or fiber optic cables may be stored in heated warehouses prior to placement in the air.  This storage in heated warehouses allows the filled copper or fiber optic cables to be transported to the project site as needed and installed while the cables are still flexible.

15.2  Some filling compounds used in the cores of filled copper cables may be stiff as the temperature decreases making it difficult to separate the cable pairs.  In general, filled copper cables installations below 40°F (4.4°C) could be slow, difficult, and possibly even halted unless special precautions are taken to offset the effects of the lower temperatures.

15.3  Filling compounds used in loose tube buffers of filled fiber optic cables should not become stiff as the temperature decreases.  This should allow the optical fibers to be easily separated at low temperatures.

15.4  As mentioned in Paragraph 15.2, the copper pairs may be difficult to separate as the temperature decreases.  At temperatures as low as 20°F (-6.7°C), the copper pairs may be separated by flexing the free ends of the cable cores and separating a few pairs at a time.  It is also interesting to note that filling compounds at a temperature of 20°F (-6.7°C) are more user friendly to work with than at elevated temperatures.  Consequently, the copper cable pairs may be spliced without wiping the pairs free of filling compound.

16.  ASSEMBLY UNITS

16.1  Detailed descriptions of all standard aerial plant assembly units are given in RUS Bulletin 345-153, Specifications and Drawings for Construction of Pole Line, Aerial Cables and Wires (RUS Form 515f).

16.2  Where standard aerial plant assembly units are insufficient to provide for unique aerial plant construction requirements, detailed “nonstandard assembly units” should be created to meet those requirements.  The aerial plant nonstandard assembly units should be approved by RUS prior to the bidding of the project.  “Nonstandard assembly units” should be kept to the absolute minimum needed for the project.

17.  NUMBERING AND ACCEPTANCE TESTING

17.1  The first, fifth, tap, breakdown, and end poles installed along the construction route should be marked with route letters, pole numbers, and, when required, the load point numbers (When loaded lines are determined by RUS to be economically feasible and the overall system design complies with the Modernization Plan [7 CFR 1751, Subpart B]).

17.2  In lieu of Paragraph 17.1, every pole along the construction route may be marked with route letters, pole numbers, and, when required, load point numbers (When loaded lines are determined by RUS to be economically feasible and the overall system design complies with the Modernization Plan [7 CFR 1751, Subpart B]) when requested by the RUS borrower.

17.3  After installation, aerial copper cables should be tested in accordance with RUS Bulletin 345-63, RUS Standard for Acceptance Tests and Measurements of Telephone Plant (PC-4) and the RUS Form 515 Contract.

17.4  After installation, aerial fiber optic cables should be tested in accordance with the procedures listed in the contract.