| Self-Assessment Guidance Card |
| --- |
| Area: Exhaust Ventilation | Date: 01/30/08 |
| Topic: Line organization Use of Exhaust Systems | Rev: Final 0 |
| References: SBMS Subject Area- Exhaust Ventilation; ACGIH Industrial Ventilation Manual |

| Performance Expectations: |
| --- |
| Are the requirements for using ventilation systems (e.g. lab hoods, “elephant trunks”, slotted tank systems, canopy hoods, etc.) determined and documented by a valid method, such as work permit, procedure or ESR? Were ventilation systems designed or approved by a qualified engineer? Are exhaust systems listed in the Facility Use Agreement inventory? Do inspection and maintenance programs meet SBMS Requirements: Regular maintenance programs (for belts, motors, and other serviceable parts of exhaust systems)? Regular lab hood face velocity? Local system duct capture velocity test? Regular filter changes of HEPA filters? Annual HEPA Filter Surveillance test? Is testing indicated on an inspection sticker or operation authorizing documents? Have users completed training for hazards requiring exhaust ventilation equipment (such as radiological or chemical hazards training)? Can the operating status of the exhaust ventilation system be observed by a device such as a Magnehelic® gauge or flow indicating sensor (when applicable and available)? Were decommissioned systems removed from service, labeled with an out-of-service label and updated in the Facility Use Agreement? Was sampling conducted or was sufficient knowledge available to determine that sampling for hazards was not needed before decommissioning (e.g. radiological hazards; perchloric acid/perchlorates; asbestos; lead; or other hazards) based on verifiable knowledge of the full historical use of the equipment? Was the Facility Support (FS) Representative contacted to arrange for radiological contamination testing prior to any demolition or modification of the system that will result in the worker's potential exposure? Was the Safety & Health Services Representative contacted to arrange for perchlorate contamination testing prior to any demolition or modification of the system where perchloric acid was used in the past or historical knowledge is incomplete? |
| Procedure: (Perform the following as applicable for the assessment) Review assessment guidance card. Review the subject area for applicable procedures/requirements. Observe the activity(ies) controlled by the procedure. Interview appropriate personnel about requirements and practices. Record observations based on comparison to guidance. Document the results. |
| Basis for the Assessment: (Why is the assessment being done?) Periodic Lessons Learned Directed by Management Responsive Targeted |
| Assessor(s): | Date of Assessment: |
| Location of Assessment: (Bldg/Room) |