A/E REVIEW CHECKLIST

STEAM DISTRIBUTION

Reviewers should - Use Checklists when reviewing any type of VA construction project for the following disciplines: 
  Site and Landscape, 
  Architectural, 
  Structural, 
  Plumbing, Fire Protection, and 
        Sanitary, 
  Heating, Ventilating, and Air 
        Conditioning (HVAC), 
  Steam Generation, 
  Steam Distribution,
  Electrical.

Reviewers should - Insure that A/E Submission Instructions 
(PG-18-15) for Schematic, Design Development, and Construction Documents are followed for various types of VA construction projects.

Reviewers should - Insure that every VA construction project is in compliance with all life safety issues.

Reviewers should - Be aware that these checklists are not all-inclusive but only provide minimum review items.

- A/E CHECKLIST

- TITLE________________________________PROJECT NO.

- LOCATION___________________________________DATE

- REVIEWED BY

- ORGANIZATION

| GENERAL INFORMATION FOR REVIEWERS |  |
| --- | --- |
| STEAM DISTRIBUTION REVIEWS |  |
| The reviewer should be thoroughly familiar with the following VA standards before conducting a design review. These are available on Internet: http://www.va.gov/facmgt/standard |  |
| 1. | DESIGN MANUALS (PG-18-10) |
| 2. | # MASTER CONSTRUCTION SPECIFICATIONS (PG-18-1) |
| 3. | STANDARD DETAILS (PG-18-4) (Available in AutoCADD 2000 Format) |
| 4. | DESIGN AND CONSTRUCTION PROCEDURES (formerly Construction Standards) (H-18-3) (Policies defining the minimum level of excellence in the design of VA facilities) |
| 5. | # DESIGN GUIDES (PG-18-12) (Graphic information on specific programs in the design development of VA facilities) |
| 6. | # DESIGN ALERTS (These alerts are issued on a regular basis for design and construction related issues) |
| 7. | # A/E QUALITY ALERTS (These alerts are issued to guard against common and repeat design errors) |
| 8. | A/E SUBMISSION INSTRUCTIONS (PG-18-15) |
| 9. | TECHNICAL SUMMARIES (The summaries of HVAC design requirements for special and critical areas) |
| 10. | NATIONAL CAD STANDARD |
| 11. | VA NATIONAL CAD STANDARD APPLICATION GUIDE |

- A/E CHECKLIST

- TITLE________________________________PROJECT NO.

- LOCATION___________________________________DATE

- REVIEWED BY

- ORGANIZATION

| SCHEMATIC 1 |  |  |
| --- | --- | --- |
| STEAM DISTRIBUTION REVIEW |  |  |
| NO. | ITEM | COMMENTS/ YES/NO/NA |
| 1 | Have A/E Submission Requirements (PG-18-15) for this review been met? List omissions. |  |
| 2 | Does A/E have latest VA Master Specifications? |  |
| 3 | Does A/E have latest VA Standard Details? |  |
| 4 | Does A/E have latest VA Design Manual? |  |
| 5 | Does A/E have access to Corps of Engineers Concrete Shallow Trench Details? |  |
| 6. | Compliance with VA National CAD Standard Application Guide and applicable National CAD Standard modules. |  |

| SCHEMATIC 2 |  |  |
| --- | --- | --- |
| STEAM DISTRIBUTION REVIEW |  |  |
| NO. | ITEM | COMMENTS/ YES/NO/NA |
| 1 | Have A/E Submission Requirements (PG-18-15) for this review been met? List omissions. |  |
| 2 | Life cycle cost method complies with NIST Handbook 135? |  |
| 3 | Acceptable responses to previous comments? |  |
| 4. | Compliance with VA National CAD Standard Application Guide and applicable National CAD Standard modules. |  |

- A/E CHECKLIST

- TITLE________________________________PROJECT NO.

- LOCATION___________________________________DATE

- REVIEWED BY

- ORGANIZATION

| DESIGN DEVELOPMENT 1 |  |  |
| --- | --- | --- |
| STEAM DISTRIBUTION REVIEW |  |  |
| NO. | ITEM | COMMENTS/ YES/NO/NA |
| 1 | Have A/E Submission Requirements (PG-18-15) for this review been met? List omissions. |  |
| 2 | System design complies with Outside Steam Distribution Design Manual. |  |
| 3 | Steam and condensate load calculations acceptable? |  |
| 4 | Pipe sizing calculations acceptable? |  |
| 5 | Plan view and sections of tunnels or manholes show adequate space for maintenance access? |  |
| 6 | Manholes properly ventilated? |  |
| 7 | Manholes properly drained? |  |
| 8 | Piping in manholes arranged to allow thermal expansion without overstress? |  |
| 9 | System layout drawings show all other underground systems within 20 feet of new system. |  |
| 10 | Acceptable responses to previous comments? |  |
| 11 | Coordination with other disciplines |  |
| 12 | Compliance with VA National CAD Standard Application Guide and applicable National CAD Standard modules. |  |

- A/E CHECKLIST

- TITLE________________________________PROJECT NO.

- LOCATION___________________________________DATE

- REVIEWED BY

- ORGANIZATION

| DESIGN DEVELOPMENT 2 |  |  |
| --- | --- | --- |
| STEAM DISTRIBUTION REVIEW |  |  |
| NO. | ITEM | COMMENTS/ YES/NO/NA |
| 1 | Have A/E Submission Requirements (PG-18-15) for this review been met? List omissions. |  |
| 2 | System Design complies with VA Outside Steam Distribution Design Manual. |  |
| 3 | Are calculations complete including pipe and equipment sizing, steam traps, thermal expansion, pipe stress? |  |
| 4 | Are Master Specs to be utilized of current issue? |  |
| 5 | Is all pipe stress within ASME B31.1 limits? |  |
| 6 | Do expansion joint movement requirements include safety factor? |  |
| 7 | Has adequate clearance been shown for maintenance access in manholes and tunnels? |  |
| 8 | Have steam lines been shown in profile with proper slope and drip traps? |  |
| 9 | Have warm-up bypasses been provided for all steam main gate valves? |  |
| 10 | Have drip pockets and steam traps been provided ahead of all steam main gate valves? |  |
| 11 | Acceptable responses to previous comments? |  |
| 12 | Coordination with other disciplines |  |
| 13 | Compliance with VA National CAD Standard Application Guide and applicable National CAD Standard modules. |  |

- A/E CHECKLIST

- TITLE________________________________PROJECT NO.

- LOCATION___________________________________DATE

- REVIEWED BY

- ORGANIZATION

| CONSTRUCTION DOCUMENTS 1 |  |  |
| --- | --- | --- |
| STEAM DISTRIBUTION REVIEW |  |  |
| NO. | ITEM | COMMENTS/ YES/NO/NA |
| 1 | Have A/E Submission Requirements (PG-18-15) for the review been met? List omissions. |  |
| 2 | Acceptable responses to previous comments? |  |
| 3 | Have any major steam lines been relocated since last review? This would require a revised stress analysis. |  |
| 4 | Are all valves, steam traps, and expansion joints accessible for maintenance? |  |
| 5 | Do structural and architectural drawings show complete details of manhole, tunnel, or trench construction? |  |
| 6 | Are locations of all pipe hangers and supports shown and types of hangers identified? |  |
| 7 | Are structural supports for pipe anchors and pipe supports in tunnels, manholes and trenches shown? |  |
| 8 | Are pipe anchors detailed for tunnels, trenches, manholes? |  |
| 9 | Coordination with other disciplines |  |
| 10 | Compliance with VA National CAD Standard Application Guide and applicable National CAD Standard modules. |  |