# To

Dockets Management Branch (HFA – 305)

Food and Drug Administration,

5630 Fisher Lane, Rm. 1061

# Rockville, MD 20852

# Dear Sirs,

I have reviewed the new proposal for the Guidance for Industry on Aseptic Processing (issued August 2003) and I submit comments for  review by the agency.

I want to emphasize that this document is a vast improvement over the previous released comment document from September 2002. It is obvious, that a great deal of listening to the comments provided from all corners helped greatly, especially  the  PQRI input.

Some general technical comments:

Unidirectional airflow is now the commonly used expression to characterise air flow derived from installations applied in pharmaceutical manufacturing. Therefore there should be consistency in the phrases, and not a swing between laminar flow and sometimes unidirectional air flow (e.g line 196, ...)

Remove all phrases referring to obsolete  FS 209 E (e.g. line 226) and state only the valid ISO classes (e.g. 14644-1) in the  main text.

In Appendix 1 Aseptic Processing Isolators the term decontamination should be replaced by biodecontamination where this refers to removal of unwanted viable particles.

There is a lack of definitions on:

Routine (used e.g. in line 147or 693, etc....)

Continuously (used in line 243)

Mechanical (line 1560)

Specific comments line by line

- Line 303 - 304:

Text:	...Capable of retaining at least 99.97 percent ...

Comment:	The specification of a minimum leak rate of 0.03 % does not correlate with international standards for HEPA filters. These guidelines have a leakage criteria that steps down in 0.25, 0.025, etc and the leakage criteria is directly linked to the specified retention grade.
There is always confusion on what is the requirement of the agency. As we read the text, FDA is talking on the retention grade of a HEPA filter being installed and measured in situ. Therefore a retention grade should be mentioned that complies with international guidelines (0.025 for a HEPA with a certified retention grade of 99.95 %). I even think it is better to make reference to an international – also adopted standard by US – standard specifying a certified HEPA filter retention grade and not mentioning an insitu retention grade at all.

Proposal:	All HEPA filters should be certified and leak tested according to a written procedure. Acceptance criteria for passing filter integrity testing should be calculated according international standards, such as EN 1822

- Line 312 - 314:

Text:	...depending on the accuracy of the photometer.. with an appropriate photometer probe ..air flow rating.

Comment:	Since there are other challenge aerosols on the market and widely used (Emery 3004), DOP, which is under suspect to cause cancer, should not be mentioned as the only one. On the other hand, it is superfluous to mention the upstream concentration since later one the requirement for leakage calculation is required, which makes it necessary anyway to have an upstream concentration sufficient for reaching acceptance criteria.

Proposal:	The leak test should be done with a challenge aerosol (e.g. Emery 3004, DEHS, or DOP) with an upstream concentration sufficient to allow leak rate calculation in the specified range.

- Line 312 & 315:

Text:	... with an appropriate photometer probe, ...

Comment:	New ISO 14644-3 allows use of photometers AND particle counters, therefore not a single device type should be mentioned. Instead please use approach of ISO 14644-3 and leave it open, which devices and procedure are used.

Proposal:	... with an appropriate photometer or particle counter

- Lines 935 - 944:

Text:	When filling ...following investigation

Comment:	These recommended criteria go away from all the other standards being applied throughout the world (e.g. ISO 13408 Aseptic processing of health care products, EC-GMP guideline, PIC/S guideline). They are not only more stringent than the ones mentioned above, they also do not have any statistical considerations in it. In consequence it will lead the industry to fill only the minimum number specified (5000, up to 10.000 and 10.000 only, since there is no rational given, what are the expected results for a 30.000 unit media fill.
Therefore I propose to stick to the already existing acceptance criteria and take these acceptance criteria  from ISO standards into the guideline text .

Proposal:	Acceptance criteria for media fills should be derived from ISO 13408.

- Line 1560:

Text:	Mechanical integrity tests ...

Comment:	It is probably not meant, that the gloves are subjected to mechanical stress prior to batch. If it is meant, that gloves should be test by physical means and not only by visual inspection, then this should be clearly stated.

Proposal:	Automated integrity tests should be performed routinely along with visual inspection.

- Line 1588:

Text:	... well as ease of cleaning and sterilization.

Comment:	This refers to the construction materials of the isolation systems and components, and not to the components of a filling unit with a aseptic fluid path. Therefore the expression should be exchanged to the word sanitization, because this is what is required. The whole paragraph does only talk on decontamination and not on sterilisation.

Proposal:	... well as ease of cleaning and bio-decontamination

- Line 1597:

Text:	... approximately 0.07” to 0.2” water gauge.

Comment:	Most of the other text is stating limits in metric values, therefore this should be applied here as well. SI units should be used. 0.2 is not widely used in aseptic filling operations in isolation technology. Therefore the upper limit mentioned should be decreased to a more widely used value.

Proposal:	... approximately 12.5 – 30 Pa in most cases. Special cases exist for designated processes.

- Line 1615 - 1616:

Text:	An aseptic processing isolator should not be located in an unclassified room.

Comment:	Since the whole guide is on aseptic processing, it is not necessary to mention “aseptic” isolator (scope of this guide). If it is the agency’s opinion, that isolators for aseptic processing should be located in class 8 (ISO) (as a minimum), then this should be clearly stated in the sentence above.

Proposal:	Delete whole sentence

- Line 1654:

Text:	A decontamination method should be developed, that renders the inner surface of the isolator free of viable microorganisms.

Comment:	This wording tends to say, that the agency is asking for a sterilisation cycle for the inner surfaces of the isolator. This is in conflict with the surface requirement for viable particles stated in line 143. There a limit of one is mentioned for air borne particles, and none for surfaces. European and PIC/S guidelines require a limit of 1 for viable surface contaminants as well. Therefore rephrase in such a way, that there is the overall goal of developing and applying a bio-decontamination cycle is to achieve a inner surface contamination of less than 1 cfu/sample (e.g. obtained by applying rodac contact plate multi sampling).

Proposal:	Bio-decontamination cycle development should prove that a quantified challenge of BIs can be reduced to the specified limit. Normally a 4 log reduction for inner surfaces is seen as sufficient.

- Line 1681:

Text:	A breach of isolators integrity should lead to a decontamination cycle.

Comment:	This requirement is not justified. Not every loss in integrity (e.g. pin hole in a glove that is far away from the critical area is per definition a loss of integrity. We think, it is the intent of the agency to require subsequent bio-decontamination when there was a “major” event. Since major is not easy to specify, we propose to request a hold in production, failure investigation (what happened) and risk assessment. Based on assessment of risk a stop of production and new bio-decontamination might be necessary.

Proposal:	A breach of isolators integrity should lead to a hold in production, failure investigation (what happened) and risk assessment. Based on this risk assessment  a stop of production and new bio-decontamination might be necessary. A decision tree for potential faults should be developed with rationale.

- Line 2001 - 2002:

Text:	High efficiency particulate air filter with a minimum 0.3 micron particle retaining efficiency of 99.97 percent

Comment:	This definition does not comply with national and international adopted standards (ISO guidelines). Therefore a rephrasing should be done.

Proposal:	HEPA (High efficiency  particulate air) filter in the sense of this guideline means a filter of a certified retention grade of 99.95 as a minimum.

- Line 2008 - 2010:

Text:	Isolator: A decontaminated unit, ...

Comment:	An isolator can be in a status either “bio-decontaminated” or “not bio-decontaminated” (depending on the state of operation or modus); it is not necessary said, that someone can call this installation an isolator only after biodecontamination has been executed. Therefore rephrase in such a way that an isolator in the sense of this guideline is a device being capable of being bio-decontaminated  automatically (this would also comply to ISO 13408-6 and ISO 14644-7).

Proposal:	A device complying to ISO class 5 or higher in operation, being capable of being bio-decontaminated, that provides uncompromised, continuous isolation ...

best regards

Dr. Berthold Düthorn

Director Validation Services

ROBERT BOSCH GmbH

Packaging Technology Division

P.O. Box 1454

D-74554 Crailsheim

Telefon:	+49 (0) 7951 402 - 414

Fax:	+49 (0) 7951 402 - 405

E-Mail:	berthold.duethorn@boschpackaging.com