# Parenteral Society Comments on

Guidance for Industry

Sterile Drug Products Produced by Aseptic Processing   -

Current Good Manufacturing Practice

Draft Guidance

Docket Number 2003 D – 0382

November 2003

## Introduction

The Parenteral Society is a UK based professional not for profit society with approximately 1200 members with a worldwide geographic distribution.

The comments below have been co-ordinated by the Parenteral Society, based on information received from members of the Parenteral Society and other European organisations who are members of the European Sterile Products Confederation (ESPC).

Members of ESPC are APV (Germany), R3 Nordic (Nordic Countries), A3P (France), AEFI (Spain).  In total these organisations represent over 10,000 professionals working in activities related to the pharmaceutical industry.

Parenteral Society

99 Ermin Street

Swindon, Wiltshire

SN3 4NL

England

## Comments

| Comment Number | Page | Line | Comment | Proposal |
| --- | --- | --- | --- | --- |
| 1 | 2 | 22, 23, 70, 71 | The text in lines 70 and 71 is superfluous in that it is already stated in lines 22 and 23 that the document refers to products produced by aseptic processing. | Delete lines 70 and lines 73 thru 78 |
| 2 | 3 | 92, 93 | The sentence commencing Alterminally sterlized drug product…, is out of context. See comment 1. | Delete the sentence in lines 93 and 93 |
| 3 | 3 | 114 | “In such cases” is not a defined situation | Delete “In such cases” |
| 4 | 4 | 127, 128 | The sentence starting “Design of a given area at seq. Is not clear | Replace the sentence with “Microbiological and Particulate Standards are defined in regulations and recommended guidance documents. The activities, equipment, components and products exposed must be appropriate to the types of products being processed and they should be controlled to meet class requirements |
| 5 | 4 | 137 | This line is in conflict with line 176 | Replace “on a routine basis” with “whenever processing operations are being conducted |
| 6 | 5 | 142 | Table: No mention of 5 micron particles Equivalence of ISO and GMP requirements is not clear. Microbiological levels are not stated to be upper or maximum limits | The table should be re-organised to current ISO 14644-1 in first column, superseded FS 209E equivalent in second column and metric equivalent in third column |
| 7 | 5 | 160 | “preserve sterility” is incorrect | Replace “preserve sterility” with “to minimise the risk of contamination” |
| Comment Number | Page | Line | Comment | Proposal |
| 8 | 5 | 172 – 176 | Uses metric and imperial units | Use only S1 units, replace micron with micrometer throughout the document |
| 9 | 5 | 176 | The sentence on this line is out of context and misleading | Delete This level of air cleanliness is also known as class 100 (ISO 5) |
| 10 | 6 | 196 | Laminar flow is not defined in ISO 14644-1 | Replace Laminar flow with unidirectional flow for consistency with ISO 14644 |
| 11 | 7 | 238 | The use of 12.5 pascal is inappropriate Harmonization with the EU 10 – 15pa | Harmonise with EU 10 – 15 pa |
| 12 | 7 | 247 - 250 | These lines can be misinterpreted | Replace the sentence in lines 249 and 250 with “For areas of higher cleanliness, significantly higher air change rates are likely to be required to achieve the required levels of “in-operation” air cleanliness |
| 13 | 7 | 258 | D. Air Filtration is too restrictive | Replace “Air Filtration” with “Filtration of Gases” |
| 14 | 8 | 272 | The sentence commencing “Sterilized holding tanks ---. Is restrictive | Replace with “Sterilized vessels and contained liquids should be maintained under conditions which minimise the possibility of microbial contamination |
| 15 | 8 | 280 | It is not common practice to test filters during processing as this increases manipulations | Replace “and periodically thereafter”, with at “end of use” Delete (e.g. including at end of use) |
| 16 | 8 | 283 | High Efficiency Particulate Air (HEPA) is meaningless | Replace with High Efficiency Particulate Air Filters (HEPA filters) |
| Comment Number | Page | Line | Comment | Proposal |
| 17 | 8 | 288 | Integrity testing of HEPA filters in unidirectional air work stations and critical areas should be carried out twice per year. HEPA filters in other locations should be “in situ” tested once per year. |  |
| 18 | 8 | 297 | Diocytyl phthalate is carcinogenic | Delete diocytyl phthalate (DOP) |
| 19 | 9 | 330 | “can have an effect” is ambiguous | Insert “ adverse” between “an” and “effect” |
| 20 | 10 | 344 | The first sentence is unclear as to its meaning | Replace with “Aseptic processes must be designed, configured and operated to minimise exposure of sterile articles to potential contamination |
| 21 | 11 | 365 | “prefastened” is not a recognised industry word | Use “preassembled” to replace prefastened |
| 22 | 11 | 374 | “---- provide class 100 (ISO 5)” is not adequately descriptive | Replace with “critical area level” |
| 23 | 12 | 403 | The sentence “With rare exceptions, drains are not considered appropriate for classified area of the aseptic processing facility” is not correct. | Replace the sentence with “With rare exceptions, open drains are not appropriate for critical areas. Where drainage is required outside the critical area it is preferable for the waste to be piped to a drain in a less sensitive technical area |
| 24 | 13 | 422 | The process should not only be well designed but also operated and maintained | Replace existing with “A well designed, operated and maintained aseptic process minimises personnel intervention” |
| 25 | 14 | 443 | This line/sentence is redundant | Delete sentence |
| 26 | 15 | 475 | “Only personnel who have been qualified” is incorrect | Replace with “Only personnel who are currently qualified-----“ |
| Comment Number | Page | Line | Comment | Proposal |
| 27 | 15 | 477 | A gown will not “prevent” contamination | Replace “prevent” with “minimise” |
| 28 | 15 | 493/494 | This sentence is not clear | Delete semi-annual. Current industry practice is annual requalification |
| 29 | 17 | 564 - 566 | These lines are too cumbersome | Replace with “Parenteral products are intended to be non pyrogenic. Any component failing to meet defined endotoxial limits must be rejected |
| 30 | 24 | 805 | ISO 13408 requirements should be used in place of current text | Refer to ISO 13408 |
| 31 | 36 | 1292 | The words “species” and “genus” appear to be reversed | Replace with “-----the program should require genus (or where appropriate, species) ------ |
| 32 | 36 | 1309 | The meaning of the sentence is not clear | Start sentence with “The testing of incoming lots ----- |
| 33 | 46 | 1596 | Replace wg with pascal | Use S1 units throughout |
| 34 | 38 – 42 | 1338 - 1499 | The section X1 Sterility Testing is redundant | Delete section. Add one line. For details of sterility testing refer to current United States Pharmacopoeia |
| 35 | 45, 48 | 1547, 1556, 1682 | Text is not clear | Replace with “All breaches of integrity should be investigated. A risk analysis should be conducted if product has or may have been compromised |
| 36 | 46 | 1587 1648 | “Sterilization” is inappropriate in this sentence “Sterilant” is inappropriate | Replace “sterilization” with the word “decontamination” Replace “sterilant” with “decontaminant” |
| 37 | 59 | 2021, 2022 | Laminar flow is not a correct term in this context and is not used in the text. | Delete the definition |