## Meter Data
Potato Storage Consumption Data (recommend minimum 3 years)
Year | 2003
Meter # | 123456
|  | Est | Season
Month | KWH | storage days | Total
Jan | 45000 | 31
Feb | 44000 | 28
Mar | 39000 | 31
Apr | 4320 | 5
May | 520 | 0
Jun | 680
Jul | 440
Aug | 920
Sep | 1880 | 1
Oct | 32000 | 25
Nov | 45600 | 30
Dec | 47800 | 31
Year | 2004
Meter # | 123456
|  | Est | Season
Month | KWH | storage days | Total
Jan | 45500 | 31
Feb | 45000 | 28
Mar | 52000 | 31
Apr | 38500 | 20
May | 3400 | 0 |  | kWh/season
Jun | 7000 | 0 | 197 | 318680
Jul | 13000
Aug | 15000
Sep | 7000 | 0
Oct | 59000 | 25
Nov | 54500 | 30
Dec | 55000 | 31
Total | 394900
Year | 2005
Meter # | 123456
|  | Est | Season
Month | KWH | storage days | Total
Jan | 55000 | 31
Feb | 41000 | 28
Mar | 43000 | 31
Apr | 39000 | 30
May | 13000 | 15
Jun | 1300 | 0 | 221 | 367800
Jul | 1400 | 0
Aug | 1900 | 0
Sep | 1500 | 0
Oct | 35000 | 15
Nov | 55000 | 30
Dec | 52000 | 31
Total | 339100
Avg | 343240 |  | 209
kWh/day | 1642.2967

## Storage VFD
Potato and Onion Storage VFD Analysis
Project Name | XYZ Potato Shed |  | Blue = User Inputs
Contact | Operator 1
Contact Phone No. | 509-527-6211
Location | Walla Walla, WA 99362
Farm Name | Nice Cultivars |  | Utility Provider | Nice REA
Storage Capacity (ton) | 4000 |  | Utility Contact | Good Guy
Storage Capacity (cwt) | 80000 |  | Energy Cost ($/kWh) | 0.05
Design Airflow (cfm/ton) | 20 |  | Avg Energy Consumption | 343240 | (2-3 yr history)
Total Fan HP | 80 |  | Estimated Energy Savings | 64316.2853
Fan Motor Loading (est) | 90% |  | Percent Energy Savings | 18.74% | (range 10-30%)
Fan Motor Efficiency | 95% |  | Energy Cost Savings | 3215.8143
Calculated Fan Use (kW) | 56.5389 |  | Estimated Project Cost | 16000 | ($100-200/HP)
VFD Efficiency | 95% |  | Potential Incentive | 11200 | (may need to adjust formula)
Total Measured Fan (kW) | 54.7 |  | Payback w/o incentive (yr) | 4.9754
Refrigerated (Yes/No) | Yes |  | Payback with incentive (yr) | 1.4926
No VFD (Current) Ventilation System Profile
Storage Phase | Starting Dates | Days | Fans In-Use | Fan Run Time | Calculated Usage | Typical Fan Operation
|  |  | (%) | (hr/day) | (kWh)
Harvest / Load | 2006-09-15 | 5 | 100% | 10 | 2735 | Start fans when loading
Cure / Suberize | 2006-09-20 | 5 | 100% | 24 | 6564 | Continuous/Recirc if no OSA
Ramp to Hold Temp | 2006-09-25 | 40 | 100% | 24 | 52512 | Run Anytime OSA Avail
Winter Holding | 2006-11-04 | 45 | 100% | 24 | 59076 | Run Anytime OSA Avail
Spring Holding | 2006-12-19 | 99 | 100% | 16 | 86644.8 | Run Anytime OSA Avail
Unload | 2007-03-28 | 15 | 100% | 12 | 9846 | Continuous w/ OSA or Refrig
empty | 2007-04-12 | 0 | 100% | 0 | 0 | Run Anytime OSA Avail
Storage Season Length |  | 209 |  | Total = | 217377.8
Estimated VFD Ventilation System Operation Profile
Storage Phase | Starting Dates | Days | Fan Speed | Fan Run Time | Calculated Usage | Typical Fan Operation
|  |  | (%) | (hr/day) | (kWh)
Harvest / Load | 2006-09-15 | 5 | 70% | 10 | 1138.908 | Start fans when loading
Cure / Suberize | 2006-09-20 | 5 | 100% | 24 | 6909.4737 | Continuous/Recirc if no OSA
Ramp to Holding Temp | 2006-09-25 | 40 | 90% | 24 | 42030.5892 | Run Anytime OSA Avail
Winter Holding | 2006-11-04 | 45 | 80% | 24 | 34811.3962 | Run Anytime OSA Avail
Spring Holding | 2006-12-19 | 99 | 75% | 24 | 64754.4236 | Run Anytime OSA Avail
Unload | 2007-03-28 | 15 | 70% | 10 | 3416.7239 | Continuous w/ OSA or Refrig
empty | 2007-04-12 | 0 | 0% | 0 | 0 | Run Anytime OSA Avail
Storage Season Length |  | 209 |  | Total = | 153061.5147
|  |  |  | Estimated Savings = | 64316.2853
Notes:
Use utility billing history to help verify storage time
Work with grower to determine tonnage by month (eg unloading reduces refrigeration need)
If refrigerated storage, the estimated usage above will not match historical utility billing history- allow 30% for refrigeration usage
For these estimates, use 70% as the lowest VFD speed
Savings should be based on kWh per day, however, tonnage may also need to be factored in.
Energy savings may not be reflected on power bill until later in storage season.
For verification of savings, update spreadsheet using actual monthly VFD run time and kWh data and billing history
Formulas:
XYZ Potato Shed = [XYZ Potato Shed, row above]+[Days, row above]