## RESULTS
Table S2-1 NPDES outfall analytical results for 2006
Outfall | TA-bldg | Description | PH(MIN) | PH(MX) |  | TSS (AVG) |  | TSS(MX) |  | CHLORINE(AVG) |  | CHLORINE(MX)
|  |  | SU | SU |  | MG/L |  | MG/L |  | UG/L |  | UG/L
001 | 3-22 | Power Plant 2006
|  | Jan | 7.5 | 7.5 |  | 2 |  | 2 |  | 0 |  | 0
|  | Feb | 7.8 | 7.8 |  | 2 |  | 2 |  | 0 |  | 0
|  | Mar | 7.8 | 7.8 |  | 2 |  | 2 |  | 0 |  | 0
|  | Apr | 8 | 8 | < | 1 | < | 1 |  | 0 |  | 0
|  | May | 7.7 | 7.7 | < | 1 | < | 1 |  | 0 |  | 0
|  | Jun | 7.6 | 7.6 |  | 1 |  | 1 |  | 0 |  | 0
|  | Jul | 7.9 | 7.9 | < | 1 | < | 1 |  | 0 |  | 0
|  | Aug | 7.6 | 7.6 | < | 1 | < | 1 |  | 0 |  | 0
|  | Sep | 7.6 | 7.6 |  | 1 |  | 1 |  | 0 |  | 0
|  | Oct | 7.9 | 7.9 |  | 1 |  | 1 |  | 0 |  | 0
|  | Nov | 7.9 | 7.9 |  | 1 |  | 1 |  | 0 |  | 0
|  | Dec | 7.6 | 7.6 |  | 2 |  | 2 |  | 0 |  | 0
|  |  | 7.5 | 8 | < | 1.3333 | < | 2 |  | 0 |  | 0
Outfall | TA-bldg | Description | PH(MIN) | PH(MX) |  | TSS(AVG) |  | TSS(MX) |  | PHOSPHORUS(AVG) |  | PHOSPHORUS(MX) | SULFITE (AVG) | SULFITE (MX) | IRON (AVG) | IRON (MX)
|  |  | SU | SU |  | MG/L |  | MG/L |  | MG/L |  | MG/L | MG/L | MG/L | MG/L | MG/L
129 | 21-357 | TA-21 Steam Plant 2006
Jan
Feb
|  | Mar | 7.5 | 7.5 | < | 1 | < | 1 |  | 12 |  | 12 | 2 | 2 | 0 | 0
Apr
May
|  | Jun | 7.4 | 7.4 | < | 1 | < | 1 |  | 6 |  | 6 | 2 | 2 | 0 | 0
Jul
Aug
|  | Sep | 7.5 | 7.5 | < | 2 | < | 2 |  | 4 |  | 4 | 8 | 8 | 0 | 0
Oct
Nov
|  | Dec | 7.8 | 7.8 |  | 0 |  | 0 |  | 5 |  | 5 | 5 | 5 | 0 | 0
|  |  | 7.4 | 7.8 | < | 1 | < | 2 |  | 6.75 |  | 12 | 4.25 | 8 | 0 | 0
Outfall Number | TA-bldg | Description | PH(MIN) | PH(MX) |  | TSS(AVG) |  | TSS(MX) |  | PHOSPHORUS(AVG) |  | PHOSPHORUS(MX) | CHLORINE (AVG) | CHLORINE (MX)
|  |  | SU | SU |  | MG/L |  | MG/L |  | MG/L |  | MG/L | UG/L | UG/L
03A021 | 3-29 | CMR Air Washers
Jan
Feb
(NO DISCHARGE) Mar
Apr
May
|  | Jun | 8.4 | 8.4 | < | 1 | < | 1 |  | 1 |  | 1 | 0 | 0
Jul
Aug
|  | Sep | 7.2 | 7.2 |  | 6 |  | 6 |  | 1 |  | 1 | 0 | 0
Oct
Nov
|  | Dec | 8 | 8 |  | 1 |  | 1 |  | 0 |  | 0 | 0 | 0
|  |  | 7.2 | 8.4 | < | 2.6667 | < | 6 |  | 0.66667 |  | 1 | 0 | 0
Outfall Number | TA-bldg | Description | PH(MIN) | PH(MX) |  | TSS(AVG) |  | TSS(MX) |  | PHOSPHORUS(AVG) |  | PHOSPHORUS(MX) | CHLORINE (AVG) | CHLORINE (MX)
|  |  | SU | SU |  | MG/L |  | MG/L |  | MG/L |  | MG/L | UG/L | UG/L
03A022 | 3-2238 | Sigma Cooling Tower
Jan
Feb
|  | Mar | 7.9 | 7.9 | < | 1 | < | 1 |  | 2 |  | 2 | 0 | 0
Apr
May
|  | Jun | 8 | 8 |  | 1 |  | 1 |  | 2 |  | 2 | 0 | 0
Jul
Aug
|  | Sep | 8.6 | 8.6 | < | 1 | < | 1 |  | 4 |  | 4 | 0 | 0
Oct
Nov
|  | Dec | 8.9 | 8.9 | < | 1 | < | 1 |  | 2 |  | 2 | 0 | 0
|  |  | 7.9 | 8.9 | < | 1 | < | 1 |  | 2.5 |  | 4 | 0 | 0
Outfall Number | TA-bldg | Description | PH(MIN) | PH(MX) |  | TSS(AVG) |  | TSS(MX) |  | PHOSPHORUS(AVG) |  | PHOSPHORUS(MX) | CHLORINE (AVG) | CHLORINE (MX)
|  |  | SU | SU |  | MG/L |  | MG/L |  | MG/L |  | MG/L | UG/L | UG/L
03A027 | 3-2327 | Strategic Computing Complex Cooling Tower
Jan
Feb
|  | Mar | 8.4 | 8.4 |  | 2 |  | 2 |  | 3 |  | 3 | 0 | 0
Apr
May
|  | Jun | 8.5 | 8.5 |  | 2 |  | 2 |  | 4 |  | 4 | 0 | 0
Jul
Aug
|  | Sep | 8.5 | 8.5 |  | 1 |  | 1 |  | 3 |  | 3 | 0 | 0
Oct
Nov
|  | Dec | 8.9 | 8.9 | < | 1 | < | 1 |  | 4 |  | 4 | 0 | 0
|  |  | 8.4 | 8.9 | < | 1.5 | < | 2 |  | 3.5 |  | 4 | 0 | 0
Outfall Number | TA-bldg | Description | PH(MIN) | PH(MX) |  | TSS(AVG) |  | TSS(MX) |  | PHOSPHORUS(AVG) |  | PHOSPHORUS(MX) | CHLORINE (AVG) | CHLORINE (MX)
|  |  | SU | SU |  | MG/L |  | MG/L |  | MG/L |  | MG/L | UG/L | UG/L
03A028 | 15-202 | PHERMEX Cooling Tower
Jan
Feb
(NO DISCHARGE) Mar
Apr
May
(SAMPLE MISSED) Mar
Jul
Aug
(NO DISCHARGE) Mar
Oct
Nov
(NO DISCHARGE) Mar
Outfall Number | TA-bldg | Description | PH(MIN) | PH(MX) |  | TSS(AVG) |  | TSS(MX) |  | COPPER(A VG) |  | COPPER(MAX) | PHOSPHORUS(AVG) | PHOSPHORUS(MX) | CHLORINE (AVG) | CHLORINE (MX)
|  |  | SU | SU |  | MG/L |  | MG/L |  | MG/L |  | MG/L | MG/L | MG/L | UG/L | UG/L
03A048 | 53-963/978 | LANSCE Cooling Tower
Jan
Feb
|  | Mar | 8.7 | 8.7 | < | 1 | <1 | 1 |  | 0 |  | 0 | 0 | 0 | 0 | 0
Apr
May
|  | Jun | 8.8 | 8.8 | < | 1 | < | 1 |  | 0 |  | 0 | 0 | 0 | 0 | 0
Jul
Aug
|  | Sep | 8.2 | 8.2 | < | 1 | < | 1 |  | 0 |  | 0 | 0 | 0 | 0 | 0
Oct
Nov
|  | Dec | 8.7 | 8.7 | < | 2 | < | 2 |  | 0.002 |  | 0.002 | 0 | 0 | 0 | 0
|  |  | 8.2 | 8.8 |  | 1.25 |  | 2 |  | 0.0005 |  | 0.002 | 0 | 0 | 0 | 0
Outfall Number | TA-bldg | Description | PH(MIN) | PH(MX) |  | TSS(AVG) |  | TSS(MX) |  | PHOSPHORUS(AVG) |  | PHOSPHORUS(MX) | CHLORINE (AVG) | CHLORINE (MX)
|  |  | SU | SU |  | MG/L |  | MG/L |  | MG/L |  | MG/L | UG/L | UG/L
03A113 | 53-293/952 | LANSCE Cooling Tower
Jan
Feb
|  | Mar | 7.6 | 7.6 |  | 3 |  | 3 |  | 0 |  | 0 | 0 | 0
Apr
May
|  | Jun | 7.2 | 7.2 |  | 1 |  | 1 |  | 0 |  | 0 | 0 | 0
Jul
Aug
|  | Sep | 8.1 | 8.1 | < | 1 | < | 1 |  | 0 |  | 0 | 0 | 0
Oct
Nov
|  | Dec | 7.8 | 7.8 | < | 3 | < | 3 |  | 0 |  | 0 | 0 | 0
|  |  | 7.2 | 8.1 | < | 2 | < | 3 |  | 0 |  | 0 | 0 | 0
Outfall Number | TA-bldg | Description | PH(MIN) | PH(MX) |  | TSS(AVG) |  | TSS(MX) |  | PHOSPHORUS(AVG) |  | PHOSPHORUS(MX) | CHLORINE (AVG) | CHLORINE (MX)
|  |  | SU | SU |  | MG/L |  | MG/L |  | MG/L |  | MG/L | UG/L | UG/L
03A158 | 21-209 | TA-21 CoolingTower
Jan
Feb
|  | Mar | 8 | 8 |  | 3 |  | 3 |  | 0 |  | 0 | 0 | 0
Apr
May
|  | Jun | 7.6 | 7.6 | < | 2 | < | 2 |  | 0 |  | 0 | 0 | 0
Jul
Aug
|  | Sep | 8.2 | 8.2 | < | 1 | < | 1 |  | 0 |  | 0 | 0 | 0
Oct
Nov
|  | Dec | 8 | 8 | < | 2 | < | 2 |  | 0 |  | 0 | 0 | 0
|  |  | 7.6 | 8.2 | < | 2 | < | 3 |  | 0 |  | 0 | 0 | 0
Outfall Number | TA-bldg | Description | PH(MIN) | PH(MX) |  | TSS(AVG) |  | TSS(MX) |  | PHOSPHORUS(AVG) |  | PHOSPHORUS(MX) | CHLORINE (AVG) | CHLORINE (MX)
|  |  | SU | SU |  | MG/L |  | MG/L |  | MG/L |  | MG/L | UG/L | UG/L
03A160 | 35-124 | National High Magnetic Field Laboratory Cooling Tower
Jan
Feb
|  | Mar | 8.7 | 8.7 |  | 26 |  | 41 |  | 0 |  | 0 | 0 | 0
Apr
May
|  | Jun | 8.5 | 8.5 | < | 1 | < | 1 |  | 0 |  | 0 | 0 | 0
Jul
Aug
|  | Sep | 8.8 | 8.8 | < | 1 | < | 1 |  | 0 |  | 0 | 0 | 0
Oct
Nov
|  | Dec | 8.8 | 8.8 |  | 1 |  | 1 |  | 0 |  | 0 | 0 | 0
|  |  | 8.5 | 8.8 | < | 7.25 | < | 41 |  | 0 |  | 0 | 0 | 0
Outfall Number | TA-bldg | Description | PH(MIN) | PH(MX) |  | TSS(AVG) |  | TSS(MX) |  | PHOSPHORUS(AVG) |  | PHOSPHORUS(MX) | CHLORINE (AVG) | CHLORINE (MX)
|  |  | SU | SU |  | MG/L |  | MG/L |  | MG/L |  | MG/L | UG/L | UG/L
03A181 | 55-6 | Plutonium Facility Cooling Tower
|  | Jan | 8.8 | 8.8 |  | 2 |  | 2 |  | 4 |  | 4 | 0 | 0
Feb
Mar
Apr
|  | May | 8.7 | 8.7 |  | 1 |  | 1 |  | 3 |  | 3 | 0 | 0
Jun
Jul
Aug
|  | Sep | 8.5 | 8.5 | < | 1 | < | 1 |  | 0 |  | 0 | 0 | 0
Oct
Nov
|  | Dec | 8.8 | 8.8 |  | 2 |  | 2 |  | 4 |  | 4 | 0 | 0
|  |  | 8.5 | 8.8 | < | 1.5 | < | 2 |  | 2.3333 |  | 4 | 0 | 0
Outfall Number | TA-bldg | Description | PH(MIN) | PH(MX) |  | TSS(AVG) |  | TSS(MX) |  | PHOSPHORUS(AVG) |  | PHOSPHORUS(MX) | CHLORINE (AVG) | CHLORINE (MX)
|  |  | SU | SU |  | MG/L |  | MG/L |  | MG/L |  | MG/L | UG/L | UG/L
03A185 | 15-312 | DARHT Cooling Tower
Jan
Feb
|  | Mar | 8.8 | 8.8 |  | 4 |  | 4 |  | 2 |  | 2 | 0 | 0
Apr
May
|  | Jun | 8.7 | 8.7 |  | 1 |  | 1 |  | 3 |  | 3 | 0 | 0
Jul
Aug
|  | Sep | 8.4 | 8.4 |  | 5 |  | 5 |  | 3 |  | 3 | 2200 | 2200
Oct
Nov
|  | Dec | 8.8 | 8.8 | < | 3 | < | 3 |  | 3 |  | 3 | 0 | 0
|  |  | 8.4 | 8.8 | < | 3.25 | < | 5 |  | 2.75 |  | 3 | 550 | 2200
Outfall Number | TA-bldg | Description | PH(MIN) | PH(MX) |  | TSS(AVG) |  | TSS(MX) |  | PHOSPHORUS(AVG) |  | PHOSPHORUS(MX) | CHLORINE (AVG) | CHLORINE (MX)
|  |  | SU | SU |  | MG/L |  | MG/L |  | MG/L |  | MG/L | UG/L | UG/L
03A199 | 3-1837 | Laboratory Data Communications Center
Jan
Feb
|  | Mar | 8.8 | 8.8 |  | 1 |  | 1 |  | 4 |  | 4 | 0 | 0
Apr
May
|  | Jun | 8.7 | 8.7 |  | 10 |  | 10 |  | 3 |  | 3 | 0 | 0
Jul
Aug
|  | Sep | 8.6 | 8.6 | < | 1 | < | 1 |  | 3 |  | 3 | 0 | 0
Oct
Nov
|  | Dec | 8.8 | 8.8 | < | 2 | < | 2 |  | 4 |  | 4 | 0 | 0
|  |  | 8.6 | 8.8 | < | 3.5 | < | 10 |  | 3.5 |  | 4 | 0 | 0
Outfall Number | TA-bldg | Description | PH(MIN) | PH(MX) |  | COD(AVG) |  | COD(MX) |  | TSS(AVG) |  | TSS(MX) | CADMIUM (AVG) | CADMIUM (MX) | CHROMIUM (AVG) | CHROMIUM (MX) |  | COPPER (AVG) |  | COPPER (MAX) | LEAD (AVG) | LEAD (MX) | NICKEL (AVG) | NICKEL (MAX) | ZINC (AVG) | ZINC (MX) | MERCURY (AVG) | MERCURY (MX) | TTOS (AVG) | TTOS (MX)
|  |  | SU | SU |  | MG/L |  | MG/L |  | MG/L |  | MG/L | UG/L | UG/L | MG/L | MG/L |  | MG/L |  | MG/L | UG/L | UG/L | MG/L | MG/L | MG/L | MG/L | UG/L | UG/L | MG/L | MG/L
051 | 50-1 | TA-50 Radioactive Liquid Waste Treatment Facility
|  | Jan | 6.2 | 8.3 |  | 11 |  | 28 | < | 1 | < | 1 | 0 | 0 | 0 | 0 |  | 0.002 |  | 0.012 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Feb | 6.3 | 7.5 | < | 4 | < | 4 | < | 1 | < | 1 | 0 | 0 | 0 | 0 |  | 0.007 |  | 0.015 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Mar | 6.1 | 7 |  | 11 |  | 17 | < | 1 | < | 1 | 0 | 0 | 0 | 0 |  | 0.016 |  | 0.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Apr | 6.3 | 7.7 | < | 19 | < | 38 | < | 1 | < | 1 | 0 | 0 | 0 | 0 |  | 0.005 |  | 0.019 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | May | 6.3 | 7.1 |  | 13 |  | 20 | < | 1 | < | 1 | 0 | 0 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Jun | 6.5 | 7.2 |  | 13 |  | 20 | < | 1 | < | 1 | 0 | 0 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0.02 | 0.02 | 0 | 0 | 0 | 0 | 0 | 0
|  | Jul | 6.9 | 7.7 |  | 10 |  | 17 | < | 1 | < | 1 | 0 | 0 | 0 | 0 |  | 0.009 |  | 0.01 | 0 | 0 | 0.0072 | 0.0072 | 0 | 0 | 0 | 0 | 0 | 0
|  | Aug | 6 | 8.2 | < | 7 | < | 13 | < | 1 | < | 1 | 0 | 0 | 0 | 0 |  | 0.003 |  | 0.019 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Sep | 6.4 | 7.2 | < | 7.19 | < | 9.71 | < | 1 | < | 1 | 0 | 0 | 0 | 0 |  | 0.009 |  | 0.021 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Oct | 6.9 | 7.5 | < | 10 |  | 19 | < | 2 | < | 2 | 0 | 0 | 0 | 0 |  | 0.022 |  | 0.024 | 0 | 0 | 0.028 | 0.028 | 0 | 0 | 0 | 0 | 0 | 0
|  | Nov | 7 | 8 | < | 6 | < | 6 | < | 6 | < | 14 | 0 | 0 | 0 | 0 |  | 0.041 |  | 0.066 | 0 | 0 | 0.035 | 0.035 | 0 | 0 | 0 | 0 | 0 | 0
|  | Dec | 6.3 | 7.3 |  | 8 |  | 10 | < | 2 | < | 2 | 0 | 0 | 0 | 0 |  | 0.077 |  | 0.078 | 0 | 0 | 0.011 | 0.011 | 0.01 | 0.03 | 0 | 0 | 0 | 0
|  |  | 6 | 8.3 | < | 9.9325 | < | 38 | < | 1.5833 | < | 14 | 0 | 0 | 0 | 0 |  | 0.015917 |  | 0.078 | 0 | 0 | 0.0084333 | 0.035 | 0.00083333 | 0.03 | 0 | 0 | 0 | 0
Outfall Number | TA-bldg | Description | PH(MIN) | PH(MX) |  | RDX(AVG) |  | RDX(MX) |  | TSS(AVG) |  | TSS(MX) | O&G (AVG) | O&G (MX) | TTO (AVG) | TTO (MX) |  | TNT (AVG) |  | TNT (MX)
|  |  | SU | SU |  | UG/L |  | UG/L |  | MG/L |  | MG/L | MG/L | MG/L | MG/L | MG/L |  | MG/L |  | MG/L
05A055 | 16-1508 | High Explosives Wastewater Treatment Facility
Jan
Feb
Mar
Apr
|  | May |  |  |  | 29.6 |  | 29.6
|  | Jun | 7.2 | 7.2 |  |  |  |  | < | 1 | < | 1 | 10 | 10 | 0 | 0 | < | 0.001 | < | 0.001
Jul
|  | Aug |  |  |  | 87 |  | 87
|  | Sep | 7 | 7 |  | 121 |  | 121 |  | 0 |  | 0 | 9 | 9 | 0 | 0 |  | 0.001 |  | 0.001
Oct
Nov
Dec
|  |  | 7 | 7.2 |  | 79.2 |  | 121 | < | 0.5 | < | 1 | 9.5 | 10 | 0 | 0 | < | 0.001 | < | 0.001
Outfall Number | TA-bldg | Description | PH(MIN) | PH(MX) |  | BOD (AVG) |  | BOD (MX) |  | BOD (AVG) |  | BOD (MX) | TSS (AVG) | TSS (MX) | TSS (AVG) | TSS (MAX) |  | FECAL COL (AVG) |  | FECAL COL (MX)
|  |  | SU | SU |  | LB/DY |  | LB/DY |  | MG/L |  | MG/L | LB/DY | LB/DY | MG/L | MG/L |  | #100ML |  | #100ML
13S | 46-347 | Sanitary Wastewater Treatment Plant
|  | Jan | 7.1 | 7.4 |  | 5 |  | 6 |  | 2 |  | 2 | 1 | 1 | 0 | 0 |  | 1 |  | 1
|  | Feb | 7.2 | 7.4 | < | 5 | < | 5 | < | 2 | < | 2 | 7 | 7 | 3 | 3 |  | 4 |  | 4
|  | Mar | 7.2 | 7.3 |  | 4 |  | 5 |  | 2 |  | 2 | 4 | 4 | 2 | 2 |  | 3 |  | 3
|  | Apr | 7.2 | 7.3 | < | 5 | < | 5 | < | 2 | < | 2 | 9 | 9 | 4 | 4 |  | 1 |  | 1
|  | May | 7.2 | 7.3 | < | 4 | < | 4 | < | 2 | < | 2 | 4 | 4 | 2 | 2 |  | 1 |  | 1
|  | Jun | 7.1 | 7.4 |  | 5 |  | 5 |  | 2 |  | 2 | 6 | 6 | 3 | 3 |  | 7 |  | 7
|  | Jul | 7.2 | 7.4 |  | 5 |  | 6 | < | 2 | < | 2 | 3 | 3 | 1 | 1 |  | 1 |  | 1
|  | Aug | 7.1 | 7.3 |  | 6 |  | 7 |  | 2 |  | 2 | 4 | 4 | 1 | 1 |  | 3 |  | 3
|  | Sep | 7.3 | 7.4 | < | 4 | < | 5 | < | 2 | < | 2 | 6 | 6 | 3 | 3 |  | 13 |  | 13
|  | Oct | 7 | 7.2 | < | 6 | < | 6 | < | 2 | < | 2 | 6 | 6 | 2 | 2 |  | 3 |  | 3
|  | Nov | 7.3 | 7.4 | < | 5 | < | 5 | < | 2 | < | 2 | 8 | 8 | 3 | 3 |  | 12 |  | 12
|  | Dec | 7.2 | 7.4 |  | 4 |  | 4 |  | 2 |  | 2 | 14 | 14 | 7 | 7 |  | 5 |  | 5
|  |  | 7 | 7.4 | < | 4.8333 | < | 7 | < | 2 | < | 2 | 6 | 14 | 2.5833 | 7 |  | 4.5 |  | 13
Note on C196: MST User: