# PART IX – DRAINAGE

### ITEM D-701   PIPE FOR STORM DRAINS AND CULVERTS

DESCRIPTION

701-1.1  This item shall consist of the construction of pipe culverts and storm drains in accordance with these specifications and in reasonably close conformity with the lines and grades shown on the plans.

MATERIALS

701-2.1  Materials shall meet the requirements shown on the plans and specified below.

* * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * *

The Engineer should indicate the required class, schedule, SDR, gage, and/or strength of pipe desired.

* * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * *

701-2.2  PIPE.  The pipe shall be of the type called for on the plans or in the proposal and shall be in accordance with the following appropriate requirements.

Metallic Coated Corrugated Steel Pipe (Type I, IR or II)	ASTM A 760

Galvanized Steel Corrugated Structural Plates

and Fasteners for Pipe, Pipe-Arches, and Arches	ASTM A 761

Polymer Precoated Corrugated Steel Pipe for Sewers and Drains	ASTM A 762

Post-Coated and Lined (Bituminous or Concrete)

Corrugated Steel Sewer and Drainage Pipe	ASTM A 849

Steel Sheet, Zinc and Aramid Fiber Composite Coated for

Corrugated Steel Sewer, Culvert, and Underdrain Pipe	A885/A885M-96

Corrugated Aluminum Alloy Culvert Pipe	ASTM B 745

Non-Reinforced Concrete Pipe	ASTM C 14

Reinforced Concrete Pipe	ASTM C 76

Reinforced Concrete D-Load Pipe	ASTM C 655

Reinforced Concrete Arch Pipe	ASTM C 506

Reinforced Concrete Elliptical Pipe	ASTM C 507

Precast Reinforced Concrete Box Sections	ASTM C 789 and C 850

Poly (Vinyl Chloride) Ribbed Drain Pipe & Fittings	ASTM F 794

Based on Controlled Inside Diameter

Poly (Vinyl Chloride) (PVC) Corrugated Sewer Pipe	ASTM F 949

With a Smooth Interior and Fittings

Bituminous-Coated Corrugated Metal Pipe and Pipe Arches	AASHTO M 190

Bituminous-Coated Corrugated Aluminum Alloy Culvert Pipe	AASHTO M 190 and M 196

Bituminous-Coated Structural Plate Pipe, Pipe Arch, and Arches	AASHTO M 167 and M 243

Aluminum Alloy Structural Plate for Pipe, Pipe Arch, and Arches	AASHTO M 219

Polyvinyl Chloride (PVC) Pipe	ASTM D 3034

Corrugated Polyethylene Drainage Tubing (all types)	AASHTO M 252

Corrugated Polyethylene Pipe 300 to 1200 mm Diameter (all types)	AASHTO M 294M

Poly (Vinyl Chloride) (PVC) Profile Wall Drain Pipe and Fittings Based	AASHTO M 304

on Controlled Inside Diameter

* * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * *

The Engineer shall select the pipe used for the project and may delete inappropriate requirements from paragraph 701-2.2 and from the list of material requirements.

* * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * *

701-2.3  CONCRETE.  Concrete for pipe cradles shall have a minimum compressive strength of 2000 psi (13.8 MPa) at 28 days and conform to the requirements of ASTM C 94.

701-2.4  RUBBER GASKETS.  Rubber gaskets for rigid pipe shall conform to the requirements of ASTM C 443.  Rubber gaskets for PVC pipe and polyethylene pipe shall conform to the requirements of ASTM F 477.  Rubber gaskets for zinc-coated steel pipe and precoated galvanized pipe shall conform to the requirements of ASTM D 1056, for the "RE'' closed cell grades.

701-2.5  JOINT MORTAR.  Pipe joint mortar shall consist of one part portland cement and two parts sand.  The portland cement shall conform to the requirements of ASTM C 150, Type I.  The sand shall conform to the requirements of ASTM C 144.

701-2.6  JOINT FILLERS.  Poured filler for joints shall conform to the requirements of ASTM D 1190.

701-2.7  PLASTIC GASKETS.  Plastic gaskets shall conform to the requirements of AASHTO M 198 (Type B).

* * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * *

ASTM C 789 and C 850 are primarily manufacturing specifications.  The box section dimensions, compressive strength of the concrete, and reinforcement details shown in the specifications have been designed for a combined earth dead load and AASHTO HS20 live load condition.  A modified design will be necessary when aircraft loadings are greater than HS20 live loads.

* * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * *

[701-2.8.  CONTROLLED LOW STRENGTH MATERIAL (CLSM).   Controlled low strength material shall conform to the requirements of Item P-153.  When CLSM is used all joints shall have gaskets.

* * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * *

Specification Item P-153 Controlled Low Strength Material (CLSM)contains guidance for use of CLSM.  The locations where CLSM is permitted shall be shown on the plans.  This paragraph and the option to allow Item P-153 in paragraph 701-3.5 must agree.

* * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * *

CONSTRUCTION METHODS

701-3.1  EXCAVATION.  The width of the pipe trench shall be sufficient to permit satisfactory jointing of the pipe and thorough tamping of the bedding material under and around the pipe, but it shall not be less than the external diameter of the pipe plus 6 inches (150 mm) on each side.  The trench walls shall be approximately vertical.

Where rock, hardpan, or other unyielding material is encountered, the Contractor shall remove it from below the foundation grade for a depth of at least 12 inches (300 mm) or one-half inch (12 mm) for each foot of fill over the top of the pipe (whichever is greater) but for no more than three-quarters of the nominal diameter of the pipe.  The width of the excavation shall be at least 1 foot (30 cm) greater than the horizontal outside diameter of the pipe.  The excavation below grade shall be backfilled with selected fine compressible material, such as silty clay or loam, and lightly compacted in layers not over 6 inches (150 mm) in uncompacted depth to form a uniform but yielding foundation.

Where a firm foundation is not encountered at the grade established, due to soft, spongy, or other unstable soil, the unstable soil shall be removed and replaced with approved granular material for the full trench width.  The Engineer shall determine the depth of removal necessary.  The granular material shall be compacted to provide adequate support for the pipe.

The excavation for pipes that are placed in embankment fill shall not be made until the embankment has been completed to a height above the top of the pipe as shown on the plans.

701-3.2  BEDDING.  The pipe bedding shall conform to the class specified on the plans.  When no bedding class is specified or detailed on the plans, the requirements for Class C bedding shall apply.

a.  Rigid Pipe.  Class A bedding shall consist of a continuous concrete cradle conforming to the plan details.

Class B bedding shall consist of a bed of granular material having a thickness of at least 6 inches (150 mm) below the bottom of the pipe and extending up around the pipe for a depth of not less than 30 percent of the pipe's vertical outside diameter.  The layer of bedding material shall be shaped to fit the pipe for at least 10 percent of the pipe's vertical diameter and shall have recesses shaped to receive the bell of bell and spigot pipe.  The bedding material shall be sand or selected sandy soil, all of which passes a 3/8 inch (9 mm) sieve and not more than 10 percent of which passes a No. 200 (0.075 mm) sieve.

Class C bedding shall consist of bedding the pipe in its natural foundation to a depth of not less than 10 percent of the pipe's vertical outside diameter.  The bed shall be shaped to fit the pipe and shall have recesses shaped to receive the bell of bell and spigot pipe.

b.  Flexible Pipe.  For flexible pipe, the bed shall be roughly shaped to fit the pipe, and a bedding blanket of sand or fine granular material shall be provided as follows:

Pipe Corrugation Depth				Minimum Bedding Depth

in.		mm				in.		mm

1/2		12.5				1 		25.0

1		25.0				2		50.0

2		50.0				3		75.0

2-1/2		62.5				3-1/2		87.5

c.  PVC and Polyethylene Pipe.  For PVC and polyethylene pipe, the bedding material shall consist of coarse sands and gravels with a maximum particle size of 3/4-inch (13 mm).  For pipes installed under paved areas, no more than 12 percent of the material shall pass the No. 200 (0.075 mm) sieve.  For all other areas, no more than 50 percent of the material shall pass the No. 200 (0.075 mm) sieve.  The bedding shall have a thickness of at least 6 inches (150 mm) below the bottom of the pipe and extend up around the pipe for a depth of not less than 50 percent of the pipe's vertical outside diameter.

701-3.3  LAYING PIPE.  The pipe laying shall begin at the lowest point of the trench and proceed upgrade.  The lower segment of the pipe shall be in contact with the bedding throughout its full length.  Bell or groove ends of rigid pipes and outside circumferential laps of flexible pipes shall be placed facing upgrade.

Paved or partially lined pipe shall be placed so that the longitudinal center line of the paved segment coincides with the flow line.

Elliptical and elliptically reinforced pipes shall be placed with the manufacturer's top of pipe mark within five degrees of a vertical plane through the longitudinal axis of the pipe.

701-3.4  JOINING PIPE.  Joints shall be made with (1) portland cement mortar, (2) portland cement grout, (3) rubber gaskets, (4) plastic gaskets, or (5) coupling bands.

Mortar joints shall be made with an excess of mortar to form a continuous bead around the outside of the pipe and shall be finished smooth on the inside.  Molds or runners shall be used for grouted joints in order to retain the poured grout.  Rubber ring gaskets shall be installed to form a flexible watertight seal.

a.  Concrete Pipe.  Concrete pipe may be either bell and spigot or tongue and groove.  The method of joining pipe sections shall be such that the ends are fully entered and the inner surfaces are reasonably flush and even.  Joints shall be thoroughly wetted before mortar or grout is applied.

b.  Metal Pipe.  Metal pipe shall be firmly joined by form fitting bands conforming to the requirements of ASTM A 760 for steel pipe and AASHTO M 196 for aluminum pipe.

c.  PVC and Polyethylene Pipe.  Joints for PVC and Polyethylene pipe shall conform to the requirements of ASTM D 3212 when water tight joints are required.  Joints for PVC and Polyethylene pipe shall conform to the requirements of AASHTO M 304 when soil tight joints are required.  Fittings for polyethylene pipe shall conform to the requirements of AASHTO M 252 or M 294M.

701-3.5  BACKFILLING.  Pipes shall be inspected before any backfill is placed; any pipes found to be out of alignment, unduly settled, or damaged shall be removed and relaid or replaced at the Contractor's expense.

Material for backfill shall be fine, readily compatible soil, granular material selected from the excavation or a source of the Contractor's choosing[, or shall meet the requirements of  Item P-153].  .  It shall not contain frozen lumps, stones that would be retained on a 2-inch (50.0 mm) sieve, chunks of highly plastic clay, or other objectionable material.  No less than 95 percent of a granular backfill material shall pass through a 1/2 inch (12 mm) sieve, and no less than 95 percent of it shall be retained on a No. 4 (4.75 mm) sieve.

When the top of the pipe is even with or below the top of the trench, the backfill shall be compacted in layers not exceeding 6 inches (150 mm) on both sides of the pipe and shall be brought up one foot (30 cm) above the top of the pipe or to natural ground level, whichever is greater.  Care shall be exercised to thoroughly compact the backfill material under the haunches of the pipe.  Material shall be brought up evenly on both sides of the pipe.

When the top of the pipe is above the top of the trench, the backfill shall be compacted in layers not exceeding 6 inches (150 mm) and shall be brought up evenly on both sides of the pipe to 1 foot (30 cm) above the top of the pipe.  The width of backfill on each side of the pipe for the portion above the top of the trench shall be equal to twice the pipe's diameter of 12 feet (3.5 m), whichever is less.

For PVC and polyethylene pipe, the backfill shall be placed in two stages; first to the top of the pipe and then at least 12 inches (300 mm) over the top of the pipe.  The backfill material shall meet the requirements of paragraph 701-3.2c.

All backfill shall be compacted to the density required under Item P-152.

METHOD OF MEASUREMENT

701-4.1  The length of pipe shall be measured in linear feet (meters) of pipe in place, completed, and approved.  It shall be measured along the centerline of the pipe from end or inside face of structure to the end or inside face of structure, whichever is applicable.  The several classes, types and size shall be measured separately.  All fittings shall be included in the footage as typical pipe sections in the pipe being measured.

701-4.2  The volume of concrete for pipe cradles to be paid for shall be the number of cubic yards (cubic meters) of concrete that is completed in place and accepted.

701-4.3  The volume of rock to be paid for shall be the number of cubic yards (cubic meters) of rock excavated.  No payment shall be made for the cushion material placed for the bed of the pipe.

BASIS OF PAYMENT

701-5.1  Payment will be made at the contract unit price per linear foot (meter) for each kind of pipe of the type and size designated; at the contract unit price per cubic yard (cubic meter) of concrete for pipe cradles; and at the contract unit price per cubic yard (cubic meter) for rock excavation.

These prices shall fully compensate the Contractor for furnishing all materials and for all preparation, excavation, and installation of these materials; and for all labor, equipment, tools, and incidentals necessary to complete the item.

Payment will be made under:

Item 701-5.1	[    ] inch [    ] per linear foot (meter)

Item 701-5.2	Concrete for pipe cradles—per cubic yard (cubic meter)

Item 701-5.3	Rock excavation—per cubic yard (cubic meter)

* * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * *

The Engineer shall specify the size and type of pipe for each pipe size specified in the plans.

* * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * *

MATERIAL REQUIREMENTS

ASTM A 760	Corrugated Steel Pipe, Metallic-Coated for Sewers and Drains

ASTM A 761	Corrugated Steel Structural Plate, Zinc Coated, for Field-Bolted Pipe, Pipe-Arches, and Arches

ASTM A 762	Corrugated Steel-Pipe, Polymer Precoated for Sewers and Drains

ASTM A 849	Post-Applied Coatings, Pavings, and Linings for Corrugated Steel Sewer and

Drainage Pipe

ASTM A 885/A 885M-96	Steel Sheet, Zinc and Aramid Fiber Composite Coated for Corrugated Steel Sewer, Culvert, and Underdrain Pipe

ASTM B 745	Corrugated Aluminum Alloy Culvert Pipe

ASTM C 14	Concrete Sewer, Storm Drain, and Culvert Pipe

ASTM C 76	Reinforced Concrete Culvert, Storm Drain, and Sewer Pipe

ASTM C 94	Ready Mixed Concrete

ASTM C 144	Aggregate for Masonry Mortar

ASTM C 150	Portland Cement

ASTM C 443	Joints for Circular Concrete Sewer and Culvert Pipe, Using Rubber Gaskets

ASTM C 506	Reinforced Concrete Arch Culvert, Storm Drain, and Sewer Pipe

ASTM C 507	Reinforced Concrete Elliptical Culvert, Storm Drain and Sewer Pipe

ASTM C 655	Reinforced Concrete D-Load Culvert, Storm Drain and Sewer Pipe

ASTM C 1433	Precast Reinforced Concrete Box Sections for Culverts, Storm Drains, and Sewers

ASTM D 1056	Flexible Cellular Materials—Sponge or Expanded Rubber

ASTM D 3034	Type PSM Poly (Vinyl Chloride) (PVC) Sewer Pipe and Fittings

ASTM D 3212	Joints for Drain and Sewer Plastic Pipes Using Flexible Elastomeric Seals

ASTM D 6690	Joint and Crack Sealants, Hot-Applied, for Concrete and Asphalt Pavements

ASTM F 477	Elastomeric Seals (Gaskets) for Joining Plastic Pipe

ASTM F 794	Poly (Vinyl Chloride) Ribbed Drain Pipe & Fittings Based on Controlled Inside Diameter

ASTM F 949	Poly (Vinyl Chloride) (PVC) Corrugated Sewer Pipe With a Smooth Interior and Fittings

AASHTO M 190	Bituminous-Coated Corrugated Metal Culvert Pipe and Pipe Arches

AASHTO M 196	Corrugated Aluminum Alloy Culverts and Underdrains

AASHTO M 198	Joints for Circular Concrete Sewer and Culvert Pipe Using Flexible Watertight Gaskets

AASHTO M 219	Aluminum Alloy Structural Plate for Pipe, Pipe-Arches, and Arches

AASHTO M 243	Field Applied Coating of Corrugated Metal Structural Plate for Pipe, Pipe-Arches, and Arches

AASHTO M 252	Corrugated Polyethylene Drainage Tubing

AASHTO M 294M	Corrugated Polyethylene Pipe, 300 to 1200 mm Diameter

AASHTO M 304	Poly (Vinyl Chloride) (PVC) Profile Wall Drain Pipe and Fittings Based on Controlled Inside Diameter

END ITEM D-701

Intentionally Left Blank