May 2006

CLICK HERE TO

OPEN DOCUMENT

http://www.va.gov/facmgt/standard/manuals_arch.asp			PG-18-10

Blank page left intentionally

Table of Contents

CHAPTER 1: GENERAL REQUIREMENTS

1.1	PURPOSE

1.2	VA ARCHITECTURAL STANDARDS AND CRITERIA

1.3	OTHER CODES AND STANDARDS

1.4	UNIFORM FEDERAL ACCESSIBILITY STANDARDS AND VA ACCESSIBILITY REQUIREMENTS

1.5 	ARCHITECT-ENGINEER COORDINATION

1.6	PLANNING FOR MECHANICAL AND ELECTRICAL SYSTEMS

1.7	ELEVATOR PLANNING

1.8	CONSTRUCTION MATERIALS

1.9	EXISTING CONDITIONS

1.10	FLOOR-TO-FLOOR HEIGHTS

1.11	CHANGES DURING DESIGN

1.12	COORDINATION OF DOCUMENTS

1.13	REVIEWS

1.14	SEISMIC DESIGN

1.15	VA HOSPITAL BUILDING SYSTEM

1.16	COLOR RENDERINGS

1.17	DRAWINGS

CHAPTER 2: SITEWORK, FOUNDATIONS

BASEMENT, SLABS

2.1	BUILDING PERIMETER FOUNDATION DRAINAGE

2.1	MEMBRANE WATERPROOFING AT INTERIOR FLOOR DRAINS

2.3	PIPE BASEMENTS

2.4	FLOOR SLAB DEPRESSIONS

CHAPTER 3: BUILDING ENVELOPE

3.1	ENERGY CONSERVATION

3.2	EXTERIOR ENTRANCES AND PLATFORMS

3.3	EXIT AND EGRESS DOOR LOCKS

3.4	AUTOMATIC DOORS

3.5	EXTERIOR WINDOWS

3.6	SCREENS

3.7	LOUVERS

3.8	PARAPET WALLS, ROOF STRUCTURES, AND ROOF WALKWAYS

3.9	LOW SLOPE ROOF SYSTEMS

3.10	EXTERIOR INSULATION FINISH SYSTEM

3.11	STRUCTURAL STEEL ANGLE GUARDS

CHAPTER 4: BUILDING INTERIOR

4.1	DOORS

4.2	SHADES, BLINDS, DRAPERIES, AND     CURTAINS

4.3	PARTITIONS

4.4	FINISHES

4.5	HANDRAILS, WALL GUARDS, AND CORNER GUARDS

4.6	CEILINGS

4.7	PLUMBING FIXTURES, TOILETS, AND BATHS

4.8	SHOWERS

4.9	ROOM NUMBERING

4.10	SIGNS, PLAQUES, AND EMBLEMS

CHAPTER 5: SPECIAL APPLICATIONS

5.1	ANIMAL RESEARCH FACILITY (ARF)/ VETERINARY MEDICAL UNIT (VMU)

5.2	AUDIOLOGY SOUND SUITES

5.3	COMPUTER ROOMS (CENTRAL)

5.4	DENTAL

5.5	ELECTROMAGNETIC SHIELDING

5.6	INTENSIVE CARE UNITS (ICUs)

5.7	ISOLATION ROOMS

5.8	MAGNETIC RESOURCE/RESONANCE IMAGING

5.9	PHARMACY

5.10	PSYCHIATRIC (MENTAL HEALTH AND BEHAVIORAL) AREAS

5.11	RADIATION THERAPY

5.12	RADIOLOGY (DIAGNOSTIC X-RAY)

5.13	SURGERY

5.14	TB (TUBERCULOSIS) SPACES

5.15	WALK-IN REFRIGERATORS AND FREEZERS

5.16	MORTUARY REFRIGERATORS

GLOSSARY OF ACRONYMS

INDEX

Blue indicates links. Chapters or various sections in chapters will open upon clicking of these links.

Blank page left intentionally

CHAPTER 1:  GENERAL REQUIREMENTS

1.1 	PURPOSE

1.2	VA ARCHITECTURAL STANDARDS AND CRITERIA

1.3	OTHER CODES AND STANDARDS

1.4	UNIFORM FEDERAL ACCESSIBILITY STANDARDS AND VA ACCESSIBILITY REQUIREMENTS

1.4.1	CONFIGURATION OF TOILET GRAB BARS

1.4.2	GENERAL VA ACCESSIBILITY REQUIREMENTS EXCEEDING UFAS REQUIREMENTS

1.4.3	SPECIFIC VA ACCESSIBILITY REQUIREMENTS

1.5	ARCHITECT ENGINEER COORDINATION

1.6	PLANNING FOR MECHANICAL AND ELECTRICAL SYSTEMS

1.6.1	ENERGY CENTER

1.6.2	HVAC EQUIPMENT SPACES

1.6.3	ELECTRICAL ROOMS AND VAULTS

1.6.4	FIRE ALARM EQUIPMENT ROOMS

1.6.5	TELEPHONE EQUIPMENT AND TELEPHONE CONSOLE ROOMS

1.6.6	ELECTRICAL AND TELECOMMUNICATION CLOSETS

1.7	ELEVATOR PLANNING

1.8	CONSTRUCTION MATERIALS

1.9	EXISTING CONDITIONS

1.10	FLOOR-TO-FLOOR HEIGHTS

1.10.1	NEW CONSTRUCTION ADJOINING EXISTING BUILDING

1.10.2	ANALYSIS OF RESTRICTED FLOOR-TO-FLOOR HEIGHTS

1.11	CHANGES DURING DESIGN

1.12	COORDINATION OF DOCUMENTS

1.12.1	GENERAL

1.12.2	CONSTRUCTION TERMINOLOGY

1.12.3	NAMES OF SPACES

1.13	REVIEWS

1.13.1	SCHEDULED PROGRESS REVIEWS

1.13.2	EXTERIOR DESIGN REVIEW

1.14	SEISMIC DESIGN

1.15	VA HOSPITAL BUILDING SYSTEM (VAHBS)

1.16	COLOR RENDERINGS

1.17	DRAWINGS

1.17.1	GENERAL

1.17.2	CADD

1.17.3	INDEX

1.17.4	EQUIPMENT, CASEWORK, AND PLUMBING FIXTURES

1.17.5	FIRE-RATED AND SMOKE-BARRIER PARTITIONS

1.17.6	FLOOR DRAINS

1.17.7	CEILING PLANS

Blank page left intentionally

1 GENERAL REQUIREMENTS

1.1 PURPOSE

The purpose of this publication is to serve as the master reference manual for architects, which includes the architectural requirements and criteria that they are expected to follow in the design and renovation of medical facilities for the Department of Veterans Affairs (VA).

1.2 VA ARCHITECTURAL STANDARDS AND CRITERIA

This manual and the current editions of the following documents, also found in VA’s Technical Information Library, comprise VA’s architectural standards and criteria:

A. Design Guides (for key functional areas) -- functional and space criteria integrated with architectural, equipment, and environmental requirements into "guide plates", detailed, illustrative plans for each space.

B. Design and Construction Procedures (PG-18-3) - a collection of VA requirements and guidance on various construction-related topics. Many of them were formerly VA "Construction Standards".

C. Equipment Guide List (PG-7610) -- list of equipment, furnishings, and utility requirements for each space in a functional area.

D. Equipment Reference Manual (PG-18-6) -- graphic representations of each piece of equipment to be purchased and installed by the construction contractor.

E. Room Finishes, Door and Hardware Schedule (PG-18-14) -- room-by-room standards for interior finishes, doors, and door hardware.

F. Space Planning Criteria (Handbook 7610) -- approved space criteria for each room in a functional area, plus "design considerations" for that area, space relationship diagrams, and interfunctional relationship matrices.

G. Standard Details (PG-18-4) -- scale drawings of many specific items and conditions – to be used as a guide only, except for

1. Standard details specifically stipulated by PG-18-3, VA Design and Construction Procedures; and

2. Standard Detail 08100-1 and 08100-2, VA Door Schedule, which must be used unless VA’s project manager specifically approves use of another system.

H. Master Construction Specifications (PG-18-1)

I. Infection-Control Standards – although no architectural standards explicitly address infection control, it is a basic hospital function and a consideration underlying most of VA’s standards and criteria:

1. Basic separation of clean and soiled material and activities is guided by the Space Planning Criteria, particularly by their Design Considerations and Relationship Matrixes and Diagrams.

2. Frequent hand washing is promoted by adequate and appropriately located lavatories and sinks, as per Space Planning Criteria and the Equipment Guide List.

3. Isolation of contagious or especially vulnerable patients is provided by isolation rooms or spaces in accordance with Space Planning Criteria and Tuberculosis Facility Guidance (in the Technical Information Library).

4. Control of airborne infection in general, as well as in isolation rooms, requires proper design of ventilation systems, as specified in HVAC Design Manual.

5. General cleanliness (as well as sterility in critical spaces) is facilitated by:

a. Finishes appropriate for each space, as per Room Finishes, Door and Hardware Schedule

b. Detailing of features such as door frames, casework, and finish transitions to avoid dirt-catching and hard-to-clean crevices and surfaces, as shown in Standard Detail and Equipment Reference Manual

c. Adequate and appropriately located and equipped housekeeping spaces, as provided by Space Planning Criteria and the Equipment Guide List

1.3 OTHER CODES AND STANDARDS

In addition to its own standards, VA follows the latest editions of a number of recognized model or voluntary codes, including:

A. National Fire Codes, including the Life Safety Code of the National Fire Protection Association (NFPA 101).

(Also see VA Fire Protection Design Manual, especially Article 3, "Special Protection", for additional VA requirements, VA interpretations of the National Fire Codes, and for fire protection features not addressed by the National Fire Codes).

B. The International Building Code 2003

C. The requirements of the Occupational Safety and Health Administration Standards (OSHA) published by the Secretary of Labor.

D. See Design and Construction Procedures, Topic 1, "Codes and Standards" for a complete listing.

E. National Institute of Building Sciences (NIBS) website, the Whole Building Design Guide, www.wbdg.org, is an easily accessible source of design guidance for health care facilities, with many linked standards and references.

F. VHA National CAD Standard Application Guide and applicable National CAD Standard modules.

1.4 UNIFORM FEDERAL ACCESSIBILITY STANDARDS AND VA ACCESSIBILITY REQUIREMENTS

1.4.1 CONFIGURATION OF TOILET GRAB BARS

VA facilities must comply with the Uniform Federal Accessibility Standards (UFAS) with the exception of the UFAS toilet/grab bar configuration, from which VA has specific permission to deviate. This deviation requires VA to follow the UFAS grab-bar configuration for a minimum of 10 percent of the patient toilets on nursing units (except for Spinal Cord Injury Units). The remainder will use the double upswing grab-bars shown in Standard Detail 10800-6.dwf Spinal Cord Injury Units must follow the UFAS configuration throughout.

1.4.2 GENERAL VA ACCESSIBILITY REQUIREMENTS EXCEEDING UFAS REQUIREMENTS

1.4.2.1 100 percent of bedrooms and patient toilets in Nursing Home Care Units and Medical, Surgical, and Neurological Nursing Units must be accessible.

1.4.2.2 20 percent of the bedrooms and resident toilets in Domiciliaries must be accessible.

1.4.3 SPECIFIC VA ACCESSIBILITY REQUIREMENTS

1.4.3.1 Other than the 10 percent required to follow UFAS, double upswing grab-bars will be used at each accessible water closet in patient or resident toilet rooms.

1.4.3.2 Additional specific VA accessibility requirements that differ from UFAS are given in "Barrier Free Design Guide" (PG-18-13).

1.5 ARCHITECT-ENGINEER COORDINATION

VA has found that the best design solution for a project occurs when the complete project team formed by the A/E has input in the early schematics phase. The team - planners, architects, engineers, programmers, and consultants - is required to work together from the inception of the project and must ensure that all engineering disciplines are coordinated with the architectural and programming requirements of the project. Exercise care to provide design solutions that meet the construction standards, space requirements, equipment layouts, and vertical and horizontal clearances required by VA. Resolve all conflicts between engineering systems and architectural requirements by the final design development submission.

1.6 PLANNING FOR MECHANICAL AND ELECTRICAL SYSTEMS

VA space planning criteria does not specifically program electrical and mechanical areas, but appropriate space must be allocated for these systems from the beginning of physical planning.

1.6.1 ENERGY CENTER

For guidance on design of a hospital energy center, including boiler plant, chiller plant, and engineering control center, see Design and Construction Procedures, Topic 9, "Energy Center".

1.6.2 HVAC EQUIPMENT SPACES

For guidance on locating HVAC equipment, cooling towers, and air compressors, see HVAC Design Manual, Article 1.7, "Equipment Location and Installation".

1.6.3 ELECTRICAL ROOMS AND VAULTS

A. For guidance on planning electrical switchgear rooms, transformer vaults, and emergency generator rooms, see Design and Construction Procedures, Topic 8, "Electrical, Signal, and Telephone Closets and Computer Rooms".

B. For ceiling heights in above spaces, see Paragraph 4.6.3 below.

C. For required fire ratings for transformer vaults, see HVAC Design Manual, Paragraph 2.10.7.4.

1.6.4 FIRE ALARM EQUIPMENT ROOMS

For design guidance on fire alarm equipment rooms, see Design and Construction Procedures, Topic 8, "Electrical, Signal, and Telephone Closets and Computer Rooms".

1.6.5 TELECOMMUNICATION EQUIPMENT AND CONSOLE ROOMS

1.6.5.1 For telephone equipment room requirements, see Electrical Design Manual, Articles 8.11, 8.12, and 8.13. Also see Design and Construction Procedures, Topic 8, "Electrical, Signal, and Telephone Closets and Computer Rooms", Paragraph 5.

1.6.5.2 For telephone console room requirements, see Electrical Design Manual, Article 8.14.

1.6.5.3 For size and other design requirements of the HE ("head end") equipment rooms (of the telecommunications system), see Electrical Design Manual, Paragraph 7.12.5.

1.6.6 ELECTRICAL AND TELECOMMUNICATION CLOSETS

1.6.6.1 For electric closet requirements, see Design and Construction Procedures, Topic 8, "Electric, Signal, and Telephone Closets and Computer Rooms".

1.6.6.2 For telecommunication closet requirements, see Electrical Design Manual, Article 8.15.

1.7 ELEVATOR PLANNING

Once they are located, elevators become pivotal, but inflexible, elements of a multi-story building. See VA Transport Systems Design Manual at the earliest stages of schematics and design development for guidelines on elevator arrangement, number, sizes, and types.

1.8 CONSTRUCTION MATERIALS

The A/E may propose the use of any building material and any method of assembly. Proposals for use of relatively untried materials or of unusual methods of construction, however, shall be discussed with the Office of Facilities Management as early as possible.

1.9 EXISTING CONDITIONS

VA will provide the current "as-built" documents for the project. However, it is the A/E’s responsibility to visit the site and verify existing conditions including those above existing ceilings. Where components indicated on existing drawings are not correct, make whatever changes are necessary to show the actual existing conditions.

1.10 FLOOR-TO-FLOOR HEIGHTS

1.10.1 NEW CONSTRUCTION ADJOINING EXISTING BUILDING

Ceiling heights and space to economically install mechanical and electrical systems above the ceiling require certain minimum dimensions. In developing the preliminary design, give special attention to conditions where a new structure joins an existing structure. Immediately inform the Project Manager if you find that the existing building’s floor-to-floor heights are inadequate for:

A. Maintaining VA minimum ceiling heights (see Article 4.6.2, "CEILING HEIGHTS").

B. Installing mechanical and electrical systems above the ceiling.

1.10.2 ANALYSIS OF RESTRICTED FLOOR-T0-FLOOR-HEIGHTS

If the existing building’s floor-to-floor heights are inadequate, submit composite section drawings of the most difficult conditions along with the suggested solutions to the problem so that VA can make a decision based on the A/E’s recommendations.

1.11 CHANGES DURING DESIGN

Do not withhold proposals for changes in plan arrangement, materials of construction, or architectural design for the periodic scheduled reviews. On the contrary, discuss them with the Project Manager by telephone and correspondence, and forward drawings for review as soon as they are sufficiently developed for consideration.

1.12 COORDINATION OF DOCUMENTS

1.12.1 GENERAL

The drawings and specifications shall be complete, clear, and coordinated.  The A/E must bear in mind that the Construction Contractor only agrees to produce what is depicted on the drawings and described in the specifications.  All that can be expected is satisfactory performance within the precise scope of the contract documents. The A/E is responsible for coordinating the various documents to eliminate ambiguous requirements.

1.12.2 CONSTRUCTION TERMINOLOGY

To avoid conflicts over ambiguous terms and statements, use identical terms on drawings and specifications. For example, the "roofing system" in the specifications should not be called a "built-up roof" on the drawings.

1.12.3 NAMES OF SPACES

Names of rooms and departments also play an important role in coordination. The names on the drawings must be the same as in the design program, as they impact not only finishes and equipment, but also construction details and mechanical & electrical systems. As far as possible, all room names should be within the specific rooms named.

1.13 REVIEWS

1.13.1 SCHEDULED PROGRESS REVIEWS

Your contract includes designated specific intervals for review of the development of your work. These reviews are joint consultations to exchange information, reconcile differing views on objectives, judge the quality and completeness at each stage, assure that previously noted changes have been incorporated, and warn of unacceptable departures from criteria or standards during the development of design. They are not for the purpose of discovering errors or omissions in detail. The quality, accuracy, coordination, and completeness of the contract documents remain the A/E’s responsibility (See VA Program Guide PG-18-15, A/E Submission Instructions).

1.13.2 EXTERIOR DESIGN REVIEW

1.13.2.1 GENERAL

At the Design Development 1 (DD-1) stage of major projects, there will be a review of the exterior design by the Facility Director and by the Office of Facilities Management, including Project Director’s Offices, the Facilities Quality Service, and the Consulting Support Service.

1.13.2.2 PRESENTATION OF DESIGN

For this review, suitable illustration of the exterior is needed including relationship to adjacent buildings and surroundings. Elevations may suffice but any other drawings, sketches, or models that clearly show the design intentions as to massing, fenestration, and materials are encouraged. If future vertical expansion is planned, the building must be illustrated with and without the future floors. A written description of design concept and intent may be helpful, especially for unusual or complex solutions. Color boards and photos of adjacent facilities are also helpful for evaluating the exterior design concept.

1.13.2.3 COMPARISON OF EXTERIOR MATERIALS

If a primary exterior material is proposed which differs from the primary material of existing buildings, submit studies and sketches of the exterior with both the existing and the proposed materials, and an analysis of the costs of the two different exteriors.

1.14 SEISMIC DESIGN

VA Policy for design of nonstructural elements of buildings to resist damage caused by earthquakes is set forth in "Seismic Design Requirements" (H-18-8), found under "Seismic Information" in the Technical Information Library, and in Design and Construction Procedures, "Natural Disasters Non-Structural Resistive Design" (PG-18-3).

1.15 VA HOSPITAL BUILDING SYSTEM (VAHBS)

A. For VA policy on the use of this interstitial-space system, see Design and Construction Procedures (PG-18-3), Topic 3, "VA Hospital Building System". For a complete description, see Hospital Building System Development Study (Red Book) in the Technical Information Library.

B. For a summary of fire protection requirements for buildings using the VAHBS, see VA Fire Protection Manual, Article 2.2.

1.16 COLOR RENDERINGS

Renderings, if required by your contract, shall show the true colors of the materials to be used in the construction of the project and the surroundings, including road systems and planting groups, in sufficient detail to predict the final appearance of the project. Show all penthouses, architectural screens, roof enclosures, skylights, stacks, and breechings that will be visible from the station point by accurate perspective projection. Show roof-mounted equipment unless hidden by architectural screens. On aerial perspectives, show major masses of mechanical equipment located behind architectural screens in block form. If exact size, color and/or appearance of exposed roof-mounted equipment are not known, show as accurately as

possible or provide a drawing of similar equipment on the rendering(s). Mount the rendering(s) on 750 mm high by 1000 mm wide (30 in. by 40 in.) bristol board mat. Provide borders of 125 mm (5 in.) at the top and sides and 150 mm (6 in.) at the bottom. The Project Manager will advise you as to the appropriate labeling for renderings, which should be lettered on the mat rather than on the rendering itself.

1.17 DRAWINGS

1.17.1 GENERAL

A. For VA’s general drawing requirements, including organization, size, scales, and Computer Aided Design and Drafting (CADD) format, see Design and Construction Procedures, Topic 2, "Drawings".

B. For abbreviations related to finishes and doors, see Room Finishes, Door and Hardware Schedule, Section I, "GENERAL". For other standard abbreviations, see Section 1 of any of the VA Design Guides.

C. For fire-protection and equipment drawing symbols, see Architectural Standard Detail 00000-1.dwf for Architectural Symbols.

1.17.2 Computer aided design and drafting (CADD)

VA has adapted the National CAD Standard with additional requirements for VA Application Guide.

1.17.3 INDEX

Provide a temporary index to drawings for all review submissions except the final, which is to be permanent. The index, on standard size drawings, will be part of the contract documents.

1.17.4 EQUIPMENT, CASEWORK, AND PLUMBING FIXTURES

On the 1:100 (1/8 in.) scale architectural floor plans, show all fixed items of equipment, shelving, casework, etc., which occupy floor space (and any items which require utilities). Note the proper symbols, contained in the VA Equipment Reference Manual (PG-18-6) and Equipment Guide List (PG 7610), on or immediately adjacent to each unit of shelving, casework, etc. However, when 1:50 (1/4 in.) scale equipment floor plans are drawn for certain rooms or area, show the proper symbols on these plans and not on the 1:100 (1/8 in.) scale plans. Show numerical designations ("P" numbers) for plumbing fixtures on plumbing drawings only, not on architectural drawings.

1.17.5 FIRE-RATED AND SMOKE-BARRIER PARTITIONS

Use fire protection symbols for fire-rated and smoke-barrier partitions, as indicated in Architectural Standard Detail 00000-1, "Architectural Symbols", on the 1:100 (1/8 in.) architectural floor plans where the partition types are designated, and on the fire protection plans (FA drawings).

1.17.6 FLOOR DRAINS

Show all floor drains on the 1:100 (1/8 in.) architectural plans. Because of possible problems from sewer gases, the number of floor drains is to be minimized. Nevertheless, provide floor drains in all locations where indicated in the Equipment Guide List 7610. Also provide floor drains at walk-in refrigerators and controlled temperature rooms for condensation return.  Indicate the pitch of floor to drains on the 1:100 (1/8 in.) scale drawings only.

1.17.7 CEILING PLANS

1.17.7.1 Provide a reflected ceiling plan at 1:100 (1/8 in.) scale to show acoustical tile grids, lights, diffusers, return air grilles, ceiling tracks, ceiling-mounted brackets or hangers, etc.

1.17.7.2 Provide reflected ceiling plans of all operating rooms at 1:50 (1/4 in.) scale showing ceiling-mounted oxygen and vacuum outlets, installation of ceiling-mounted tracks, etc. Also, show room numbers and ceiling heights on these drawings.

1.17.7.3 Provide reflected ceiling support plans at 1:50 (1/4 in.) scale for X-ray tube stands in Radiographic - Fluoroscopic Rooms, Special Procedures Rooms, etc.

CHAPTER 2: SITEWORK, FOUNDATIONS, BASEMENTS, SLABS

2.1	BUILDING PERIMETER FOUNDATION DRAINAGE

2.1.1	ANALYSIS OF NEED

2.1.2	LOCATION

2.1.3	PITCH

2.1.4	ROUTE TO OUTFALL

2.1.5	ELEVATION

2.2	MEMBRANE WATERPROOFING AT INTERIOR FLOOR DRAINS

2.2.1	GENERAL

2.2.2	EXCEPTIONS

2.2.3	KITCHEN MEMBRANE INSULATION

2.3	PIPE BASEMENTS

2.3.1	ANALYSIS OF NEED

2.3.2	DESIGN AND CONSTRUCTION

2.3.3	HEATING AND VENTILATION

2.4	FLOOR SLAB DEPRESSIONS

2.4.1	PURPOSE

2.4.2	DEPTHS

2.4.3	FLOOR DEPRESSIONS IN VA HOSPITAL BUILDING SYSTEM

Blank page left intentionally

2 SITEWORK, FOUNDATIONS, BASEMENTS, SLABS

2.1 BUILDING PERIMETER FOUNDATION DRAINAGE

2.1.1 ANALYSIS OF NEED

Subsoil (foundation) drainage provides a means of removing water that may percolate to the footing level of a building foundation system. Establish the need for a subsoil drainage system by an analysis of the climate, topography, soil character, water table, geological factors and the judgment of the designer. Where topographical or other factors exist which would lead to uncertainty regarding the ability of natural drainage to function and avoid damage by subsurface water, provide a subsoil drainage system and show on the architectural basement floor plans. Sections must show relative elevations compared to lowest floor level.

2.1.2 LOCATION

Provide subsoil drains, when judged advantageous and where individually required, at building perimeter wall footings adjacent to basement, crawl spaces, or pipe basements below grade.

2.1.3 PITCH

Subsoil drains shall maintain a pitch as uniform as possible and shall drain to suitable outfall. Minimum pitch shall be 1/2 of 1 percent.

2.1.4 ROUTE TO OUTFALL

Unless site conditions otherwise dictate, no subsoil drainage piping shall traverse a building area to reach an outfall. Where a condition makes this imperative, use solid pipe with sealed joints to traverse a building area.

2.1.5 ELEVATION

Subsoil drains shall in no case be lower in elevation than the base of adjacent footings. When an abrupt change in elevation of footings occurs, drain tile shall lead away from building at the higher elevation of the transition. The lower level shall be separately drained.

2.2 MEMBRANE WATERPROOFING AT INTERIOR FLOOR DRAINS

2.2.1 GENERAL

Provide membrane waterproofing under floor finishes surrounding floor drains in areas subject to wet conditions to prevent water and moisture from penetrating the underlying floor slabs and damaging the finishes and contents of the rooms or spaces below. Attach the membrane waterproofing to the floor drain by a clamp, and extend outward from the floor drain under the entire area of the surrounding floor surface which slopes toward the floor drain or which is subject to surface water, and carry up abutting vertical surfaces at least 75 mm (3 inches).

2.2.2 EXCEPTIONS

Do not provide membrane waterproofing if:

A. The floor slab is placed on grade; or

B. The floor finish itself is latex mastic with waterproofing membrane.

2.2.3 KITCHEN MEMBRANE INSULATION

2.2.3.1 GENERAL

The waterproof membrane in a kitchen floor can be damaged by the intense heat of a rack oven since these ovens rest directly on the floor. To protect the membrane, provide an insulating concrete floor under rack ovens, or specify the prefabricated insulated floor panel supplied by the oven manufacturer.  The floor, in each case, should be flush with the adjoining kitchen floor.

2.2.3.2 DRAWINGS

The design drawings must show details of the waterproof membrane, insulating concrete or panels, the thermal break between the rack-oven floor slab and the surrounding floor slab, and the structural support and anchors for the rack ovens.

2.3 PIPE BASEMENTS

2.3.1 ANALYSIS OF NEED

Evaluate the use of full or partial pipe basements on an individual project basis through a design analysis that indicates that a pipe basement is the most efficient and economical method of adapting piping, duct, and electrical conduit systems to the building.

2.3.2 DESIGN AND CONSTRUCTION

2.3.2.1 CLEARANCES

Design pipe basements to provide a minimum clearance of 1200 mm (4 ft.) under pipes, ducts, and electrical conduits for access to these systems for maintenance and repair.

2.3.2.2 ACCESS AND EGRESS

2.3.2.2.1 Provide access to the pipe basement at stairwells by means of industrial stairs.

2.3.2.2.2 All areas of a pipe basement must have two means of egress.  Provide emergency egress to the exterior through the use of areaways where necessary.

2.3.2.3 INSULATION

Insulate the exterior walls to prevent freezing temperatures in the pipe basement for locations where outside winter design temperatures are -7 degrees C (20 degrees F) or below as given in the 99% column of Table 1, ASHRAE Handbook- Fundamentals. See Article 5.4, Heating, Ventilation, and Air Conditioning (HVAC) Design Manual for design climatic conditions.

2.3.3 HEATING AND VENTILATION

2.3.3.1 Provide thermostatically controlled mechanical ventilation to prevent excessive rise in basement temperature and/or prevent moisture problems.

2.3.3.2 Provide intake louvers with dampers of sufficient size to satisfy fan requirements.

2.3.3.3 Screen ventilators and louvered openings to prevent entry of insects and small animals.

2.3.3.4 Provide heating in the pipe basement or insulate the slab or both as dictated by design computations for maintaining slab at 21 degrees C (70 degrees F).

2.4 FLOOR SLAB DEPRESSIONS

2.4.1 PURPOSE

Floor slab depressions are required in specific areas or rooms in order to:

A. Provide sloped floors to direct water into drains.

B. Insure that the floors of prefabricated rooms and access floors are level with the corridor floor.

C. Provide clearance for equipment.

D. Provide space for the installation of shielding in certain areas.

E. Provide for special floor finishes that require a setting bed.

2.4.2 DEPTHS

2.4.2.1 For initial planning, use the following minimum required depressions:

A. Ceramic Floor Tile with Slope to Drain -- 75 mm (3 in.)

B. Quarry Tile Floor without Drain --------- 50 mm (2 in.)

C. Quarry Tile Floor with Slope to Drain --- 100 mm (4 in.)

Note: Use 75mm (3 in.) plus thickness of floor finish for VA Hospital Building System (VAHBS) construction.

D. Terrazzo Floor -- 50 mm (2 in.)

E. X-Ray Rooms and Computerized Tomography (CT) Suites in Radiology -- 100 mm (4 in.)

Note: Use 75 mm (3 in.) plus thickness of floor finish for VA Hospital Building System (VAHBS) construction.

F. All Walk-in Freezers and Refrigerators -- 100 to 200 mm (4 to 8 in.)

G. Electromagnetic Interference (EMI) Shielded Rooms -- 38 mm (1 1/2 in.)

H. Central Computer Rooms 112 sq. m (1200 sq. ft) or smaller -- 300 mm (12 in.)

I. Central Computer Rooms larger than 112 sq. m (1200 sq. ft) -- 450 mm (18 in.)

Note: See Design and Construction Procedure, Topic 10, “Computer Systems” for additional information.

J. Animal Cage Washer -- 300 to 350 mm (12 to 14 in.)

K. Cart Washer -- 300 to 350 mm (12 to 14 in.)

L. Audiology - Sound Suite/Booth (prefab. audiometric unit)--175 mm (7 in.)

2.4.2.2 The above list may not include all the areas where floor slab depressions are required for a specific project.

2.4.2.3 As project planning proceeds, ensure that the listed depressions are adjusted to suit the actual equipment provided and to satisfy the actual conditions required by the specific design.

2.4.3 FLOOR DEPRESSIONS IN VA HOSPITAL BUILDING SYSTEM (VAHBS)

Where hospitals are designed in accordance with the VAHBS, a 75 mm (3 in.) topping is installed over the entire structural slab. Exceptions occur in areas requiring depressions greater than 75 mm (3 in.). In these areas, modify the framing and depress the floor slab in accordance with the requirements of the proposed equipment.

CHAPTER 3: BUILDING ENVELOPE

3.1	ENERGY CONSERVATION

3.1.1	GOVERNING REGULATIONS

3.1.2	ARCHITECTURAL REQUIREMENTS

3.2	EXTERIOR ENTRANCES AND PLATFORMS

3.2.1	AMBULANCE ENTRANCES

3.2.2	OTHER PATIENT ENTRANCES

3.2.3	MORGUE ENTRANCES/EXITS

3.2.4	LOADING DOCKS

3.2.5	OVERHEAD CLEARANCE FOR TRUCKS AND BUSES

3.2.6	MAINTENANCE-SHOP ENTRANCE PLATFORMS

3.2.7	ENTRANCE AND EXIT ACCESSIBILITY

3.3	EXIT AND EGRESS DOOR LOCKS

3.3.1	BUILDING ACCESS AND EGRESS DOORS (EXTERIOR)

3.3.2	STAIRWAY DOORS

3.4	AUTOMATIC DOORS

3.4.1	GENERAL

3.4.2	TYPES AND LOCATIONS

3.5	EXTERIOR WINDOWS

3.5.1	IN HISTORIC BUILDINGS

3.5.2	ENERGY CONSERVATION

3.5.3	INTEGRAL VENETIAN BLINDS

3.5.4	SILL HEIGHTS

3.5.5	OPERABLE WINDOWS

    - SAFETY GLAZING

3.6	SCREENS

3.6.1	WINDOW SCREENS

    - VENTILATION SYSTEM SCREENS

3.7	LOUVERS

3.8	PARAPET WALLS, ROOF STRUCTURES, AND WALKWAYS

3.8.1	PARAPET WALLS

3.8.2	ROOF STRUCTURES

3.8.3	ROOF WALKWAYS

3.8.4	ATTIC WALKWAYS

3.8.5	ROOFTOP GUARDRAILS

3.9	LOW-SLOPE ROOF SYSTEMS

3.9.1	GENERAL

3.9.2	POLICY

3.9.3	DESIGN LAYOUT OF LOW-SLOPE ROOFS

3.9.4	ROOFING SELECTION

3.9.5	ANCHORAGE OF INSULATION

3.9.6	BALLAST

3.9.7	BASE FLASHING AND PENETRATION

3.9.8	SCUPPERS

3.9.9	PROVISION FOR FUTURE VERTICAL EXPANSION

3.10	EXTERIOR INSULATION FINISH SYSTEM

3.11	STRUCTURAL STEEL ANGLE GUARDS

Blank page left intentionally

3 BUILDING ENVELOPE

3.1 ENERGY CONSERVATION

3.1.1 GOVERNING REGULATIONS

All new VA facilities must comply with Executive Order 13123, "Greening the Government through Efficient Energy Management", and meet the requirements of Department of Energy (DOE) regulations, 10 CFR Part 435, "Energy Conservation Voluntary Performance Standards for Commercial and Multi-Family High Rise Residential Buildings; Mandatory for New Federal Buildings".

3.1.2 ARCHITECTURAL REQUIREMENTS

The exterior closure of a building, its "thermal envelope" plays a major role in a structure’s energy performance. It must be designed to minimize heat gain and loss from conduction, solar radiation, and air leakage. See HVAC Design Manual, Paragraph 1.9.2, for recommended "U" values for walls, glazing, roofs, and floors.

3.2 EXTERIOR ENTRANCES AND PLATFORMS

3.2.1 AMBULANCE ENTRANCES

3.2.1.1 PLATFORMS

Provide ambulance entrances for back-in unloading with a platform 150 mm (6 inches) above the access drive. The platform shall have a minimum length of 3.9 m (13 ft.) and a minimum depth of 3 m (10 ft.). Platforms are not required for drive-through unloading, but require a ramp at the entrance door. Use drive-through ambulance entrance only as a second consideration and where the outside winter design temperatures are above 0 degrees C (32 degrees F), as given in the 99 percent column of Table 1, ASHRAE Handbook - Fundamentals.

3.2.1.2 CANOPIES

Provide a noncombustible canopy at back-in and drive-through unloading areas.  Clearance from grade to the underside of any canopy obstruction shall be 3 m (10 ft.) minimum. Since some ambulances may require even more clearance, the A/E must coordinate with the medical center and local sources of emergency transportation before firmly establishing the canopy height.

3.2.1.3 OTHER PROVISIONS

3.2.1.3.1 Make additional provisions, if deemed necessary, to provide protection from weather for patients arriving by ambulance.

3.2.1.3.2 Ambulance entrances shall include provisions for wheelchair and litter access for emergency patients arriving in vehicles other than an ambulance. For Doors, see Paragraph 3.4.2.4 below.

3.2.1.4 ENCLOSED AMBULANCE ENTRANCES

Enclose ambulance entrances where the outside winter design temperature is below -12 degrees C (10 degrees F), as given in the 99 percent column of Table 1, ASHRAE Handbook of Fundamentals. Equip the enclosed entrances with automatic overhead type doors operable from both outside and inside of the enclosure.

3.2.2 OTHER PATIENT ENTRANCES

3.2.2.1 CANOPIES

Provide non-combustible canopies over entrances to outpatient clinics, ambulatory care facilities, main hospitals, spinal cord injury facilities, emergency entrances and nursing home care units. The canopies shall extend 600 mm (2 feet) beyond the curb lines to protect patients from inclement weather. To reduce the size and cost of canopies, locate the curb line near the entrance, if compatible with other design considerations.

3.2.2.2 REVOLVING DOORS

Provide revolving door(s) at all main entrances to Health Care Facilities except spinal cord injury, nursing home care units, and emergency entrances, to exclude inclement elements from the building. For persons with disabilities, provide a secondary set of 1200 mm (4 ft.) wide, automatically operated swinging door(s) with an air lock vestibule of 6.3 m (21 ft.) between doors.

3.2.2.3 "AIR LOCKS"

At spinal cord injury unit (SCIU), nursing home care unit (NHCU), and emergency entrances, provide air locks consisting of vestibules formed by automatically operated sliding doors placed not less than 6.3 m (21 ft.) apart. These must be the break-away type that can be manually operated during a power failure. If swinging doors must be used, both the inner and outer doors shall swing outward.

3.2.3 MORGUE ENTRANCES/EXITS

3.2.3.1 Provide morgue entrances for back-in unloading with a platform 150 mm (6 in.) above the access drive.

3.2.3.2 Provide a noncombustible canopy with a clearance from grade of 3 m (10 ft.) minimum.

3.2.3.3 Screen morgue entrances from public view.

3.2.4 LOADING DOCKS

3.2.4.1 PLATFORMS

All warehouse, dietetic, laundry, and animal research facility loading dock platforms shall be 1200 mm (4 ft.) above the driveway. Platforms shall have a minimum depth of 2400 mm (8 ft.) front to back or between the back of the dock lift/leveler and the back wall.

3.2.4.2 CANOPIES

Provide a noncombustible canopy over the platform with 4.2 m (14 ft.) clearance from grade to the underside of the canopy.

3.2.4.3 PEDESTRIAN ACCESS

Provide a stair or a ramp to the platform; for platforms which are more than 15 m (50 ft.) long, provide a stair or a ramp at each end.

3.2.5. OVERHEAD CLEARANCE FOR TRUCKS AND BUSES

Maintain soffits under portions of buildings, canopies, or overhanging wings

which extend over truck and public bus traffic areas at a height which will provide 4.2 m (14 ft.) minimum head room. Maintain a grade either side of the passageway to provide the required head room for the longest wheel base trailer permitted by the state.

3.2.6 MAINTENANCE-SHOP ENTRANCE PLATFORMS

Entrance platforms to maintenance shop floors shall be 150 mm (6 in.) high above grade, at same level as shop floors, and shall be a minimum of 3 m (10 ft.) wide. Slope platform away from the building. Provide double doors at platforms to permit direct transfer of long lengths of pipe, lumber, etc. to maintenance shop storage areas.

3.2.7 ENTRANCE AND EXIT ACCESSIBILITY

3.2.7.1 All platforms, ramps and stairs adjacent to entrances shall have non-slip surfaces.

3.2.7.2 All entrances listed in paragraph 3.2.2 and all exits at grade shall be accessible to and usable by persons with disabilities, that is, level or provided with ramps, and free of steps or other obstructions. Fire stair exits, loading docks, boiler and chiller buildings, etc., are exempt.

3.3 EXIT AND EGRESS DOOR LOCKS

3.3.1 BUILDING ACCESS AND EGRESS DOORS (EXTERIOR)

3.3.1.1 ELECTROMAGNETIC LOCKING SYSTEM

3.3.1.1.1 GENERAL

When requested by the medical center, equip all building access and egress doors (pedestrian) with centrally controlled, listed locking devices, i.e. an electromagnetic locking system, meeting the requirements of Special Locking Arrangements contained in Chapter 5 of NFPA 101, "Life Safety Code". On the exterior side, provide locks that are controlled by key.

3.3.1.1.2 MONITORS AND ALARMS

Locate a central door control and monitoring console in the security service operations room. Install a second monitoring-only panel in the Engineering Control Center if requested by the medical center. An audible and visual alarm will be activated at the control panels when an individual attempts to exit through a door equipped with an electromagnetic locking system.

3.3.1.1.3 DESIGN BY SECURITY CONSULTANT

The A/E shall obtain the services of a security consultant to design the exit door locking system. The consultant shall coordinate the design with the station security officials, especially where an existing system is in place, to attempt to achieve compatibility.

3.3.1.2 MANUALLY OPERATED LOCKS

If a centrally controlled electromagnetic locking system is not used, provide exterior door locks that are controlled by key on the outside but allow egress from inside by turning a lever handle or depressing a panic bar.

3.3.2 STAIRWAY DOORS

3.3.2.1 EXTERIOR EXIT DOORS AT STAIRWAYS

Design doors and hardware for stairway exit doors leading directly to the exterior in accordance with paragraphs above, except that only panic hardware may be used.

3.3.2.2 INTERIOR STAIRWAY DOORS

Provide interior stairway doors with passage latch sets having inside and outside door handles free at all times. Exceptions are where stairway doors are required to be locked to prevent entrance into or elopement from areas such as ICUs, surgery, hemodialysis, radiology, and psychiatric nursing units. When these doors are locked from stairside, outside handles shall allow free egress into stairwells at all times, except from psychiatric areas. (See Paragraph 5.10.2.2 below for additional information.)

3.3.3 ALARMS, BELLS, AND COMMUNICATORS ON DOORS

Alarms, bells, and communicators are required on exit doors leading to the exterior unless the medical center objects to their use at specific locations.

3.4 AUTOMATIC DOORS

3.4.1 GENERAL

Design automatic doors to comply with the "Fire Protection Design Manual" and "Room Finishes Door and Hardware Schedule", and to operate manually in event of power failure. Equip controls with safety devices for pedestrian protection. Provide door-operator controls and equipment that are easily accessible for maintenance. Design automatic doors to open from both sides.

3.4.2 TYPES AND LOCATIONS

3.4.2.1 Use sliding doors operated by motion detectors and an electric-eye safety device with emergency breakaway features at:

A. Main entrance, if revolving doors are not practical

B. Ambulatory Care patient entrance, if revolving doors are not practical

C. Spinal Cord Injury entrances

D. Nursing Home Care Unit entrances

E. Corridor doors to Congregate Baths and Congregate Toilet Rooms (Spinal Cord Injury, Orthopedic, Neurological, and Rehabilitation Medicine Service (RMS) Nursing Units)

3.4.2.2 Use sliding doors operated by remote push plates at doors from Spinal Cord Injury bedrooms into toilets or baths

3.4.2.3 Use swinging doors with remote push plate operation at:

A. Main entrance doors to and from Surgery Suite

B. Recovery Room doors into corridors

C. Corridor Doors to Radiation Treatment Rooms

D. Spinal Cord Injury: Patients’ Dining Rooms, Dayrooms, Recreation Therapy Rooms, Physical Therapy (PT), and Occupational Therapy (OT) Clinics

E. Entrance Doors to Life Support Rooms, Minor Operating Rooms, and Observation and Treatment Rooms (Ambulatory Care Service)

F. Entrance Doors to Medical and Surgical Intensive Care Units (ICUs), Coronary Care ICU, and General Purpose ICU

G. NHCU & SCIU entrance doors to courtyards, patios, etc.

3.4.2.4 Use swinging doors with mat operation (requires floor slab depression) at:

A. Ambulance entrance

B. Where conditions dictate, at locations listed in paragraph 3.3.2.1 in lieu of sliding doors.

3.3.2.5 Use swinging doors with pull-chain operation at doors between loading platform and corridors.

3.5 EXTERIOR WINDOWS

3.5.1 IN HISTORIC BUILDINGS

While designing to meet project goals, use standards and guidelines in the Secretary of the Interior’s "Standards for Treatment of Historic Properties" as a guide for projects affecting windows of historic buildings.

3.5.2 ENERGY CONSERVATION

3.5.2.1 Design windows in accordance with energy requirements in HVAC Design Manual, Paragraph 1.9.2 "BUILDING THERMAL ENVELOPE".

3.5.2.2 Energy-conservation requirements will result in double-glazed windows for most locations. For double-glazed windows, provide a continuous thermal break between inner and outer sash; also between inner and outer frame components including window sill.

3.5.3 INTEGRAL VENETIAN BLINDS

Where double-glazed windows are used, enclose horizontal venetian blinds between the two glazed surfaces wherever the type of window will accommodate this feature.

3.5.4 SILL HEIGHT

Window sills/stools in patient bedrooms shall be a minimum of 450 mm (18 in.) above the finished floor.

3.5.5 OPERABLE WINDOWS

3.5.5.1 Operable windows are more costly than fixed windows and more subject to drafts, leaks, and maintenance problems, but may be required or justifiable for:

A. Washing and glazing from within the building

B. Ventilation in non-air-conditioned building

C. Code compliance (patient bedrooms in non-sprinklered buildings)

D. Emergency ventilation in case of loss of electrical power to HVAC system (when HVAC system is not on emergency power system)

3.5.5.2 Make design decisions on operability in close consultation with the medical center, specifically addressing all the factors above. Operable windows shall be in-swinging and side-hinged unless historic design compatibility or other specific conditions dictate otherwise. All operable windows in air-conditioned buildings shall normally be closed and locked.  For safety, operable windows in patient bedrooms shall have hold-open hardware which secures the window at a maximum opening of 150 mm (6 in.) for emergency ventilation.

3.5.5.3 When in open position for ventilation, window sash shall not project into the room beyond edge of stool or face of convector, nor beyond exterior reveals of window sills within 2000 mm (6 ft. 6 in.) of grade.

3.5.5.4 Mechanically operated windows shall be avoided. If they are necessary for high or inaccessible windows, then the mechanical operators shall be simple and durable.

3.5.6 SAFETY GLAZING

3.5.6.1 Glaze all windows in Psychiatric Nursing Units, Alcohol Dependency Treatment Nursing Units, Drug Abuse Treatment Nursing Units, Medical, Surgical and Neurological (MS&N) Security Bedrooms, Security Exam Rooms, and Security Holding Rooms with laminated glass. Laminated glass shall be 11 mm (7/l6 in.) thick in locked patient units and security rooms, 8 mm (5/l6 in.) thick elsewhere.

3.5.6.2 If laminated glass is required for double-glazed windows, provide it for interior panes only except in Mental Health and Behavioral Nursing Units for windows facing a courtyard with sill/stools less than 2000 mm (6 ft. 6 in.) above the ground. Where this occurs, laminated glass is required for both panes.

3.6 SCREENS

3.6.1 WINDOW SCREENS

3.6.1.1 INSECT SCREENS

Provide screens only on operable windows in spaces that are not air conditioned.

3.6.1.2 DETENTION SCREENS

Use detention screens only in existing buildings where limitations of architectural character or cost do not permit replacement of existing screened windows whose design will not accommodate laminated safety glass.

3.6.1.3 SECURITY SCREENS

Provide security screens on windows where required by Design and Construction Procedures, Chapter 14, "Security".

3.6.2	VENTILATION SYSTEM SCREENS

Provide bird screens on mechanical ventilation supply and exhaust openings in exterior walls. Provide insect screens on the inside of louvered openings in exterior walls where there are no duct connections.

3.7 LOUVERS

Location of ventilation louvers requires careful consideration of prevailing winds, as well as close coordination between the architect and mechanical engineer, to avoid the re-entry of exhaust air and the intake of exhaust fumes form vehicles and other engines. See HVAC Design Manual, Paragraph 1.8, "Location of Outside Air Intakes and Exhaust Air Outlets".

3.8 PARAPET WALLS, ROOF STRUCTURES, AND WALKWAYS

3.8.1 PARAPET WALLS

Masonry parapet walls are potential sources of water penetration, unequal thermal expansion, additional structural loads, and increased costs.

Therefore, do not use such walls for any building unless specifically permitted by the Project Manager. Proposed parapet walls must be justified by aesthetic, functional or economic considerations. Where permitted, design and reinforce them to assure stability and water tightness when subjected to lateral or thermal forces.

3.8.2 ROOF STRUCTURES

Make roof structures, such as penthouses and architectural screens enclosing or concealing roof-mounted mechanical equipment, compatible in appearance and with the material, texture, color, and shape of the building. Where it is necessary to expose roof-mounted mechanical equipment, minimize its appearance by location, low silhouette, and color.

3.8.3 ROOF WALKWAYS

Provide roof walkways of prefabricated asphalt planks with non-slip surfaces on access routes over roofs to mechanical equipment requiring recurrent maintenance. Where necessary for safety of maintenance workers, provide ladders, stairs and/or platforms. Show their locations and provide details on architectural drawings.

3.8.4 ATTIC WALKWAYS

In attic spaces to have batt or loose floor insulation, provide walkways for access to mechanical and electrical equipment. Show the location and details of attic walkways on architectural drawings.

3.8.5 ROOFTOP GUARDRAILS

Whenever mechanical equipment requiring periodic maintenance is installed on a roof more than 6 m (20 ft.) above the ground, provide guardrails or fences between the roof edge and any equipment or walkways less than 3 m (10 ft.) from the edge. Design the guardrails 1050 mm (42 in.) high and in accordance with OSHA requirements for standard guardrails.

3.9 LOW-SLOPE ROOF SYSTEMS

3.9.1 GENERAL

3.9.1.1 Design low-slope roof systems in accordance with the recommendations of the National Roofing Contractors Association (NRCA) Roofing and Waterproofing Manual and this manual.

3.9.1.2 Low-slope roof systems include but are not limited to the following roofing membranes with roof insulation:

A. Bituminous built-up roofing systems

B. Modified bituminous roofing systems

C. Single-ply sheet roofing system

D. Fluid-applied roofing systems

3.9.1.3 Re-roofed areas shall conform to this Article.

3.9.1.4 Where alterations or repairs are required to over 40 percent of flat roof, consider entire re-roofing.

3.9.2	POLICY

No roofs shall be dead flat; design all roofs with slope to roof drains or gutters.

3.9.3 DESIGN LAYOUT OF LOW-SLOPE ROOFS

3.9.3.1 Design low-slope roof systems with a positive slope: a minimum of 1:50 (0.25 in. per ft.) up to a maximum of 1:12 (1.0 in. per ft.) to drains:

A. Use tapered insulation, sloped structural systems, or level structural system with sloped fill to achieve the required slope.

B. Do not use NRCA defined "One-way slope" (Sloping to a level valley). See NRCA – "Tapered Roof Insulation Systems."

C. Use NRCA defined "Two-Way slope" (actually sloping in four directions).

3.9.3.2 Use a uniform square grid to lay out roof slopes to drains. Roofs shall not slope to level valleys, but may have one-way slopes to gutters at gravel-stop edges.

3.9.3.3 Locate drains at points of maximum deck deflection; generally at mid span of the deck between supports where possible.

3.9.4 ROOFING SELECTION

It is very important to select the right roofing system. Some of the factors that may influence the roofing choice are:

A. The shape of the building and roof

B. The location of the drains, whether exterior or interior

C. Aesthetic considerations

D. Roof and insulation attachment methods that are dictated by the deck type

E. The insulating values desired for energy conservation and HVAC sizing

F. The type of building use and operations. For example, the water vapor generated from a swimming pool, or emissions from a boiler plant, may dictate the choice of roofing

G. Thermal insulation versus storm water management

3.9.5 ANCHORAGE OF INSULATION

Anchor insulation to deck. Loose laid insulation is not permitted except for protective membrane roof insulation system.

3.9.6 BALLAST

Show ballast types and weight(s) on roof plans and describe in detail in project specifications. See VA Master Construction Specifications, Section 07570, "Pavers and Aggregate Roof Ballast" for guidance.

3.9.7 BASE FLASHING AND PENETRATIONS

Use 200 mm (8 in.) high base flashing at walls and penetrations. Do not use pitch pockets or similar penetration seals.

3.9.8 SCUPPERS

Locate overflow scuppers in parapet walls at top of membrane so that ponding does not exceed high point of slopes.

3.9.9 PROVISION FOR FUTURE VERTICAL EXPANSION

Where the roof deck is to become a future floor slab, design the roof system as follows:

3.9.9.1 Depress roof slab as required by Design and Construction Procedures, Topic 12, "Future Vertical Expansion".

3.9.9.2 Provide a separation between the roof system and the roof deck (future floor slab).

3.9.9.3 Design for easy removal of the roofing system down to the roof deck.

3.9.9.4 Detail connections for future columns and exterior walls to prevent water infiltration into the roof system.

3.10 EXTERIOR INSULATION FINISH SYSTEM

If an exterior insulation finish system (EIFS) is used for the exterior finish, use only "Drainable" type. Sheathing shall be concrete backer board.

3.11 STRUCTURAL STEEL ANGLE GUARDS

Provide structural steel angle guards, protected from corrosion by painting or galvanizing, for exterior use in the paths of motor vehicle traffic to the loading dock and at exposed corners on the platform.

Blank page left intentionally

CHAPTER 4: BUILDING INTERIOR

4.1	DOORS

4.1.1	GENERAL

4.1.2	CORRIDOR-TO-CORRIDOR DOORS

4.1.3	FIRE-PARTITION AND SMOKE-BARRIER DOORS

4.2	SHADES, BLINDS, DRAPERIES, AND CURTAINS

4.2.1	LIGHTPROOF SHADES

4.2.2	OPAQUE SHADES

4.2.3	OTHER SHADES AND WINDOW TREATMENTS

4.2.4	WINDOW HEADS

4.3	PARTITIONS

4.3.1	METAL STUD PARTITIONS

4.3.2	STRUCTURAL DESIGN

4.3.3	GYPSUM WALLBOARD

4.3.4	SECURITY PARTITIONS

4.4	FINISHES

4.4.1	VA GUIDE TO ROOM FINISHES

4.4.2	FINISH SCHEDULE

4.5	HANDRAILS, WALL GUARDS, AND CORNER GUARDS

4.5.1	HANDRAILS AND WALLGUARDS

4.5.2	CORNER GUARDS

4.6	CEILINGS

4.6.1	CUBICLE CURTAIN TRACKS

4.6.2	CEILING HEIGHTS

4.6.3	EFFECTS OF VA HOSPITAL BUILDING SYSTEM

4.7	PLUMBING FIXTURES, TOILETS, AND BATHS

4.7.1	TOILET ROOM PARTITIONS

4.7.2	VISUAL SCREENING

4.7.3	WALL PROTECTION AT PLUMBING FIXTURES

4.7.4	WATER COOLERS

4.8	SHOWERS

4.8.1	ENCLOSURES

4.8.2	FLOORS

4.8.3	ACCESSIBILITY

4.9	ROOM NUMBERING

4.9.1	GENERAL

4.9.2	FLOOR DESIGNATIONS

4.9.3	FLOOR AREA DESIGNATIONS

4.9.4	ROOMS

4.9.5	CORRIDORS, STAIRS, AND ELEVATORS

4.9.6	ADDITIONS TO EXISTING BUILDINGS

4.10	SIGNS, PLAQUES, AND EMBLEMS

4.10.1	SAFETY SIGN

4.10.2	CONSTRUCTION SIGN

4.10.3	DEDICATION PLAQUE

4.10.4	VA EMBLEM

Blank page left intentionally

4 BUILDING INTERIOR

4.1 DOORS

4.1.1	GENERAL

4.1.1.1 Follow VA Program Guide PG-18-14, Room Finishes, Door and Hardware Schedule, for sizes, types and symbols of doors. Provide solid core wood or hollow metal interior doors. Wood is preferred, except for locations where metal is required for functional reasons.

4.1.1.2 Provide metal door frames.

4.1.1.3 For automatic-door requirements, see Paragraph 3.4.

4.1.2 CORRIDOR-TO-CORRIDOR DOORS

All corridor-to-corridor doors shall have 0.06 sq. m (100 sq. in.) glass vision panels and shall swing in opposite directions from each other.

4.1.3 FIRE-PARTITION AND SMOKE-BARRIER DOORS

4.1.3.1 Doors in fire partitions and smoke barriers shall have fire rated glazing vision panels and be held open with electromagnetic holders, except doors which should remain closed for functional reasons.

4.1.3.2 Do not use wood labeled fire doors in areas where they may be subjected to heavy traffic or hard use, such as by carts, trucks, kitchen equipment, etc., nor for pairs of opposite-swinging doors. In these locations, use hollow metal labeled doors.

4.2 SHADES, BLINDS, DRAPERIES, AND CURTAINS

4.2.1 LIGHTPROOF SHADES

Provide lightproof shades to prevent outside light from infiltrating into the room on windows in electron microscopy rooms and fluorescent microscopy rooms. (See Master Specification Section 12514).

4.2.2	OPAQUE SHADES

Provide opaque (room-darkening) shades on windows of radiographic and fluoroscopic rooms, special procedures rooms, cardiac catheterization rooms, eye-clinic rooms, and rooms containing image intensifiers.

4.2.3	OTHER SHADES AND WINDOW TREATMENTS

Other shades, blinds, draperies, and curtains are not part of the construction contract, except for integral venetian blinds. (See Paragraph 3.5.3 above.)

4.2.4	WINDOW HEADS

The construction of window heads shall include a wood plate, board, or trim piece above the head designed to accommodate the attachment of window treatments that may be installed by the medical center after completion of the building construction.

4.3 PARTITIONS

4.3.1 METAL STUD PARTITIONS

For general interior partition framing, use 100 mm (4 in.) metal studs. Use

double row of 100 mm (4 in.) studs between adjacent X-ray rooms (with lead shielding between rows of studs) and 150 mm (6 in.) studs for other walls of X-ray rooms. Isolated power units require thicker walls, generally 150 to 200 mm (6 to 8 in.), depending on size of units. Therefore, use nominal 150 mm (8 in.) partitions for surgical operating rooms until completion of design development determine a more precise size. Certain recessed electric panels outside of electrical closets may require walls thicker than usual; coordinate with Project Electrical Engineer. For walls with piping and other special requirements, use other sizes or systems as appropriate.

4.3.2 STRUCTURAL DESIGN

Coordinate with Structural Engineer for design of partitions supporting wall-hung equipment and TV support brackets, and for wind-load design of exterior walls.

4.3.3 GYPSUM WALLBOARD

4.3.3.1 GENERAL

Where gypsum wallboard is called for, use 16 mm (5/8 in.) thick Type X gypsum board, except for special conditions.

4.3.3.2 LEAD-LINED PARTITIONS

Use lead-lined gypsum wallboard for shielding of X-ray rooms. See Architectural Standard Details 13091-1.dwf and 13091-2.dwf for lead protection required. Radiation Therapy rooms will require services of a registered physicist to establish the shielding protection required. (See Article 5.11, "RADIATION THERAPY", below for shielding of these rooms.)

4.3.3.3 HEIGHT OF GYPSUM BOARD

4.3.3.3.1 See VA Master Construction Specifications, Section 09260, Paragraph 3.1, for height of gypsum wallboard on metal stud partitions in most applications.

4.3.3.3.2 In addition, extend one layer of gypsum board from floor to underside of structure above on partitions enclosing isolation room or suite.

4.3.4 SECURITY PARTITIONS

Partitions housing service windows of pharmacy, agent cashier, and credit union must be of solid masonry or other special construction to provide security. See Design and Construction Procedures (PG-18-3), Topic 14, "Security".

4.4 FINISHES

4.4.1 VA GUIDE TO ROOM FINISHES

Interior finishes are prescribed in VA Program Guide PG-18-14, Room Finishes, Door and Hardware Schedule. The project management team must review any deviation from this document prior to start of construction document phase.

4.4.2	FINISH SCHEDULE

Combine the finish schedule and color design schedule and include them in the specifications, not on the drawings. Use the finish schedule format included in Room Finishes, Door, and Hardware Schedule. Demolition plans must show the existing finishes.

4.5 HANDRAILS, WALL GUARDS, AND CORNER GUARDS

4.5.1 HANDRAILS & WALL GUARDS

Provide, except in administrative areas, handrails and wall guards (crash rails) on both sides of all corridors with walls constructed of gypsum board, veneer plaster, or plaster. This includes all nursing units, clinical and patient care areas, and dietetic and service areas where walls are not ceramic tile or masonry. Provide continuous reinforcing in the wall for attachment of handrails and wall guards. (See Standard Detail 10260-1.dwf, "Wall Guards")

4.5.2 CORNER GUARDS

4.5.2.1 RESILIENT SHOCK-ABSORBING, OR STAINLESS STEEL

4.5.2.1.1 Provide resilient or stainless steel corner guards for the external corners of finished interior walls and columns in the paths of wheeled traffic in the following places:

A. Corridors of:

1. Domiciliary Buildings

2. Nursing Units

3. Operating Suites

4. Kitchen and Dietetic Areas

5. Ambulatory Care and Clinical Areas

6. Maintenance and Repair Areas

7. Warehouse and Receiving Areas

8. Laundry and Linen Areas

Note: Corner guards are not required in corridors where continuous handrails and wall guards are used around external corners.

B. Areas of:

1. Food Preparation and Distribution

2. Food Serving and Dining

3. Cart Storage

4. Pharmacy

5. Supply Processing and Distribution

6. Morgue and Autopsy Rooms

7. Service Elevator Lobbies

8. Rooms containing dumbwaiters or cart-lift elevators

9. Maintenance and Repair

10. Warehouse and Receiving

11. Laundry and Linen

4.5.2.1.2 Choice of corner-guard material is governed by wall finish:

A. Use surface-applied (full height) resilient type corner guards on gypsum board, veneer plaster, or plaster walls.

B. Use stainless steel corner guards on masonry or ceramic tile walls.

4.5.2.2 RIGID ADHESIVE-APPLIED ACRYLIC/VINYL

At external corners in patient bedrooms, use rigid, acrylic or vinyl, surface-mounted corner guards, self-adhesive or applied with double-faced tape.

4.5.2.3 STRUCTURAL STEEL

Provide structural steel angle guards, suitably painted or galvanized, for the external corners of exposed masonry interior walls and columns in the paths of motorized wheeled vehicles in corridors and areas of:

A. Warehouse and Receiving

B. Laundry and Linen Service

C. Parking Garages and Ambulance Garages

4.6. CEILINGS

4.6.1 CUBICLE CURTAIN TRACKS

Examination rooms, and patient bedrooms, except in Mental Health and Behavioral Patient Care Units, are to have cubicle curtain tracks for privacy. All cubicle curtain tracks are to be surface mounted and should be shown on the 1:100 (1/8 in.) reflected ceiling plans.

4.6.2 CEILING HEIGHTS

4.6.2.1 Minimum clear ceiling heights from finished floor to finished ceiling or underside of any obstruction above finished floor shall be 2700 mm (9 ft.) except for areas listed below:

A. Animal Research Operating Rooms and

Radiographic rooms 						2.9 m (9 ft. 6 in.)

B. Camera Rooms (Medical Media Production)	      3.0 m (10 ft.)

C. Cardiac Catheterization Rooms (X-ray)              2.9 m (9 ft. 6 in.)

Note: See Paragraph 5.12.3.3 below for exceptions.

D. Chapels constructed as separate buildings – (The wall height at the nave shall be to the intersection of the underside of the roof slab with the exterior surface of the nave wall.)				3.6 m (12 ft.)

E. Corrective Therapy Rooms (Rehabilitation Medicine) 3.0 m (10 ft.)

F. Corridors                                          2.4 m (8 ft.)

G. Domiciliary Buildings (Patient Bed Areas)          2.4 m (8 ft.)

H. Emergency Generator Rooms:

1. Generators smaller than 500 KW                     3.6 m (12 ft.)

2. Generators 500 KW and larger                       3.8 m (14 ft.)

I. Engineering Shops                                  3.0 m (10 ft.)

J. Laundries - (clear headroom below duct work, piping, conveyors and other obstructions):

1. Clean linen distribution areas                     4.8 m (16 ft.)

2. Production area                                    4.8 m (16 ft.)

3. Soiled linen area                                  4.8 m (16 ft.)

K. Libraries (health science and patients)            2.9 m (9 ft. 6 in.)

L. Vocational rehabilitation therapy                  2.9 m (9 ft. 6 in.)

M. Multipurpose Recreation Rooms, smaller than

225 sq. m (2400 sq. ft.)				  	3.0 m (10 ft.)

N. Multipurpose recreation rooms

225 sq. m (2400 sq. ft.) and larger			6.6 m (22 ft.)

NOTE: For hospital buildings, locate multipurpose recreation rooms having ceiling heights of 6.6 m (22 ft.) outside of and contiguous to the exterior wall of the main structure. For nursing home care buildings and domiciliary buildings, ceiling heights of multipurpose rooms 225 sq. m (2,400 sq. ft.) and above shall be in keeping with the design and uniformity of the structure.)

O. Nuclear Medicine Pet/Cyclotron Rooms               3.0 m (10 ft.)

P. Nursing Home Care Buildings (Patient Bed Areas)    4 m (8 ft.)

Q. Operating Rooms                                    2.9 m (9 ft. 6 in.)

Note:  Additional 200 mm (8 in.) of accessible space must be available   above the ceiling to accommodate ceiling-mounted operating microscopes:  Otherwise, ceiling height must be 3.1 m (10 ft. 2 in.).

R. Parking structures-minimum clearance               2.3 m (7 ft. 6 in.)

Note: Life Safety Code, NFPA-101, requires a means of egress to have minimum headroom of 2300 mm (7 ft. 6 in.) and any projection from the ceiling to be at least 2800 mm (6 ft. 8 in.) from the floor.

S. Patient Bedrooms without ceiling-hung television

sets 								2.4 m (8 ft.)

T. Physical Therapy Clinics (Rehabilitation Medicine) 2.9 m (9 ft. 6 in.)

U. Radiation Therapy Rooms                            2.9 m (9 ft. 6 in.)

V. Switchgear Rooms (High Voltage)                    3.3 m (11 ft.)

W. Therapeutic Pools-the height from floor to

underside of truss or ceiling				3.0 m (10 ft.)

X. Transformer Rooms                                  3.3 m (11 ft.)

Y. Warehouses                                         4.5 m (15 ft.)

Z. X-ray Rooms                                        2.9 m (9 ft. 6 in.)

Note: See Paragraph 5.12.3.3 below for exceptions.

4.6.3 EFFECTS OF VA HOSPITAL BUILDING SYSTEM

When the VA Hospital Building System concept is used as the basis of design, maintain to the extent feasible uniform walk-on deck and ceiling elevations in accordance with the principles of the system concept.

4.7 PLUMBING FIXTURES, TOILETS, AND BATHS

4.7.1 TOILET ROOM PARTITIONS

4.7.1.1 All toilet stall partitions are to be ceiling hung.

4.7.1.2 Use steel with baked-on enamel finish for toilet stall partitions and room entrance screens. Exceptions:

A. Provide stainless steel toilet stall partitions adjacent to urinals.

B. Room entrance screens that double as part of a toilet partition enclosure shall be of typical stud construction, from floor to ceiling.

4.7.1.3 Provide stainless steel wall-hung urinal screen partitions.

4.7.1.4 Do not use toilet stalls or divider partitions in single-user toilet rooms in which only a lavatory and water closet are provided.

4.7.2 VISUAL SCREENING

In planning the layouts of toilet rooms and bathrooms, uses hinged doors or provide visual screening, so as to block the view from the corridors into such rooms. (See VA Standard Detail 10162-2.dwf)

4.7.3 WALL PROTECTION AT PLUMBING FIXTURES

Provide vinyl wallcovering on walls with lavatories, sinks, or electric water coolers, unless space has ceramic tile wainscot or other impermeable finish.

4.7.4 WATER COOLERS

Provide electrical water coolers in alcoves near all waiting areas and on nursing units and where specifically required by the Equipment Guide List (PG-7610). All water coolers are to be accessible per requirements of the Uniform Federal Accessibility Standards.

4.8 SHOWERS

4.8.1 ENCLOSURES

Use ceramic tile applied with thin set Portland cement to concrete-fiber reinforced backer board for shower enclosures and partitions of contiguous areas. Use prefabricated shower stalls in boiler plants, chiller buildings, and energy centers.

4.8.2 FLOORS

Use non-slip finished floors for showers and contiguous spaces. Depress the structural floor of patient showers and contiguous spaces in new hospital buildings 75 mm (3 in.) and place a 75 mm (3 in.) removable fill on the entire floor area. In new buildings, slope finished floors of patient

bathrooms toward showers to assure drainage to the shower drain. In existing buildings where standard depression is not feasible, use other means to ensure positive drainage and water tightness. Floor slopes in and around a shower shall not exceed 5 percent.

4.8.3 ACCESSIBILITY

Construct all patient showers without curbs, and at least one shower stall in non-patient shower rooms. Provide grab bars for all showers. (See Architectural Standard Details 10800-1, 10800-2, 10800-3, 10800-4 and 10800- 5.)

4.9 ROOM NUMBERING

4.9.1 GENERAL

Work closely with the facility to establish the room numbering system to be used for the new or remodeled space, since change in room numbers late in the design and construction process is a sure cause of confusion and error. The VA Environmental Graphics Design Program Guide, dated July 1996, provides sign types for room numbering.

4.9.2	FLOOR DESIGNATIONS

Designate the main entrance lobby as the first floor level, identified by the number "1". Identify the level immediately below the first floor by the letter "B". If there is more than one level below the first floor, designate them B1, B2, B3, etc., with B1 being the level immediately below the first floor level. If there are any penthouse floors, continue the floor numbering system, such as 7, 8, and 9. Designate parking floors in a building the same way as basement, except using the letter "P" instead of "B".

4.9.3 FLOOR AREA DESIGNATIONS

4.9.3.1 Divide each floor or level into a convenient number of areas beginning with the letter "A". Determine the size of the areas by the configuration of the building, the number of rooms in the area, and the location of main corridors, which should be used as area borders. Since the size and location of departments may change, use the main corridors, and not departments, to establish area borders.

4.9.3.2 Once the area designations have been set, each area shall continue that designation through the entire height of the building. This means that the area designation on each floor must be coordinated with other floors. The configuration of the building may be such that the upper floors will contain only Areas "A" and "D", or "A", "C" and "D". Make an effort, however, to maintain a continuous area designation such as "A", "B", "C" on the upper floors.

4.9.4 ROOMS

4.9.4.1 Room numbers will start with the number 100 in each area. The range of room numbers available in each area shall be 100-999. At the point of entry into the area from the elevator lobby, trace the most likely path of travel throughout the area in general clockwise direction, assigning the room numbers in alternate sequence across the corridor. Designate inner rooms by a letter subscript.

4.9.4.2 For rooms along short dead-end corridors or corridors terminated by an exit, number consecutively down one side of the corridor toward the dead end and up the other side to the starting point.

4.9.5 CORRIDORS, STAIRS, AND ELEVATORS

Corridors, stairs, and elevators shall have a separate numbering system and are not to be included in the general numbering.

4.9.5.1 Designate stairs as Stair 1, Stair 2, etc.

4.9.5.2 Designate corridors as C1-2, C3-8, etc. The letter "C" represents the corridor and the first number represents the floor. The second number indicates the particular corridor. Give separate numbers, as part of the corridor system, to waiting spaces, nurses’ stations, lobbies, vestibules, and other alcoves open to the corridor.

4.9.5.3 Number the elevators as Elevator No. P-1 (Passenger), Elevator No. S-1 (Service), etc.

4.9.6 ADDITIONS TO EXISTING BUILDINGS

When a new building joins an existing building, make the new room numbering consistent with the existing room numbering system used for the spaces in the existing building.

4.10 SIGNS, PLAQUES AND EMBLEMS

4.10.1 SAFETY SIGN

Provide a safety sign for each VA construction project over $2 million in cost. For details, see Master Specifications, Section 01010, General Requirements, and Standard Detail 01010-2.

4.10.2 CONSTRUCTION SIGN

Provide a construction sign at the site of VA construction projects over $2 million in cost. For details, see Master Specifications, Section 01010, General Requirements, and Standard Detail 01010-1.

4.10.3 DEDICATION PLAQUE

VA will furnish a dedication plaque and the contractor will install it. The plaque will be located in the lobby of the building, and shown on contract drawings. See Standard Detail 10360-2 and "Plaques and Seals" in the Technical Information Library.

4.10.4 EMBLEM

The VA emblem (seal) is to be prominently displayed on all major buildings.  Replicas are available in bronze in three sizes as shown on Standard Detail No. 10360-1. Incorporate the emblem in the design near the main entrance so as to be seen by persons approaching either in vehicles or on foot.

CHAPTER 5: SPECIAL FUNCTIONS

5.1	ANIMAL RESEARCH FACILITY (ARF) / VETERINARY MEDICAL UNIT (VMU)

5.2	AUDIOLOGY SOUND SUITES

5.3	COMPUTER ROOMS (CENTRAL)

5.4	DENTAL

5.5	ELECTROMAGNETIC SHIELDING

5.5.1	GENERAL

5.5.2	AVOIDANCE OF EMI SOURCES

5.5.3	SIGNAL STRENGTH TESTS

5.6	INTENSIVE CARE UNITS (ICUs)

5.7	ISOLATION ROOMS

5.7.1	FUNCTION

5.7.2	NEGATIVE ISOLATION FOR TUBERCULOSIS (TB)

5.7.3	ISOLATION ROOMS INPATIENT CARE UNITS (NURSING UNITS)

5.7.4	ISOLATION ROOMS IN AMBULATORY CARE

5.7.5	ISOLATION AUTOPSY ROOM IN MORGUE

5.7.6	SECLUSION ROOMS IN MENTAL HEALTH AND BEHAVIORAL (PSYCHIATRIC) PATIENT CARE UNITS

5.7.7	ISOLATION ROOM DESIGN

5.8	MAGNETIC RESOURCE/RESONANCE IMAGING

5.8.1	DESCRIPTION

5.8.2	DESIGN

5.9	PHARMACY

5.9.1	MAJOR DESIGN ISSUES

5.9.2	SECURITY

5.10	PSYCHIATRIC (MENTAL HEALTH AND BEHAVIORAL) AREAS

5.10.1	GENERAL

5.10.2	FINISHES AND DOORS

5.10.3	WINDOWS

5.10.4	CUBICLE CURTAIN TRACKS

5.11	RADIATION THERAPY

5.11.1	GENERAL

5.11.2	SHIELDING POLICY

5.11.3	SPECIFICATION OF PROTECTIVE SHIELDING

5.11.4	CERTIFICATION

5.11.5	DESIGN

5.12	RADIOLOGY (DIAGNOSTIC X-RAY)

5.12.1	GENERAL

5.12.2	EQUIPMENT ACQUISITION AND INSTALLATION

5.12.3	DESIGN

5.13	REFRIGERATORS AND FREEZERS (BUILT-IN)

5.13.1	REFRIGERATORS AND FREEZERS IN KITCHEN AREAS

5.13.2	MORTUARY REFRIGERATORS

5.14	SURGERY

5.15	TB (TUBERCULOSIS) SPACES

Blank page left intentionally

5 SPECIAL FUNCTIONS

5.1 ANIMAL RESEARCH FACILITY (ARF) / VETERINARY MEDICAL UNIT (VMU)

A. Veterinary Medical Unit, a part of Research and Development, has many special requirements. They range from HVAC, electrical, and plumbing, to equipment and finishes. If automatic cage washers are used, they require large floor depressions, which will affect the structural design. (See Paragraph 2.4, "Floor Slab Depressions", above.)

B. See VA Design Guides, Research Series, for a comprehensive graphic consolidation of VA Design Criteria for VMUs, including room-by-room guide plates.

C. For complete criteria and standards, see "Research and Development" sections of the documents described in Paragraph 1.2 above.

5.2 AUDIOLOGY SOUND SUITES

A. Sound suites (prefabricated audiometric suites or booths) are the key elements of Audiology and Speech Pathology Clinics. They require slab depressions for level access. (See Paragraph 2.4, "Floor Slab Depressions", above.)

B. See VA Space Planning Criteria (VA Handbook 7610), Chapter 204, "Audiology and Speech Pathology Service", for numbers, sizes, and (under "Design Considerations") detailed requirements for sound suites.

5.3 COMPUTER ROOMS (CENTRAL)

See Design and Construction Procedures, Topic 10, "Computer Systems", for guidelines on design of Central Computer Rooms.

5.4 DENTAL

A. VA criteria for dental spaces are very detailed and specific in many aspects, and especially so with regard to equipment, utility requirements, and furnishings.

B. See Space Planning Criteria, Chapter 222, "Dental Service", for number and size of spaces, design considerations, and functional relationships. Note that the standard operatories have doorless openings, and that minimum room dimensions, as well as areas, are given for some spaces.

C. See Equipment Guide List (PG 7610) for guidelines on specialized equipment, utilities, and furnishings.

D. In addition, room guide plates for many dental spaces are available from the Facilities Quality Service of the VA Office of Facilities Management.

E. Also see Room Finishes, Door and Hardware Schedule (PG-18-14).

5.5 ELECTROMAGNETIC SHIELDING

5.5.1 GENERAL

Attenuate electromagnetic interference (EMI) to insure satisfactory operation of electroencephalography (EEG) suites, electromyography (EMG) suites, neurosurgical operating rooms and other functional spaces housing EMI-sensitive instrumentation, as described below.

5.5.2 AVOIDANCE OF EMI SOURCES

Avoid electromagnetic interference by locating EEG suites, neurosurgical operating rooms, and other functional spaces housing EMI-sensitive instrumentation with the following separation from sources:

A. At least 15 m (50 ft.) from elevator motors, air handling motors, and electrical distribution transformers

B. At least 7.5 m (25 ft.) from electrical lines carrying 100 A (amperes) or more

C. As far as practicable from hospital broadcasting and wireless stations

5.5.3 SIGNAL STRENGTH TEST

5.5.3.1 During the construction phase of the project after the structure has been constructed but prior to installing the finish work in the neurosurgical operating room, EEG and EMG suites, and other spaces housing EMI-sensitive instruments, conduct a signal strength test to measure the field strength of radio and television signals in these spaces if the building is located within a mile of the following facilities:

A. A short-wave radio antenna transmitting at over 100,000 W (watts)

B. A VHF television or FM radio antenna transmitting at over 250,000 W (watts)

C. A UHF television antenna transmitting at over 1,000,000 W (watts)

5.5.3.2 These tests are also required if the separation requirements given above in paragraph 5.5.2 are not met. If signal strength exceeds 0.07 V/m (volts/meter), then provide these areas with EMI shielding. (This may require a floor slab depression; see Paragraph 2.4.2.1G)

5.5.3.3  An organization that has had previous experience in signal strength measurements shall conduct the field tests and evaluate them over the entire frequency spectrum up to 200 MHz (megahertz).

5.6 INTENSIVE CARE UNITS (ICUs)

A. Intensive Care Units are specialized nursing facilities for patients whose conditions are too acute for conventional nursing units. They are categorized as Medical, Surgical, Coronary Care, and, for small hospitals, General Purpose. All ICUs, except Coronary Care, have one or more isolation rooms; the remainders of the beds are in open-ended cubicles.

B. See Space Planning Criteria, Chapter 102, "Intensive Care Units", for room sizes, design considerations, and relationship diagrams and matrices.

C. For complete criteria, see the other documents described in Article 1.2 above.

5.7 ISOLATION ROOMS

5.7.1 FUNCTION

5.7.1.1 Isolation rooms may either be negative isolation (for those whose communicable diseases must be contained) or positive isolation (for those whose immune systems cannot tolerate normal exposures), depending on the difference in air pressure between the rooms and adjoining spaces.

5.7.1.2 Formerly, isolation rooms could be designed for alternate use as negative or positive. This is no longer permitted by the CDC (Center for Disease Control), so isolation rooms must be specifically designated as negative or positive, and so designed. This requires that the proposed use for each one be specified at the time of design by appropriate medical center authority.

5.7.2 NEGATIVE ISOLATION FOR TUBERCULOSIS (TB)

Negative isolation is generally required for containment of tuberculosis.  See "Tuberculosis Facility Guidance" in the Technical Information Library for detailed guidance on the many functional areas where isolation rooms or some degree of isolation may be required for TB containment.

5.7.3 ISOLATION ROOMS IN PATIENT CARE UNITS (NURSING UNITS)

VA Space Planning Criteria provides isolation rooms, without specifying whether negative or positive, in all:

A. Intensive Care Units

B. MS&N (Medical, Surgical, and Neurological) Patient Care Units

C. Spinal Cord Injury Centers

5.7.4 ISOLATION ROOMS IN AMBULATORY CARE

Space Planning Criteria provides a negative isolation room called "Multi-Purpose Exam Room" in Emergency Care (ER) suites.

5.7.5 ISOLATION AUTOPSY ROOM IN MORGUE

Space Planning Criteria provides an "Isolation/Teaching Autopsy Room" in the morgue (a part of Pathology and Laboratory Medicine Service) of larger hospitals.

5.7.6 SECLUSION ROOMS IN MENTAL HEALTH AND BEHAVIORAL (PSYCHIATRIC) PATIENT UNITS

These spaces are sometimes called "isolation rooms", but, they serve a different function, prevention of self-injury, rather than limiting the spread of disease.

5.7.7 ISOLATION ROOM DESIGN

5.7.7.1 The most significant feature of an isolation room is its air pressure with regard to that of adjoining spaces; thus it must be clearly designated as negative or positive. The pressure differential depends on the design of the HVAC system. See HVAC Design Manual, Paragraph 3.11, "Isolation Rooms".

5.7.7.2 For size and number of isolation rooms in a given functional area, see VA Space Planning Criteria (Handbook 7610).

5.7.7.3 Isolation rooms require a tight enclosure to maintain the desired pressure differentials. See Paragraph 4.3, "Partitions", above for partition construction. See "Room Finishes, Door and Hardware Schedule" for finishes, etc.

5.8 MAGNETIC RESONANCE IMAGING (MRI)

5.8.1 DESCRIPTION

MRI is a diagnostic imaging technique that uses a very strong magnetic field.  The magnetic field is produced by a high-strength magnet cooled to a very low temperature (about 4 degrees Kelvin).

5.8.2 DESIGN

5.8.2.1 The magnetic field is subject to distortion by ferrous materials within its critical area, both fixed items of construction and moving items such as carts and elevators. Since such distortions reduce the quality of the desired image, limiting them is a major consideration of MRI unit design.

The magnetic field may also affect computerized equipment and devices such as pacemakers within its critical area, so control of this area is a major design consideration.

5.8.2.2 The space that houses the magnet, patient table, and related equipment is called the gantry room. The gantry room requires radio-frequency shielding, and may require special magnetic shielding, usually of steel sheets. All equipment in the room should be made of non-magnetic material. Ductwork, plumbing, and electrical items must also be non-magnetic within certain distances, depending on the MRI unit to be installed.

5.8.2.3 The magnetic field extends in three dimensions; thus proper sitting of an MRI unit is of critical importance, and larger units are often best accommodated in new space at ground level.

5.8.2.4 For details of space, design, construction, and equipment, see Space Planning Criteria, Chapter 275, "Magnetic Resource Imaging", and the Equipment Guide List. For a comprehensive functional narrative, functional diagrams, and guide plates, see Design Guide "Magnetic Resonance Imaging" (in the "Imaging" series).

5.9 PHARMACY

5.9.1 MAJOR DESIGN ISSUES

Pharmacy design must reconcile the need for security with the functional need to distribute medications throughout the facility. Ideally, this leads to a layout focused on a dedicated dumbwaiter or other secure transport system.  See Space Planning Criteria, Chapter 268, "Pharmacy Service", for a diagram of such a system, as well as space, design considerations, and relationship diagrams and matrices. See Design Guides "Pharmacy" (in the “Clinical” series) and "Outpatient Pharmacy" (in the "Primer" series) for narratives of pharmacy operations, functional diagrams, and guide plates.

5.9.2 SECURITY

Both inpatient and outpatient pharmacies require special features for security, including vaults for controlled substances. See Design and Construction Procedures, Chapter 14, "Security", for vault construction and other security requirements, including "bullet-proof" outpatient dispensing (service) windows. Also, see Architectural Standard Detail 11022-1.dwf for service window and package transfer box.

5.10 PSYCHIATRIC (MENTAL HEALTH/BEHAVIORAL) AREAS

5.10.1 GENERAL

5.10.1.1 Psychiatric nursing units are called "Mental Health and Behavioral Patient Care Units" by the VA. They include:

A. Psychiatric Units

B. Substances Abuse Units

1. Drug Abuse Treatment Units

2. Alcohol Dependency Units

See Space Planning Criteria, Chapter 110, "Mental Health and Behavioral Patient Care Units" for detailed space criteria, including design considerations, space relationship diagrams, and interfunctional relationship matrix.

5.10.1.2 Other psychiatric areas (and their corresponding criteria) include:

A. Mental Health Clinic (Chapter 260)

B. Substance Abuse Clinic (Chapter 202)

C. Day Hospital (Chapter 300)

D. Day Treatment Center (Chapter 261)

5.10.2 FINISHES AND DOORS

5.10.2.1 GENERAL

See "Room Finishes, Door and Hardware Schedule" (PG-18-14) in the Technical Information Library for room-by-room listings of finishes, door size and type, and hardware in the various psychiatric areas. See Master Construction Specifications Section 08710, "Builders Hardware", for special door hardware requirements.

5.10.2.2 BARRIER DOORS AND STAIRWAY DOORS

Barrier doors and stairway doors in Mental Health and Behavioral Patient Care Units shall be locked at all times (rigid handle), but locks shall be operable by key from either side of doors. Attendants, nurses, and other psychiatric nursing unit staff shall carry keys at all times to control entry and exiting from psychiatric units. See Master Construction Specifications Section 08710, "Builders Hardware", for special requirements for psychiatric keys.

5.10.3 WINDOWS

5.10.3.1 For glazing requirements in psychiatric areas, see Article 3.5.6 above.

5.10.3.2 Use of floor to ceiling window wall system in psychiatric areas is not recommended without addressing all patient safety and security concerns. Provide details for holding glass in the framing system in such a manner that it can withstand lateral forces in excess of force required to break the glass.

5.10.4 CUBICLE CURTAIN TRACKS

Do not use cubicle curtain tracks in patient bedrooms of Mental Health and Behavioral Nursing Units.

5.10.5 PATIENT TOILETS AND BATHROOMS

5.10.5.1 The VA Equipment Guide List call for grab bars in all Psychiatric toilets and baths, although the Uniform Federal Accessibility Standards requires only 10% of them to be so equipped. For areas to be used by high-risk patients, “institutional grab bars are available with a continuous flange, closing the space between the bar and the wall.

5.10.5.2 Mirrors in Mental Health and Behavioral Patient Care Units should be heat tempered glass; see Equipment Guide List, Chapter 110.xls.

5.10.5.3 Shower rods in Mental Health and Behavioral Patient Care Units should not support the weight of a patient. See Master Construction Specifications Section 10800, "Toilet and Bath Accessories".

5.11 RADIATION THERAPY

5.11.1 GENERAL

5.11.1.1 Radiation therapy employs high energy X-rays, gamma rays, and electron beams to treat tumors and other malignancies. This radiation is generated by devices ranging from 50 kilovolt X-ray units, to supervoltage units (Cobalt 60) for gamma rays, to linear accelerators of more than 10 million electron volts.

5.11.1.2 The more powerful units usually require shielding by concrete vaults with maze-like entries.

5.11.2 SHIELDING POLICY

Provide shielding as prescribed by a physicist, approved by the American Board of Radiology in accordance with the appropriate standards and regulations contained in Report No.102 of the National Council on Radiation Protection and Measurements, obtainable from NCRP Publications, 7910 Woodmont Avenue, Suite 400, Bethesda, MD-20814.

5.11.3 SPECIFICATION OF PROTECTIVE SHIELDING

State the prescribed shielding in terms of millimeters of lead or in millimeters (in.) of wall, ceiling, floor and door construction of equivalent protection thickness.

5.11.4 CERTIFICATION

Post a certificate, stating the lead equivalent protection of each surface, in all rooms with radiation shielding.

5.11.5 DESIGN

5.11.5.1 See Space Planning Criteria, Chapter 277, "Radiation Therapy Service" for space requirements, operating rationale, and design considerations.

5.11.5.2 See Design Guides, "Radiation Therapy" (in the "Imaging" series) for

consolidated requirements, including a functional narrative and guide plates for the principal treatment rooms.

5.11.5.3 For other details of criteria, see the documents described in Paragraph 1.2 above.

5.12 RADIOLOGY (DIAGNOSTIC X-RAY)

5.12.1 GENERAL

5.12.1.1 Radiology consists of various spaces for diagnostic imaging, primarily by the use of X-rays (ionizing radiation):

A. Radiographic/Fluoroscopic Rooms – including general purpose rooms, dedicated chest rooms, and automated radiographic rooms

B. Special Procedure Rooms – complex radiographic/fluoroscopic rooms which may be designated as angiographic or vascular/neuroradiology

C. Mammography Room – a specialized radiographic room

D. Computerized Tomography Imaging System Suite (CT Suite)

5.12.1.2 Ultrasound Rooms are also part of Radiology, although they do not use X-rays.

5.12.1.3 X-ray suites include film processing areas, which should accommodate both automated daylight film processing systems and darkroom facilities. A central silver collection room (for recovery of silver from film processing solutions) should be located below radiology.

5.12.2 EQUIPMENT ACQUISITION AND INSTALLATION FOR X-RAY ROOMS

5.12.2.1 All rooms with high-tech radiology equipment should be designed for a generic installation system, or to be shelled in with finish work scheduled for completion as late as possible in the construction process.

5.12.2.2 Where a generic installation system will be used, provide a universal X-ray raceway system (DOD/VA Universal X-ray (R-F) Room). See Architectural Standard Details 13091-3.dwf and 13091-4.dwf. This universal raceway system is capable of accepting all routine radiographic, fluoroscopic, and tomographic equipment, but should not be used in potentially wet locations, such as cystographic rooms.

5.12.2.3 If the shelled-in option is chosen, for Special Procedures Rooms, the A/E shall develop a list of work items and materials required for the completion of shelled-in spaces and list these on the construction documents.  Unit costs for these items will be provided by the construction contractor.

5.12.3 DESIGN

See Space Planning Criteria, Chapter 276, "Radiology Service" for space needs, functional descriptions, design considerations and overall functional layout diagrams. See Design Guides, "Radiology Service" (in the "Imaging" series) for a detailed narrative of operations, technical requirements, detailed functional diagrams of Special Procedures and CT Suites, and guide plates.

5.12.3.1 X-RAY CONTROL ROOMS

5.12.3.1.1 Provide single-pane viewing windows of conventional lead glass for

X-ray control rooms. Where the control room projects into and is located near the corner of the diagnostic X-ray room, the projecting control room partition shall have a portion of wall angled toward the X-ray work space.  Locate the viewing window in this angled section.

5.12.3.1.2 To allow for clearance of X-ray tube crane travel, do not exceed a height of 2300 mm (7 ft. 6 in.) above the floor for that portion of the shielded partition of a control room which projects into a diagnostic X-ray room. Feed all electric service into the projecting control-room partition up from the floor or horizontally from the wall where the control room projects. Leave the space above the projecting control area clear to allow X-ray equipment to traverse.

5.12.3.2 PARTITIONS AND SHIELDING

See paragraph 4.3 above for partition construction. Use lead-lined gypsum wallboard for shielding, as per Architectural Standard Details 13091-1.dwf and 13091-2.dwf.

5.12.3.3 CEILING HEIGHTS

Some manufacturers’ equipment for cardiac cath and special procedures rooms may require more than the standard 3.0 m (9 ft. 6 in.). Verify requirements with medical center before establishing a firm ceiling height in these spaces.

5.12.3.4 CEILING SUPPORT SYSTEM

Provide a ceiling support system for all diagnostic rooms in accordance with Architectural Standard Detail 13091-5.dwf.

5.12.3.5 FLOOR DEPRESSIONS

Floors in radiographic and special procedure rooms must be depressed to accommodate the floor trench duct system. (See paragraph 2.4 above.) Some floors of the CT Suite must be similarly depressed for an access floor system. (See Guide Plate 4-5 in the Radiology Design Guide.)

5.13 REFRIGERATORS AND FREEZERS (BUILT-IN)

5.13.1 REFRIGERATORS AND FREEZERS IN KITCHEN AREAS

5.13.1.1 TYPE AND SIZE

When walk-in refrigerators and freezers are programmed, provide the prefabricated sectional type, with a minimum size of 4.5 sq. m. (48 sq. ft.) net floor area. If smaller size is required, use reach-in type.

5.13.1.2 DOORS

Doors shall be 1200 mm (48 in.) wide. Exception:  Doors for freezers with floor area less than 14 m2 (150 sq. ft.) may be 900 mm (36 in.) wide.

5.13.1.3 FLOOR

Refrigerator/freezer floor shall be flush with the floor of adjoining room.  Exception: a raised refrigerator/freezer floor with ramp may be used in

existing buildings where it would be impracticable to install a flush floor.  Floor finish shall be non-slip quarry tile on tile setting bed. Floor insulation shall be load bearing type. For freezer spaces on grade or above grade with fill, provide floor heating system beneath floor insulation to prevent frost formation and subsequent floor heaving.

5.13.1.4 CEILING SPACE ENCLOSURE

Enclose ceiling space above refrigerator/freezer along corridors and finished rooms with finish materials as required from top of refrigerator/freezer up to finished ceiling. Do not locate compressor on top of refrigerator or freezer.

5.13.1.5 SPACE FOR COOLING SYSTEMS

Coordinate with Mechanical Engineer to provide appropriate space for refrigeration cooling systems. See HVAC Design Manual, Article 4.11.4 for guidance.

5.13.1.6 ENTRY TO FROZEN FOOD FREEZERS

Provide entrance to frozen food freezer through a refrigerator of higher temperature.

5.13.2 MORTUARY REFRIGERATORS

5.13.2.1 TYPES

Provide prefabricated walk-in type mortuary refrigerators, except at small facilities where self-contained mortuary refrigeration units are specifically requested.

5.13.2.2 DESIGN AND CONSTRUCTION

Walk-in-type mortuary refrigerators shall be built as described above for kitchen refrigerators and freezers except:

5.13.2.2.1 Door shall be standard 1200 mm (48 in.) width.

5.13.2.2.2 Install mortuary refrigerators in existing buildings so that the finished floor levels are the same. This shall be accomplished by installing such a prefabricated refrigerator enclosure, minus the enclosure floor, directly upon the floor slab. Seal the enclosure perimeter against air and waste leakage, and, where required by climate or location, place insulation with vapor barrier below the slab to avoid condensation.

5.14 SURGERY

A. See VA Design Guides, Surgical Series, for a comprehensive graphic consolidation of VA design criteria for surgery, as well as a detailed narrative of the functional assumptions upon which the criteria are based. Additional details of criteria are found in the documents described in paragraph 1.2 above.

B. For neurological operating rooms, see Paragraph 5.5 above for electromagnetic shielding.

5.15 TB (TUBERCULOSIS) SPACES

A. See Tuberculosis Facility Guidance in the Technical Information Library for a summary of technical requirements for addressing tuberculosis, and a discussion of the many functional areas where isolation rooms or some degree of isolation may be required.

B. See Design Guides, Primer Series, "Tuberculosis (TB)" for a comprehensive graphic consolidation of TB criteria, as well as a functional narrative and guide plates. VA Space Planning criteria does not specifically address TB, but provides for non-specific isolation rooms, which may serve as TB rooms, in several areas.(See Article 5.7 above.)

- - - - - - END - - - - - -

# GLOSSARY OF ACRONYMS

A/E	Architect Engineer

ARF	Animal Research Facility

ASHRAE	American

CADD	Computer Aided Design and Drafting

CDC	Center for Disease Control

CT	Computerized Tomography

DD-1	Design Development 1

DOD	Department of Defense

DOE	Department of Energy

EEG         Electroencephalograph

EIFS	Exterior Insulation Finish System

EMG	Electromyography

EMI	Electromagnetic Interference

HVAC	Heating, Ventilating and Air Conditioning

ICU	Intensive Care Unit

MRI	Magnetic Resonance Imaging

MS&N	Medical, Surgical, and Neurological

NFPA	National Fire Protection Association

NHCU	Nursing Home Care Unit

NIBS	National Institute of Building Sciences

OSHA	Occupational Safety and Health Administration

OT	Occupational Therapy

PT	Physical Therapy

R-F	Radiographic - Fluoroscopic

RMS	Rehabilitation Medicine Service

SCIU	Spinal Cord Injury Unit

TB	Tuberculosis

UFAS	Uniform Federal Accessibility Standards

VA	Department of Veterans Affairs

VAHBS	VA Hospital Building System

VHA	Veterans Health Administration

VMU	Veterinary Medical Unit

Blank page left intentionally

INDEX

ABBREVIATIONS	1.17.1B

ACCESSIBILITY	1.4

Entrances and exits	3.2.7

Showers	4.8.3

AMBULANCE ENTRANCES	3.2.1

ANIMAL RESEARCH FACILITIES (ARF)	5.1

ATTIC WALKWAYS	3.8.4

AUDIOLOGY SOUND SUITES	5.2

AUTOMATIC DOORS	3.4

CADD REQUIREMENTS	1.17.2

CAGE WASHERS, SLAB DEPRESSION FOR	2.4.2.1J

CANOPIES

Extending over paths of trucks or buses	3.2.5

Over ambulance entrances	3.2.1.2

Over patient entrances	3.2.2.1

Over loading dock platforms	3.2.4.2

CART WASHERS, SLAB DEPRESSION FOR	2.4.2.1K

CEILING HEIGHTS	4.6.2

CEILING PLANS	1.17.7

CODES	1.3

COMPUTER ROOMS	5.3

CONSTRUCTION SIGN	4.10.2

CORNER GUARDS	4.5.2

CORRIDOR, STAIR, AND ELEVATOR NUMBERING	4.9.5

CRITERIA

Architectural	1.2

Space Planning	1.2F

CUBICLE CURTAIN TRACKS	4.6.1

DEDICATION PLAQUE	4.10.3

DENTAL SPACES	5.4

DETAILS, STANDARD	1.2G

DOORS	4.1

DOOR LOCKS

Exterior doors	3.3

Psychiatric nursing units	5.10.2.2

DRAWINGS	1.17

DRINKING FOUNTAINS/ELECTRIC WATER COOLERS	4.7.4

Wall protection at	4.7.3

ELECTRICAL SPACES	1.6

Electrical closets	1.6.6

Electrical rooms	1.6.3

Transformer vaults	1.6.3

ELECTROMAGNETIC LOCKING SYSTEMS	3.3.1.1

ELECTROMAGNETIC SHIELDING	5.5

ELEVATORS	1.7

ENERGY CONSERVATION	3.1

ENTRANCES, PATIENT	3.2.2, 3.2.7

EQUIPMENT	1.2C, 1.2D, 1.17.4

EXIT DOOR LOCKS	3.3

EXTERIOR INSULATION FINISH SYSTEM	3.10

FINISHES	1.2E, 4.4

Finish schedule	4.4.2

FIRE ALARM EQUIPMENT ROOMS	1.6.4

FLOOR DRAINS	1.17.6

Membrane waterproofing at floor drains	2.2

Floor slope to drains	2.4.1A

FLOOR NUMBERING	4.9.2

FLOOR SLAB DEPRESSIONS	2.4

FLOOR-TO-FLOOR HEIGHTS	1.10

FOUNDATION DRAINS	2.1

GRAB BARS	1.4.1, 1.4.3.1, 4.8.3

GYPSUM WALLBOARD	4.3.3

HANDRAILS AND WALLGUARDS	4.5.1

INFECTION CONTROL	1.2I

INSULATION	3.1.2

INTENSIVE CARE UNITS (ICUs)	5.6

ISOLATION ROOMS	5.7

LAVATORIES AND SINKS, WALL PROTECTION AT	4.7.3

LEAD-LINED PARTITIONS	4.3.3.2

LOADING DOCKS	3.2.4

LOUVERS, VENTILATION	3.7

MAGNETIC RESONANCE IMAGING (MRI)	5.8

MECHANICAL SPACES	1.6

Energy center	1.6.1

MENTAL HEALTH & BEHAVIORAL PATIENT CARE UNITS	5.10

METAL STUDS	4.3.1

MORGUE ENTRANCES/EXITS	3.2.3

NAMES OF ROOMS AND SPACES	1.12.3

PARAPET WALLS	3.8

PARTITIONS	4.3

PHARMACY	5.9

PIPE BASEMENTS	2.3

PSYCHIATRIC AREAS	5.10

Patient toilets and baths	5.10.5

Windows	5.10.3

QUARRY TILE FLOORS, SLAB DEPRESSIONS FOR	2.4.2.1

RADIATION THERAPY	5.11

Shielding policy	5.11.2

RADIOLOGY (X-RAY)	5.12

REFRIGERATORS & FREEZERS, KITCHEN	5.13.1

REFRIGERATORS, MORTUARY	5.13.2

RENDERINGS	1.16

REVIEWS	1.13

Exterior design reviews	1.13.2

REVOLVING DOORS	3.2.2.2

ROOFS, LOW-SLOPE	3.9

ROOF DRAINS	3.9.3.3

ROOF GUARDRAILS	3.8.5

ROOF WALKWAYS	3.8.3

ROOM NUMBERS	4.9

SAFETY SIGN	4.10.1

SCREENS	3.6

Security screens	3.6.1.3

Ventilation system screens	3.6.2

SECLUSION ROOMS	5.7.6

SECURITY PARTITIONS (AT SERVICE WINDOWS)	4.3.4

SEISMIC DESIGN	1.14

SHOWERS	4.8

SILVER COLLECTION ROOM	5.12.1.3

SURGERY	5.14

TELECOMMUNICATION CLOSETS	1.6.6

TELECOMMUNICATION EQUIPMENT AND CONSOLE ROOMS	1.6.5

TOILET ROOM PARTITIONS	4.7.1

TRANSFORMER VAULTS	1.6.3

TUBERCULOSIS (TB)	5.7.2, 5.15

ULTRA-SOUND	5.12.1.2

VA HOSPITAL BUILDING SYSTEM (VAHBS)	1.15

Slab depressions for VAHBS	2.4.3

Ceiling heights in VAHBS	4.6.2

VA SEAL/EMBLEM	4.10.4

VETERINARY MEDICAL UNIT (VMU)	5.1

WINDOWS	3.5

Safety glazing of	3.5.6

Screens	3.6

Shades and blinds	4.2

Sill height	3.5.4

With integral blinds	3.5.3

X-RAY ROOMS/RADIOLOGY	5.12

Ceiling support systems	5.12.3.4

Control rooms	5.12.3.1

Equipment acquisition & installation	5.12.2

Shielding	4.3.3.2, 5.12.3.2

Slab depressions for	2.4, 2.4.3, 5.12.3.5

Universal x-ray raceway system	5.12.2.2

- - - - - - END - - - - - -

# Text boxes

Architectural Design Manual

For

- New Hospitals

- Replacement Hospitals

- Ambulatory Care

- Clinical Additions

- Energy Centers

- Outpatient Clinics

Department of Veterans Affairs

Office of Facilities Management

Facilities Quality Service (181A)

810 Vermont Avenue, N.W.

Washington, D.C. 20420

Department of

Veterans Affairs