Jack Lysfjord’s Comments to “Sterile Drug Products Produced by Aseptic Processing—Current Good Manufacturing Practice”  Draft.  Docket # 2003D-0382.

An overall general comment that communications are improving between the Agency and industry.  A great deal of listening took place between the September 2002 version and the September 2003 version.  My compliments to the team for all their work and to PQRI and other organizations and industry experts for the positive changes in this document.

#1  Line 143,157.,.,.,.,……

If we are looking to the future and not the past, why are we using the obsolete “Class 100” designator instead of ISO 5?  If class 100 is referenced IT should be in parentheses not the ISO value.  ISO has superceded the old system.

#2  Line 196, 199

Why does the document dance between “Laminar Flow” and “Unidirectional Flow”?

My understanding is that terminology is now “Unidirectional Flow”.

#3  Lines 1534-1540

Thank you for the very positive statement on the favorable use of isolators for aseptic processing.  This paragraph only refers to positive pressure isolators.

As new pharmaceutical and biopharmaceutical products are developed, there is a trend toward a great increase in the number of potent products requiring containment.  The 2002 Survey conducted by Lysfjord/Porter found 32 out of 108 respondents reported using isolators for containment reasons or 29%.  This number will be increasing based on the products in development and clinical trials.  Depending on the product operator exposure levels and therefore the design requirements of the isolator system, a negative pressure system may be the best compromise along with a change in surrounding room classification.  A brief paragraph  at the end of appendix 1 that would allow the possibility for this type of design based on good science would keep this document viable for a longer time period and not create the impression that ONLY positive pressure isolators are acceptable.

#4  Lines 1570-1583 Airflow

I don’t understand why turbulent flow is allowable in a closed isolator and not an open isolator.  As and isolator gets narrower and narrower, turbulence has a greater probability compared to an open cleanroom.  The goal is unidirectional flow as much as possible, KEEPING PEOPLE OUT of the critical area and maintaining the requisite environmental conditions within the isolator.

#5  Lines 1591- 1607  Pressure Differential

This is an example of “more is not necessarily better”.  Increasing pressure can cause the following:

- Blowing over of small lightweight containers at transition points (Mouseholes)

- Powder filling lines where product “float” is an issue can be detrimental.  This is especially true when the product is potent and requires containment.

- Higher particle counts in a specific location due to vortexes picking up particles on either side of a depyrogenation tunnel belt.

- Pressure balance issues for depyrogenation tunnels connected to isolators

The controlling issue again is maintaining the requisite environmental conditions within the isolator and not the pressure by definition.  The design and qualification of the system should protect the product by maintaining the interior environmental conditions.

Respectfully submitted 11-04-2003

Jack Lysfjord, Vice President Consulting

Valicare Division, Bosch Packaging Technology

763 493 6771

Fax:  763 493 6783

jack.lysfjord@boschpackaging.com