## Department of Veterans Affairs				MSN IV Circular 774-02-005

National Cemetery Administration				August 30, 2002

Memorial Service Network IV					Page 1

## Indianapolis, Indiana

# SUBJECT:  Portable Fire Extinguisher Inspection and Maintenance Procedures

1.  PURPOSE:  To establish standard procedures for the inspection and maintenance of portable fire extinguishers.

2.  POLICY:  Portable fire extinguishers will be inspected and maintained to ensure that they are properly located and operational in accordance with NFPA standards.

3.  DEFINITIONS:

- Inspection is a “quick check” that an extinguisher is available and will operate.  It is intended to give reasonable assurance that the extinguishers are fully charged and operable.  This is done by seeing that it is in its designated place, that it has not been actuated or tampered with, and that there is no obvious or physical damage of condition to prevent operation.

- Maintenance is a “thorough examination” of the extinguisher.  It is intended to give maximum assurance that an extinguisher will operate effectively and safely.  It includes a thorough examination and perform any necessary repairs or replacement of an extinguisher.  It will normally reveal the need for hydrostatic testing.

4.  TYPE OF EXTINGUISHER:  Portable fire extinguishers located at our facilities range in size from 2.5 to 20 pounds.  The extinguishing agents used are – carbon dioxide for class B - C fires and dry chemical for class B - C and class A - B - C fires.  The type and rating of portable fire extinguishers at our facilities are as follows.

- 5 lb. CO2

- 15 lb CO2

- 2.5 lb. A-B-C

- 5 lb. A-B-C

- 10 lb. A-B-C

- 20 lb. A-B-C

- 10 lb. B-C

5.  RESPONSIBILITIES:

- The Cemetery Director will bear the overall responsibility for portable fire extinguisher inspections within the Cemetery Facilities.

- The Cemetery Foreman/Safety Officer will be directly responsible for the proper inspection and annual maintenance check of all portable fire extinguishers (in buildings, outside buildings, mounted on equipment or in vehicles).  Repair request will be submitted through the Cemetery Director to correct any deficiencies identified during inspections.

6.  GUIDELINES AND PROCEDURES:

- Portable fire extinguishers will be inspected monthly.  The inspection should include the following:

Department of Veterans Affairs				MSN IV Circular 774-02-005

National Cemetery Administration				August 30, 2002

Memorial Service Network IV					Page 2

Indianapolis, Indiana

  - Extinguishers are located in their designated location, are secured properly and are the proper type.

  - Extinguishers are not obstructed with respect to access or visibility.

  - Extinguishers are examined for obvious physical damage, corrosion, leakage, or clogged nozzles.

  - Legible operating instructions are on the extinguisher nameplate facing outward.

  - Seals and tamper indicators are not broken or missing.

  - Pressure-gauge readings or indicators are in the operable ranges.

- Annual maintenance will involve a thorough examination of the fire extinguisher shell and its external mechanical parts.  The maintenance will include the following:

  - All monthly inspection items.

  - Inspection of the hose and nozzle for cracks, blockages, or other damage.

  - Inspection of extinguisher shell for corrosion, dents, or other damage.

  - Carbon dioxide extinguishers are weighed to ensure no weight deviation greater than 10%.

- When inspection or maintenance of any extinguisher reveals a deficiency in operating condition, the following corrective actions are to be taken immediately.

  - A spare extinguisher of the same type and equal or greater rating shall replace the extinguisher.

  - Defective extinguishers are to be marked as such and placed in appropriate place until repair and/or recharging is performed.

- Documentation of inspection and maintenance will be provided by maintaining the following records:

  - The fire extinguisher checklist, which contains the location of each fire extinguisher; its weight, type, and dates of inspections; and annual maintenance.

  - A fire extinguisher inspection record tag is attached to each extinguisher and provides the following information:

    - The date the extinguisher was inspected.

    - The condition of the extinguisher.

    - The initials of the person performing the inspection.

  - The fire extinguisher inspection record must indicate the date of the last charge; recharge & the last date of hydrostatic testing must be recorded.

- Hydrostatic testing of extinguishers is to be performed at 5-year intervals for CO2 extinguishers and 12-year intervals for dry chemical and halon extinguishers.  Extinguishers that require one 12-year hydrostatic test shall be emptied and subjected to maintenance every six years interval.

Department of Veterans Affairs				MSN IV Circular 774-02-005

National Cemetery Administration				August 30, 2002

## Memorial Service Network IV					Page 3

Indianapolis, Indiana

- If these inspections and maintenance procedures are performed by outside vendors under contracts, the Cemetery Director will obtain a copy of the annual inspection and maintenance report from the vendor and submit a copy of this report to the Memorial Service Network IV Safety Officer by the end of the contract and fiscal year.

- See Attachment “A”:  Sample of a Fire Extinguisher Inspection Record Log (Monthly).

- See Attachment “B”:  Sample of a Fire Extinguisher Maintenance Record Log (Annual).

7.  REFERENCES:  NFPA –10 & Safety Requirements for VA National Cemeteries Handbook.

8.  RECESSIONS:  None.

9.  REVIEW DATE:  Annual – One year from date of policy.

George M. Webb

MSN IV Director

Attachments:

“A”

“B”

Distribution:

Cemetery Directors

Safety Officers

Supervisors/Foremen/Work Leaders

Attachment “A”

Attachment “B”