UNITED STATES DEPARTMENT OF AGRICULTURE

Rural Electrification Administration

BULLETIN 1751E-302

SUBJECT:  Power Requirements for Digital Central Office Equipment

To:  All Telephone Borrowers

REA Telephone Staff

EFFECTIVE DATE:  Date of Approval

EXPIRATION DATE:  Three years from effective date

OFFICE OF PRIMARY INTEREST:  Central Office Equipment Branch,

Telecommunications Standards Division

PREVIOUS INSTRUCTIONS:  This bulletin replaces REA

Telecommunications Engineering & Construction Manual (TE&CM) Section 302, Power Requirements for Community Central Office Equipment, Issue No. 6, dated April 1989.

FILING INSTRUCTIONS:  Discard REA Telecommunications Engineering & Constructions Manual (TE&CM) 302, Power Requirements for Digital Central Office Equipment, Issue 6, dated April 1989, and replace it with this bulletin.  File with 7 CFR 1751 and on REANET.

PURPOSE:  This bulletin provides REA borrowers, and other interested parties with information concerning power requirements for digital central office equipment.

James B. Huff Sr.						10/15/93

____________________________          ___________________________

Administrator                              Date

TABLE OF CONTENTS

1.  GENERAL.....................................................4

2.  BASIS FOR CALCULATIONS......................................4

3.  CALCULATIONS................................................6

FIGURE   1    -  NORTHERN TELECOM, DMS-100......................8

FIGURE   1.1  -  NORTHERN TELECOM DMS-100 (EXAMPLE).............9

FIGURE   1.2  -  NORTHERN TELECOM DMS-100......................10

FIGURE   1.3  -  NORTHERN TELECOM DMS-100 (EXAMPLE)............11

FIGURE   1.4  -  NORTHERN TELECOM DMS-10 400 SERIES............12

FIGURE   1.5  -  NORTHERN TELECOM DMS-10 400 SERIES (EXAMPLE)..13

FIGURE   1.6  -  NORTHERN TELECOM DMS-10 400 SERIES............14

FIGURE   2    -  SIEMENS STROMBERG-CARLSON DCO DCO-E/DCO-SE....16

FIGURE   2.1  -  SIEMENS STROMBERG-CARLSON DCO DCO-E/DCO-SE....19

FIGURE   3    -  REDCOM MDX....................................22

FIGURE   4    -  AT&T 5ESS SWITCH..............................23

FIGURE   4.1  -  AT&T 5ESS SWITCH (EXAMPLE)....................25

FIGURE   5    -  MITEL GX5000..................................27

FIGURE   5.1  -  MITEL GX5000 (EXAMPLE)........................28

FIGURE   6    -  TRANSMISSION ELECTRONICS CURRENT DRAIN........29

FIGURE   7    -  ESTIMATING TELEPHONE BATTERY SIZES............30

FIGURE   8    -  CHARGER CAPACITY..............................31

INDEX:

Power Requirements For Digital Central Office Equipment

ABBREVIATIONS

AC     Alternating Current

AH     Ampere Hour

AM     Administrative Module

AMAF   Automated Message Accounting Frame

BHA    Busy Hour Attempts

BMC    Billing Media Converter

BTU    British Thermal Unit

CC     Common Control

CCS    Hundred Call Seconds

CM     Communication Module

CMF    Control and Maintenance Frame

COE    Central Office Equipment

CPU    Central Processing Unit

CUA    Circuit Unit Assembly

DAT    Digital Analog Trunk

DC     Direct Current

dc-ac  direct current - alternating current

dc-dc  direct current - direct current

DCI    Digital Carrier Interface

DCM    Digital Carrier Module

DCO-E  Digital Central Office Exchange

DCS-SE Digital Central Office Small Exchange

DCTU   Digital Carrier Trunk Unit

DLTU   Digital Line & Trunk Unit

DTC    Digital Trunk Controller

DTMF   Dual - Tone Mutlifunction

GDSU   Global Digital Service Unit

GPIO   General Purpose Input Output

LCE    Line Concentrating Equipment

LCE    Line Concentrator Equipment

LGC    Line Group Controller

LLS    Local Line Switch

LTF    Line Trunk Frame

LU     Line Unit

MDX    Modular Digital Exchange

MMSU   Modular Metallic Service Unit

MSU    Modular Shelf Unit

MTM    Maintenance Trunk Module

OPM    Outside Plant Module

OPSM   Outside Plant Subscriber Module

P.E.   Peripheral Equipment

PCCM   Power Cooling Control Module

PDC    Power Distribution Center

PWBA   Printed Wire Board Assembly

RLCM   Remote Line Concentrator Module

RLG    Remote Line Group

RSLE   Remote Line Subscriber Equipment

RSLM   Remote Subscriber Line Module

SCM    Subscriber Carrier Module

SLC    Subscriber Loop Carrier

T&M    Trunk and Maintenance

TM     Trunk Module

TMF    Toll Multifunction

TU     Trunk Unit

v      volts

1.  GENERAL

1.1  This bulletin is intended to provide REA borrowers, consulting engineers, contractors and other interested parties with technical information for use in the design and construction of REA borrowers' telephone systems.  It discusses, in particular, the methods used in calculating the power requirements for central offices.  It provides means to calculate the required capacities of the storage batteries and charging equipment for particular applications.

1.2  This bulletin replaces REA TE&CM 302, Power Requirements for Digital Central Office Equipment, Issue No. 6, dated April 1989.  This bulletin provides power calculation methods for various digital, stored program controlled central office equipment.

1.3  General specifications governing storage battery and charging equipment for proposed Central Office Equipment (COE) are covered in Items 12.1 and 12.2, Part III, of Bulletin 1753E-001 (Form 522), "REA General Specification for Digital, Stored Program Controlled Central Office Equipment."  Based on these general specifications, determination of the required capacities of battery and charger is made by the manufacturer.

2.  BASIS FOR CALCULATIONS

2.1  Charging equipment furnished with a central office should have sufficient capacity to supply the dc power necessary for the satisfactory operation of the office during the busy hour.  This includes the dc requirements for carrier, loop extenders, voice frequency repeaters, and dc-dc converters or dc-ac inverters to operate input/output devices.

2.1.1  Determination of the requirements for emergency generating and charging equipment is covered in Bulletin 1751E-320, "Emergency Generating and Charging Equipment."  A suggested method of charger size computation is provided in Figure 8.

2.2  Charging equipment for digital central offices should be provided on one of the following bases:

(a)  Two chargers either of which is capable of carrying the

full office load; or

(b)  Three chargers each of which is capable of carrying

half the office load.

Arrangement (a) may be used in any central office power system.  Arrangement (b) may offer potential cost savings when applied to power requirements in relatively large digital, stored program controlled offices.

2.3  Storage Battery

2.3.1  The storage battery furnished with a central office should have sufficient capacity to supply the dc power necessary to sustain satisfactory operation of the exchange for the period specified.

Specific REA minimum requirements are in 7 CFR 1755.522, which is also contained in Part III of REA Bulletin 1753E-001 (Form 522).  Appropriate allowances should be included for any equipment which is normally ac operated but arranged for dc operation in case of an ac failure.  See paragraph 1.3 of this bulletin for location of specific requirements in central office equipment specifications.

2.3.2  The minimum usable voltage to be delivered to the central office equipment during battery discharge should be determined using COE manufacturer's design criteria.  When power flows from the battery through the power board to the equipment, a voltage drop (IR loss) is experienced as a result of the resistance of the current carrying conductors.  In many cases equipment design is based on 44 volts being available at the power entry to the bay.  Performance of the digital COE at voltages less than 44 volts becomes unpredictable.  For effective design, voltage drop from the source to the equipment bay is considered by allocation as follows:

Battery to Power Board                0.5

Power Board to Equipment Bay          0.5

Minimum Equipment Voltage            44.0

Total                                45V dc - 45.0 Vdc

In the case of a 24-cell battery (45/24) = 1.88 volts per cell becomes the minimum operating voltage.

2.3.3  The computation of battery size to meet the site power requirement is described in Figure 7 - Estimating Telephone Battery Sizes.  This method permits computation with differing numbers of hours of reserve and numbers of cells in the battery string.  The computation is applicable to lead-acid batteries, lead antimony, or lead-calcium batteries (see manufacturer's data for capacity, dimensions, etc.).

2.3.4  REA recommends that the battery provided should have the capacity to maintain the central office load for a period of     8 hours.  Systems that are equipped with emergency generators are allowed to reduce the 8 hours to a 3-hour reserve time.

2.3.5  Determination of battery capacity to be supplied should be based on power outages experienced at the site and on the evaluation of the future performance of the ac power system.  Another consideration is the size of the dc load to be supplied.  Small electromechanical switching systems have a limited amount of fixed power consuming devices, while a large part of system devices only require power when in use.  As a result battery capacity determinations were made assuming busy hour switching activity.  The telecommunications industry considers 8 busy hour battery capacity appropriate for most small installations.  The expectation of 8 consecutive busy hours of usage following a power interruption was negligible, resulting in battery power being usable for longer than the 8-hour period.  Power consumption in digital switching equipment is almost constant, whether or not calls are being processed.  In addition, the total power consumed by digital switches is greater than the electromechanical systems.  The concept of "busy hour drain" has lost its impact in digital offices where the operating drain represents the constant load.  The solution most often used is to provide an emergency generator to supply power on a long-term basis and to install a battery with 3 hours capacity.

3.  CALCULATIONS

3.1  The following sample calculations describe the suggested procedure to determine the power requirements for digital, stored program controlled central office equipment.  Sample calculations are included for the following switching equipment types:

System

Manufacturer                         Designation

Figure 1 - Northern Telecom           DMS-100, DMS-10

Figure 2 - Siemens Stromberg-Carlson  DCO

Figure 3 - Redcom                     MDX

Figure 4 - AT&T                       5 ESS

Figure 5 - Mitel                      GX5000

3.2  Figure 6 lists various power requirements for loop extenders, voice frequency repeaters, carrier equipment and other equipment.

3.3  Figure 7 illustrates the method used in determining the capacity of a storage battery required for a particular application.  This figure also illustrates, in Example 2, a method for calculating the ampere-hour reserve of existing batteries when the current requirement of the central office equipment is changed as a result of equipment additions or higher than anticipated calling rates, etc.

3.4  Figure 8 illustrates the suggested method used in determining charger capacity required for a particular application.  If 110 percent of the rated output of the charger is equal to or greater than the calculated charger dc current requirement, the charger is considered as satisfactorily meeting the specification requirements.  Three suggested solutions in terms of the number of chargers and their capacity are included.

3.5  In some cases specialized equipment requires power at a voltage different from the -48V dc central office battery.  Dc-dc converters can be supplied at +24V dc, +48V dc, +130V dc and other values.  These other voltages are used to supply radio and carrier equipment operated at -24 volts, coin collect circuits at +130 volts and other equipment.  The power required by the dc-dc converters has to be included in the total load to be carried by the central office dc power system.

3.6  It should be kept in mind that the calculation methods shown in this section are to provide estimates only.  Engineering judgment has to be used for each individual application.  It is, therefore, recommended that the manufacturer of the system be consulted for specific applications.

Figure 1  NORTHERN TELECOM DMS-100

DC DRAIN

1.  Basic (CPU)                                                       78.5

CC Frame E/W 4 Memory Shelves

I/O Frame E/W 2 Disk + 1 Mag Tape

2.  PDC Bays         x 6.5 Amps                                      _____

3.  LAMA or CAMA (10 Amps)                                           _____

4.  Combined Network Frame         x 24 Amps                         _____

5.  Double Shelf Network         x 14 Amps                           _____

6.  DTC         x 8.5 Amps                                           _____

7.  MTM          x 3.3 Amps                                          _____

8.  TM         x 2.2 Amps                                            _____

9.  LGC         x 8.5 Amps                                           _____

10. Line Circuits LCE _______ x 8.2 + 4W (Note 1)                    _____

Subtotal   _____

Customer Drain _______                                               _____

DMS Current Total _______                                            _____

Note 1:  W = 2 way CCS per line in unit drain formula

Figure 1.1  NORTHERN TELECOM DMS-100

E X A M P L E

1000 Lines, 50 Digital Trunks, 50 Analog Trunks, 3.2 CCS/Line

DC DRAIN

1.  Basic (CPU)                                                      78.5

CC Frame E/W 4 Memory Shelves

I/O Frame E/W 2 disk + 1 Mag Tape Drive

2.  PDC Bays 1 x 6.5 Amps                                             6.5

3.  LAMA or CAMA, 10 Amps                                           _____

4.  Combined Network Frame  1 x 24 Amps                              24.0

5.  Double Shelf Network      x 14 Amps                             _____

6.  DTC  1  x 8.5 Amps                                                8.5

7.  MTM  4  x 3.3 Amps                                               13.2

8.  TM  1  x 2.2 Amps                                                 2.2

9.  LGC  1  x 8.5 Amps                                                8.5

10.   Line Circuits   LCE    1    x 8.2 + 4W (Note 1)                21.0

(Sample = 1 x 8.2 + 4 x 3.2 = 21)

Subtotal        162.4

Customer Drain  20                                                   20.0

DMS Current Total                                                   182.4

NOTE 1:  W = 2 way CCS per line in unit drain formula

Figure 1.2  NORTHERN TELECOM DMS-100

HEAT DISSIPATION

Heat

Dissipation

Per Frame      Total Heat

Type of Frame           Quantity       (Watts/Hr)     Dissipation

Central Control Complex                        1720        ___________

Input/Output Frame                              850        ___________

Miscellaneous Equipment                         220        ___________

Network Combined                               1000        ___________

Digital Trunk Equipment                        1120        ___________

Trunk Module Equipment

Frame                                           480        ___________

Line Concentrating

Equipment                                      1050        ___________

Line Group Equipment                            980        ___________

Power Distribution Center                       200        ___________

TOTAL WATTS/HOUR ___________

Figure 1.3  NORTHERN TELECOM DMS-100

E X A M P L E

1400 Lines, 50 Digital Trunks, 50 Analog Trunks, 3.2 CCS/L

HEAT DISSIPATION

Heat

Dissipation

Per Frame      Total Heat

Type of Frame           Quantity       (Watts/Hr)     Dissipation

Central Control Complex         1              1720              1720

Input/Output Frame              1               850               850

Miscellaneous Equipment         1               220               220

Network Combined                1              1000              1000

Digital Trunk Equipment         1              1120              1120

Trunk Module Equipment

Frame                           2               480               960

Line Concentrating

Equipment                       1              1050              1050

Line Group Equipment            1               980               980

Power Distribution Center       1               200               200

TOTAL WATTS/HOUR       8100

Figure 1.4  NORTHERN TELECOM STANDARD DMS-10 400 SERIES

DC DRAIN

Basic System                                                       25.0 Amps

DCM Shelves        x  4.0   =                                           Amps

DCI Shelf          x  3.0   =                                           Amps

SCM-10S            x 10.0   =                                           Amps

P.E. Shelf         x  0.75  =                                           Amps

LCE Lines          x  0.015 =                                           Amps

BMC                x  5.0   =                                           Amps

D.C./A.C. Inverter (0.5 KW)________ x 15 =                              Amps

Total =                                       Amps

Heat Dissipation

D.C. Drain

Northern Telecom DMS-10 400 Generic (3 Bay)

Basic System                                                      30.0 Amps

P.E. Shelf         x  0.75  =                                          Amps

DCM Shelf          x  4.0   =                                          Amps

LCE Lines          x  0.015 =                                          Amps

Total =                                      Amps

Heat Dissipation

D.C. Drain         x 52                                                Watts

Figure 1.5  NORTHERN TELECOM STANDARD DMS-10 400 SERIES

Example #1

5000 Lines, 576 Trunks, 1 RLCM, 1 SLC-96, 1 RSLE, 1  RSLM

@ 3.2 CCS/line

DC Drain

Basic System                                             25.0  Amps

DCM Shelves             4   x   4.0   =                  16.0  Amps

DCI Shelf               1   x   3.0   =                   3.0  Amps

SCM-10S                 1   x  10.0   =                  10.0  Amps

P.E. Shelf              2   x   0.75  =                   1.5  Amps

LCE Lines            5000   x   0.015 =                  75.0  Amps

BMC                     2   x   5.0   =                  10.0  Amps

D.C./A.C. Inverter (0.5 KW)     1    x 15.0 =            15.0  Amps

Total =                        155.5  Amps

Heat Dissipation

DC Drain              155.5  x   52   =                  8086  Watts

Example #2

Northern Telecom DMS-10 400 Generic (3 Bay)

1280 Lines, 144 Trunks, @ 3.2 CCS

Basic System                                             30.0  Amps

P.E. Shelf              2   x  0.75   =                   1.5  Amps

DCM Shelf               1   x  4.0    =                   4.0  Amps

LCE Lines             1280  x  0.015  =                  19.2  Amps

Total =                      54.7  Amps

Heat Dissipation

D.C. Drain             54.7 x  52    =                   2844  Watts

Figure 1.6  NORTHERN TELECOM STANDARD DMS-10 400 SERIES

(Page 1 of 2)

1 - Standard 400 Series	AMPS

Basic System Current Drain	25.0

Network Module (Max. = 2 Modules)	12.0

DCM Shelf	 4.0

DCI Shelf	 3.0

SCM-10 (DMS-1) Shelf	 4.0

SCM-10S (SLC-96) Module	10.0

Mag Tape Bay	 7.8

BMC (each)	 5.0

DC/AC Inverter 0.5 KW	15.0

DC/AC Inverter 1.0 KW	26.0

P.E. Lines	 0.020

P.E. Shelf (with service circuits)	 0.75

LCM Lines (per line)	 0.015

2 - DMS-10 400 Series (3 bay)	AMPS

Basic System Current Drain	30.0

(includes combination CPU/Network

shelf and GPIO shelf)

3 - DMS-10 400 series (2 bay)	AMPS

CONTROL AND TRUNK BAY

CPU/Network Shelf (5.8 amps ea. two required)	11.6

GPIO Shelf	 4.8

T & M Shelf	 2.9

PCCM Shelf	 1.5

DAT Shelf	 2.9

LINE AND TRUNK BAY

Two Shelf LCM (E/W 640 Lines)	 9.6

Bay Supervisory Panel	 0.2

DAT Shelf each (max. = 2 shelves)	 2.9

4 - DMS-10 400 Series (1 bay)	AMPS

CPU/Network Shelf (5.8 amps ea. two required)	11.6

T & M Shelf	 2.9

PCCM Shelf	 1.5

DAT Shelf	 2.9

FSP (Frame Supervisory Panel) and

LCM Shelf (E/W 256 lines)	 4.8

Figure 1.6  NORTHERN TELECOM STANDARD DMS-10 400 SERIES

(Page 2 of 2)

5 - OPM                                                            AMPS

One Cabinet                                                   15.0

Line Current                                                   0.015/L

6 - OPSM                                                           AMPS

One Cabinet                                                    9.0

Line Current                                                   0.015/L

7 - RSLM                                                           AMPS

RSLM Bay                                                       6.0

Line Current                                                   0.015/L

8 - RSLE                                                           AMPS

RSLE Bay (up to 512 lines)                                    10.5

RSLE Bay (from 512 to 1024 lines)                             21.0

Line Current                                                   0.015/L

9 - RLCM                                                           AMPS

RLCM Bay                                                      10.0

LCE Bay                                                        0.015/L

Figure 2  SIEMENS STROMBERG - CARLSON DCO-E/DCO-SE

(Page 1 of 3)

DC DRAIN

1.  CONTROL & MAINTENACE FRAME (CMF)                                  WATTS

DCO-E CMF (ONE PER DCO-E)       1    X 2400                      =_____

DCO-SE CMF (ONE PER DCO-SE)     1    X 2000                      =_____

2.  LOCAL LINE SWITCH FRAME (LLS) (DCO-E & DCO-SE)

Quantity of Lines ________ x ____CCS/L X   0.069 (LOAD)          =_____

Quantity of Lines                _____ X   0.158 (IDLE)          =_____

Quantity Of Line CUAs            _____ X  30.0                   =_____

Quantity of RLG Host CUAs        _____ X  31.0                   =_____

Quantity of SLC Host CUAs        _____ X 158.0                   =_____

Quantity of LLS Frames           _____ X 306.0                   =_____

TOTAL LLS FRAME POWER REQUIREMENTS                               =_____

3.  LINE/TRUNK FRAME POWER (LTF) (DCO-E ONLY)                         WATTS

Quantity of DTMF Receiver PWBAs        _____ X 19.3             =_____

Quantity of DTMF Sender PWBAs          _____ X  5.0             =_____

Quantity of TMF Receiver PWBAs         _____ X  8.5             =_____

Quantity of TMF Sender PWBAs           _____ X  3.9             =_____

Quantity of Busy Verification PWBAs    _____ X  2.3             =_____

Quantity of Analog Trunk PWBAs         _____ X  8.2             =_____

Quantity of LTF CUAs                   _____ X 19.3             =_____

TOTAL LTF POWER REQUIREMENTS                                    =_____

4.  DIGITAL TRUNK FRAME POWER (DTF) (DCO-E ONLY)                     WATTS

Quantity of T1 Interface PWBAs         _____ X 11.2             =_____

Quantity of Message Assemblers         _____ X 57.3             =_____

Quantity of DTF CUAs                           67.4             =_____

TOTAL DTF POWER (WATTS)                                         =_____

5.  POWER RINGING & TEST FRAME POWER (PRTF) (DCO-E ONLY)             WATTS

Power Ringing & Test Frame               1   X 92.0             = 92.0

TOTAL PRTF POWER REQUIREMENTS                                   = 92.0

Figure 2  SIEMENS STROMBERG-CARLSON DCO-E/DCO-SE

(Page 2 of 3)

DC DRAIN

6.  DATA COLLECTION FRAME POWER (AMAF)/(DCF) (DCO-E & DCO-SE)        WATTS

AMA Frame (E/W Tape  Drives)     _____ x 495.0                  =_____

CODC Data Collection Frame       _____ X 523.0                  =_____

TOTAL AMAF/DCF POWER REQUIREMENTS                               =_____

7.  COMMON EQUIPMENT FRAME POWER (CEF) (DCO-E) & DCO-SE)             WATTS

Variable (Dependent on OEM Equipment Installed)

TOTAL CEF POWER REQUIREMENTS                                    =_____

8.  UNIVERSAL POWER FRAME (DCO-SE ONLY)                              WATTS

Universal Power Frame (UPF)                    1   X  92.0      = 92.0

Expanded Ringing CUA                         _____ X  70.0      =_____

*Universal Service CUA                       _____ X 155.0      =_____

*Universal Trunk/Service CUA                 _____ X 155.0      =_____

*Universal Trunk CUA                         _____ X 132.0      =_____

*Customber Trunk Group CUA                   _____ X 107.0      =_____

Quantity of DTMF Receiver PWBAs              _____ X  19.3      =_____

Quantity of DTMF Sender PWBAs                _____ X   5.0      =_____

Quantity of TMF Receiver PWBAs               _____ X   8.5      =_____

Quantity of TMF Sender PWBAs                 _____ X   3.9      =_____

Quantity of Busy/Verification PWBAs          _____ X   2.3      =_____

Quantity of Analog Trunk PWBAs               _____ X   8.2      =_____

TOTAL UPF POWER REQUIREMENTS                                    =_____

9.  REMOTE LINE SWITCH POWER (RLS)                                  WATTS

RLS Frame (1080 Lines Maximum)     1   X 906.0                 =906.0

Quantity of Lines  _____ X _____ CCS/L X   0.069 (LOAD)        =_____

Quantity of Lines                _____ X   0.158 (IDLE)        =_____

Quantity of Line CUAs            _____ X  30.0                 =_____

Quantity of RLG CUAs             _____ X  31.0                 =_____

Quantity of SLC CUAs             _____ X 158.0                 =_____

TOTAL RLS FRAME POWER REQUIREMENTS                             =_____

*ONLY 3 CUAs TOTAL CAN BE EQUIPPED

Figure 2  STROMBERG-CARLSON DCO-E/DCO-SE

(Page 3 of 3)

DC DRAIN

10.  REMOTE LINE SWITCH - 450 POWER (DC)                             WATTS

Basic DC Power (Maximum)                                        = 1200

Maximum Allowed Customer Power                                  =  250

RLS-450 DC POWER TOTAL WATTS (Maximum)                          = 1450

RLS-450 RATED AC POWER INPUT (Typical)                          = 6000

(Based on cold weather heating plus maximum short term load.)

SYSTEM DC POWER SUMMARY

11.  DCO-E SYSTEM POWER                                             WATTS

Total Control & Maintenance Frame Power                        = 2400

Total Local Line Switch Power                                  =_____

Total Line/Trunk Frame Power                                   =_____

Total Digital Trunk Frame Power                                =_____

Total Power Ringing & Test Frame Power                         = 92.0

Total AMA/Data Collection Frame Power                          =_____

Total Common Equipment Frame Power                             =_____

TOTAL DCO-E SYSTEM DC POWER REQUIREMENTS                           =_____ AMPS

TOTAL DCO-E DC BUSY HOUR LOAD (Total DC Power divided by

52.1 Volts)                                                      =_____

12.  DCO-SE SYSTEM POWER                                            WATTS

Total Control & Maintenance Frame Power                        = 2000

Total Local Line Switch Frame Power                            =_____

Total AMA/Data Collection Frame Power                          =_____

Total Universal Power Frame Power                              =_____

Total Common Equipment Frame Power                             =_____

TOTAL DCO-SE SYSTEM DC POWER REQUIREMENTS                      =_____

TOTAL DCO-SE DC BUSY HOUR LOAD                                =_____ AMPS

(Total DC Power divided by 52.1 Volts)

Figure 2.1  SIEMENS STROMBERG-CARLSON DCO-E/DCO-SE

(Page 1 of 3)

Example

1000 LINES AT 3.2 CCS

1.  CONTROL & MAINTENANCE FRAME POWER (CMF)                           WATTS

DCO-E                                     1  X 2400             = 2400

DCO-SE                                    1  X 2000             = 2000

2.  LOCAL LINE SWITCH FRAME (LLS) (DCO-E & DCO-SE)                    WATTS

Quantity of Lines      1000 X   3.2 CCS/L X 0.069 (LOAD)          220.8

Quantity of Lines                       1000 X    0.158 (IDLE)  = 158.0

Quantity of Line CUAs                    12  X   30.0           = 360.0

Quantity of RLG Host CUAs                 0  X   31.0           =   0

Quantity of SLC Host CUAs                 0  X  158.0           =   0

Quantity of LLS Host CUAs                 1  X  306.0           = 306.0

TOTAL LLS FRAME(S) POWER (WATTS)                                =1044.8

3.  LINE/TRUNK FRAME POWER (LTF) (DCO-E ONLY)

Quantity of DTMF Receiver PWBAs           2  X 19.3             =  38.6

Quantity of DTMF Sender PWBAs             2  X  5.0             =  10.0

Quantity of TMF Receiver PWBAs            2  X  8.5             =  17.0

Quantity of TMF Sender PWBAs              2  X  3.9             =   7.8

Quantity of Busy Verification PWBAs       2  X  2.3             =   4.6

Quantity of Analog Trunk PWBAs            0  X  8.2             =     0

Quantity of LTF CUAs                      2  X 19.3             =  38.6

TOTAL LTF POWER (WATTS)                                         = 116.6

4.  DIGITAL TRUNK FRAME POWER (DTF) (DCO-E ONLY)

Quantity of T1 Interface PWBAs            5  X 11.2             =  56.0

Quantity of Message Assemblers            0  X 57.3             =   0

Quantity of DTF CUAs                      1  X 67.4             =  67.4

TOTAL DTF POWER (WATTS)                                         = 123.4

5.  POWER RINGING & TEST FRAME POWER (PRTF) (DCO-E ONLY)

Power Ringing & Test Frame                1  X 92.0             =  92.0

TOTAL PRTF POWER (WATTS)                                        =  92.0

Figure 2.1  SIEMENS STROMBERG-CARLSON DCO-E/DCO-SE

(Page 2 of 3)

Example

6.  AMAF/DATA COLLECTION FRAME (AMAF/CODC) (DCO-E & DCO-SE)           WATTS

AMA Frame                        _____ X 495.0                   =_____

CODC Data Collection Frame       _____ X 523.0                   =_____

TOTAL AMAF/DCF POWER (WATTS)                                     =    0

7.  COMMON EQUIPMENT FRAME POWER (CEF) (DCO-E) & DCO-SE)

Variable (Dependent on OEM Equipment Installed)

TOTAL CEF POWER (WATTS)                                          =    0

8.  UNIVERSAL POWER FRAME (DCO-SE ONLY)                               WATTS

Universal Power Frame (UPF)                   1   X  92.0        =  92.0

Expanded Ringing CUA                              X  70.0        =______

*Universal Service CUA                            X 155.0        =______

*Universal Trunk/Service CUA                  1   X 155.0        = 155.0

*Universal Trunk CUA                          1   X 132.0        = 132.0

*Customber Trunk Group CUA                    1   X 107.0        = 107.0

Quantity of DTMF Receiver PWBAs               2   X  19.3        =  38.6

Quantity of DTMF Sender PWBAs                 2   X   5.0        =  10.0

Quantity of TMF Receiver PWBAs                2   X   8.5        =  17.0

Quantity of TMF Sender PWBAs                  2   X   3.9        =   7.8

Quantity of Busy/Verification PWBAs           2   X   2.3        =   4.6

Quantity of Analog Trunk PWBAs                0   X   8.2        =     0

TOTAL UPF POWER (WATTS)                                          = 564.0

9.  REMOTE LINE SWITCH POWER (RLS)

RLS Frame (1080 Lines Maximum)     1   X 906.0                   = 906.0

Quantity of Lines     1000 x 3.2  CCS/L X  0.069                 = 220.8

Quantity of Lines                 1000 X   0.158                 = 158.0

Quantity of Line CUAs               12 X  30.0                   = 360.0

Quantity of RLG CUAs             _____ X  31.0                   =______

Quantity of SLC CUAs             _____ X 158.0                   =______

TOTAL RLS FRAME POWER (WATTS)                                    =1644.8

*ONLY 3 CUAs TOTAL CAN BE EQUIPPED

Figure 2.1  SIEMENS STROMBERG-CARLSON DCO-E/DCO-SE

(Page 3 of 3)

Example

10.  REMOTE LINE SWITCH - 450 POWER (DC)                           WATTS

TYPICAL Basic RLS-450 (Maximum)                            = 1200

CUSTUMBER POWER (250W Maximum)                             =    0

TOTAL RLS-450 DC POWER TOTAL WATTS (Maximum)                      = 1200

RLS-450 Rated Ac Power Input (Typical)                            = 6000

(Based on typical cold weather heating plus maximum short term  system load.)

11.  SYSTEM DC POWER SUMMARY

1.  DCO-E SYSTEM POWER

Total Common Control Frame Power                              =2400.0

Total Local Line Switch Power                                 =1044.8

Total Line/Trunk Frame Power                                  = 116.6

Total Digital Trunk Frame Power                               = 123.4

Total Power Ringing & Test Frame Power                        =  92.0

Total AMA/Data Collection Frame Power                         =     0

Total Common Equipment Frame Power                            =     0

TOTAL DCO-E SYSTEM DC POWER REQUIREMENTS                          =3776.8

TOTAL DCO-E DC BUSY HOUR LOAD (TOTAL WATTS/52.1 VOLTS)            =  72.5 AMPS

12.  DCO-SE SYSTEM POWER

Total Control & Maintenance Frame Power                       =2000.0

Total Local Line Switch Frame Power                           =1044.8

Total AMA/Data Collection Frame Power                         =     0

Total Universal Power Frame Power                             = 564.0

Total Common Equipment Frame Power                            =     0

TOTAL DCO-SE SYSTEM DC POWER REQUIREMENTS                         =3608.8

TOTAL DCO-SE DC BUSY HOUR LOAD (TOTAL WATTS/52.1 Volts)           =  69.3 AMPS

FIGURE 3  REDCOM MDX

DC DRAIN

Quantity     Multiply By       Amps

MSU Shelves (One per 40 Lines)      __________        3.5         _______

HEAT DISSIPATION

Heat Dissipation (Watts) = 52.1 x DC Drain       ________ = _______ Watts

E X A M P L E

150 Lines

DC DRAIN

Quantity     Multiply By       Amps

MSU Shelves (One per 40 Lines)           4             3.5            14

HEAT DISSIPATION

Heat Dissipation (Watts) = 52.1 x DC Drain          14    =   730   Watts

FIGURE 4 AT&T 5ESS  SWITCH

(Page 1 of 2)

DC DRAIN

1.  Basic (AM and CM)                                                 55.76

2.  No. of Disk Drive Units                      _____ x 1.30 Amps  _______

3.  No. of Switching Modules w 32Mb Memory       _____ x 9.94 Amps  _______

4.  No. of MMSUs                                 _____ x 0.20 Amps  _______

5.  No. of LUs                                   _____ x 5.60 Amps  _______

6.  No. of TUs                                   _____ x 0.18 Amps  _______

7.  No. of DCTUs                                 _____ x 2.00 Amps  _______

8.  No. of GDSUs                                 _____ x 0.61 Amps  _______

9.  No. of DLTUs                                 _____ x 0.02 Amps  _______

10.  No. of DLTU Packs                            _____ x 0.12 Amps  _______

SUBTOTAL                                                        _______

Additional Drains                                               _______

TOTAL DC Drain                                                  _______

FIGURE 4 AT&T 5ESS  SWITCH

(Page 2 of 2)

HEAT DISSIPATION

Heat

Dissipation

Per Frame           Total Heat

Type of Frame         Quantity            (BTUs)           Dissipation

Basic (AM and CM)          ________           9931.42             ______

No. of Disk Drives         ________            231.54             ______

No. of Switching Modules   ________           1770.41             ______

No. of MMSUs               ________             36.27             ______

No. of LUs                 ________            997.42             ______

No. of TUs                 ________             32.95             ______

No. of DCTUs               ________            356.22             ______

No of GDSUs                ________            108.05             ______

No. of DLTUs               ________            174.55             ______

TOTAL BTUs                                                        ______

FIGURE 4.1 AT&T 5 ESS  SWITCH

(Page 1 of 2)

EXAMPLE

1 SM Office with 1000 Analog Lines,

12 Analog Trunks, and 192 Digital Trunk Circuits.

DC DRAIN

1.  Basic (AM and CM)                                                 55.76

2.  No. of Disk Drive Units                        4   x 1.30 Amps     5.20

3.  No. of Switching Modules w 32Mb Memory         1   x 9.94 Amps     9.94

4.  No. of MMSUs                                  11   x 0.20 Amps     2.20

5.  No. of LUs                                     3   x 5.60 Amps    16.80

6.  No. of TUs                                     4   x 0.18 Amps     0.72

7.  No. of DCTUs                                   1   x 2.00 Amps     2.00

8.  No. of GDSUs                                   3   x 0.61 Amps     1.83

9.  No. of DLTUs                                   1   x 0.02 Amps     0.02

10.  No. of DLTU Packs                              8   x 0.12 Amps     0.96

SUBTOTAL                                                          95.43

Additional Drains                                               _______

TOTAL DC Drain                                                    95.43

FIGURE 4.1 AT&T 5ESS  SWITCH

(Page 2 of 2)

EXAMPLE

1 SM Office with 1000 Analog Lines,

12 Analog Trunks, and 192 Digital Trunk Circuits

HEAT DISSIPATION

Heat

Dissipation

Per Frame          Total Heat

Type of Frame         Quantity             (BTUs)           Dissipation

Basic (AM and CM)                1             9931.42              9931.42

No. of Disk Drives               4              231.54               926.16

No. of Switching Modules         1             1770.41              1770.41

No. of MMSUs                    11               36.27               398.97

No. of LUs                       3              997.42              2992.26

No. of TUs                       4               32.95               131.80

No. of DCTUs                     1              356.22               356.22

No of GDSUs                      3              108.05               324.15

No. of DLTUs                     1              174.55               174.55

TOTAL BTUs                                                         17005.94

FIGURE 5  MITEL GX5000

D.C. DRAIN

EQUIPMENT                   QUANTITY     MULTIPLY BY     WATTS

First peripheral pair and Main

control (includes all features,

AMA, matrix and first cabinet)           1            460          460

Additional peripheral pair                             96          ___

Additional cabinet                                    105          ___

Single Party line card (16 ckts)                       10          ___

DS1 trunk card (2 spans)                               29          ___

Universal line card (6 ckts)                            9          ___

Total D.C. Drain                                                       Watts

Converted to AMPS (Watts/Battery Voltage) = Watts/52 = ____ Amps

Heat dissipation = _____ Watts or (3.41 X ____Watts) = ____ BTU

FIGURE 5.1  MITEL GX5000

Example System:  1008 lines, 96 Digital Trunks

D.C. DRAIN

EQUIPMENT                         QUANTITY   MULTIPLY BY   WATTS

First peripheral pair and Main

control (includes all features,

AMA, matrix and first cabinet)                 1          460        460

Additional peripheral pair                     2           96        192

Additional cabinet                             1          105        105

Single Party line card (16 ckts)               63          10        630

DSI trunk card (2 spans)                       2           29         58

Universal line card (6 ckts)                   0            9          0

Total D.C. Drain                                                   1,445 Watts

Converted to AMPS (Watts/Battery Voltage) = 1,445 Watts/52 = 27.7 Amps

Heat dissipation = 1,445 Watts or (3.41 X 1,445 Watts) = 4927 BTU

Figure 6  TRANSMISSION ELECTRONICS CURRENT DRAIN

48-Volt Battery Drain

Amperes Per Unit

Equipment

Loop Extenders                                               0.075

VF Repeaters

1.  Negative Impedance                                       0.035

2.  Hybrid                                                   0.035

3.  Automatic Gain Control                                   0.080

4.  Loop Extender/Repeater Combination                       0.100

5.  Automatic Gain Control

Loop Extender/Repeater Combination                     0.200

Carrier Systems

1.  D1 or D2                                                 3.0

2.  D3 (24 Channel)                                          0.7

3.  D4 (24 Channel)                                          0.35

4.  T1 Span Line                                             0.6

5.  Station Carrier (1 Channel)                              0.04

6.  Station Carrier (Multi-Channel) Per Channel              0.1

7.  Pair Gain Devices (Switching)

(See Notes 1 & 2 for Office End)

Echo Canceller

1.  VF (1 Channel)                                           0.075

2.  Digital (24 Channel)                                     1.7

Remote Office Line Test

1.  Test Console (110V ac, 0.4A)                             0.7

2.  Remote Terminal                                          0.7

120V, 60Hz Load

Maintenance and Control Center                     Amperes Per Unit (Note 3)

Co-located with COE:

Video Display (CRT)                                        0.5

Printer (1200 Baud)                                        0.5

Remotely Located:

Teletypwriter (e/w 300 Baud Modem)                         0.35

NOTES:

1.  Refer to the manufacturer's data sheets for specific current drain

requirements.

2.  Line concentrators or other pair gain devices incorporating switching

functions are generally locally powered at remote site.

3.  Voltage:  95 to 128V ac   -   Frequency:  48 to 65Hz

Figure 7  ESTIMATING TELEPHONE BATTERY SIZES

8-Hour Ampere Hour Capacity Required

for Each Ampere of Load

Number of Hours                               Final Cell Voltages

Reserve                         1.75   1.80   1.85   1.88   1.90   1.95

1                           2.2    2.5    2.8    3.2    3.5    5.0

2                           3.2    3.4    3.7    4.3    4.7    6.2

3                           4.0    4.3    4.7    5.2    5.6    7.5

4                           4.9    5.1    5.6    6.1    6.5    8.6

5                           5.7    6.0    6.5    7.0    7.4    9.6

6                           6.5    6.8    7.3    7.8    8.2   10.6

7                           7.2    7.6    8.1    8.7    9.1   11.6

8                           8.0    8.3    8.9    9.6   10.0   12.6

9                           8.8    9.1    9.6   10.4   10.9   13.7

10                           9.5    9.9   10.4   11.4   12.0   15.0

Voltage (24 Cells)                 42     43.2   44.4   45.1   45.6   46.8

EXAMPLES:

1.  Required:  The capacity of a 24-cell battery to handle a 3-hour load of 34.0 amperes to a limited voltage of 45 volts.

45/24 = 1.88

From the above chart, each ampere of load requires 5.2 ampere hours of capacity.

Total capacity required = 5.2 x 34.0 = 177 ampere hours.  Select next larger catalog size.

2.  Calculate the ampere hour reserve of an existing 24-cell, 480-ampere hour battery with the load increased to 69 amperes to a final voltage of 1.88 volts.

Formula:  K = B/C

Where

K = 8-hour ampere hour capacity required for

each ampere of load.

B = Ampere hour capacity of existing battery.

C = Actual current drain of all equipment.

K = 480/69 = 7.0

On the chart, locate 7.0 in the 1.88-volt column

and to the left read 5 hours of reserve.

FIGURE 8  CHARGER CAPACITY

The battery charger has to supply power for operation of the COE.  Its capacity should be great enough to carry the entire load, including peak power requirements, to avoid taking power from the battery.  Additional capacity is required to recharge the battery after a power service interruption.

EXAMPLE:

Drain                                                       66 Amps

Battery Discharged for 3 Hours and Recharged

in 12 Hours:  3 x 66 / 12 =                               16.5 Amps

Calculated Charger DC Current Requirement                   82.5 Amps

Rated Charger Capacity (as indicated in

Paragraph 3.4)                                            75 Amps

The charger capacity sizes commercially available include:

2 @ 75 Amps	-	Traditional arrangement with

load sharing between the two

chargers.

3 @ 50 Amps	-	Potential cost saving over

buying two larger units.

Potential operating cost

saving by operating only

two units.