This page intentionally left blank

UNITED STATES DEPARTMENT OF AGRICULTURE

Rural Utilities Service

BULLETIN 1753F-152

SUBJECT:	Specifications and Drawings for Construction of

Aerial Plant, RUS Form 515c

TO:  All Telecommunications Borrowers

RUS Telecommunications Staff

EFFECTIVE DATE:  September 17, 2001

OFFICE OF PRIMARY INTEREST:  Outside Plant Branch, Telecommunications Standards Division.

AVAILABILITY:  This bulletin supersedes RUS Bulletin 345-153, Specifications and Drawings for Construction of Pole Lines, Aerial Cables and Wires, RUS Form 515f, issued May 25, 1989.

This bulletin can be accessed via the Internet  at http://www.usda.gov/rus/telecom/publications/bulletins.htm

PURPOSE:  This specification provides Contractors, Engineers, and RUS Borrowers with assembly unit descriptions, materials, construction and installation, and drawings for aerial plant associated with RUS Form 515, Telecommunications System Construction Contract.

Roberta D. Purcell	8/21/01

### Roberta D. Purcell	Date

Assistant Administrator

Telecommunications Program

RUS Bulletin 1753F-152

Specifications and Drawings for Construction of

Aerial Plant, RUS Form 515c

TABLE OF CONTENTS

# Page

List of Changes	i

Part I – Description of Assembly Units and Proposal and

Contract Sections	1

Part II – Specifications and Materials	14

1.	Scope	14

2.	General	14

3.	Poles	14

4.	Miscellaneous	14

Part III – Specifications for Construction and Installation	14

1.	General	14

2.	Pole Lines	15

3.	Mounting Hardware and Guys	17

4.	Anchors	17

5.	Self Supporting Fiber Optic Cable	18

6.	Suspension Strand	19

7.	Filled Aerial Cable	20

8.	Filled Aerial Cable Placement	20

9.	Cable Splicing and Terminals	22

10.	Clearing Right-of-Way	23

List of Construction Drawings and Plans	24

INDEX

### ASSEMBLY UNITS:

Cable Plant, Aerial

CABLE:

Aerial Cable Plant Construction

Assembly Units

### CONSTRUCTION:

Aerial Cable Plant

Fiber Optic Cable Plant

### POLES LINES:

Design of

POLES:

Numbering

RIGHT-OF-WAY:

Clearing and Trimming Assembly Units

### SPECIFICATIONS AND STANDARDS:

Outside Plant

WIRE:

Seven Wire Aluminum Clad Steel Strand

Steel, 7 Wire Galvanized Strand

LIST OF CHANGES

1.	Modification of Pole Units from Section 1 to Section A.

2.	Elimination of Section C and Section CF.

3.	Addition of Section CFO, Self Supporting Filled Fiber Optic Cable Assembly Units.

4.	Modification of CO and CW units as follows:

(a)	Provide for compensation on a per foot basis;

(b)  Redefined compensation to include the sum of the cable distances between supporting structures as indicated by the sequential foot markings;

(c)	Specified utility grade galvanized steel strand as the default type.

5.	Elimination of suffixes "N" and "R" under Section HA.  For ready access splice closures specified under the "R" suffix, a new unit designated HR was created.

6.	Addition of Section HR, Ready Access Splice Closure Assembly Unit.

7.	Modification of Section HC as follows:

(a)	Redefined unit to provide compensation on a single pair basis;

(b)	Created HC5 unit in order to provide compensation for terminating cable pairs on a terminal block within a ready access closure.

8.	Modification of Section HO to provide compensation for testing a fiber.

9.	Elimination of section PC and section PDS.

10.	Modification of Section PE to indicate utility grade galvanized steel as the default type.

11.  Elimination of Section PG.  The terminal blocks are now included under Section PM.

12.	Modification of PM21 and PM22 to provide for a more generalized description.

13.	Addition of PM25, Filled Terminal Block Assembly Unit.

14.  Modification of Section R to provide compensation on a per foot basis.

15.	In part III, section 2, elimination of information on pole facing.

16.  In part III, the Figure 8 cable was changed to describe Self Supporting Fiber Optic Cable.

17.  In part III, eliminated references to load coils, pressurized cable, and air-core cable.

For editorial or other minor technical changes, refer to the body of the document.

Part I - DESCRIPTION OF ASSEMBLY AND PROPOSAL AND

CONTRACT SECTIONS

The Contractor’s Proposal form is divided into sections and the sections approved for construction shall be listed in the Construction Agreement by the Owner.  The sections are as follows:

Section A		- 	Pole Units

Section CFO	-	Self Supporting Filled Fiber Optic Cable

Assembly Units

Section CO	-	Aerial Filled Fiber Optic Cable Assembly 					Units

Section CW	-	Aerial Filled Copper Cable Assembly

Units

# Section HA	-	Aerial Splice Closure Assembly Units

Section HC	-	Copper Splicing Assembly Units

# Section HO	-	Fiber Optic Splicing Assembly Units

Section HR	-	Ready Access Closure Assembly Units

Section PE	-	Guy Assembly Units

Section PF	-	Anchor Assembly Units

Section PM	-	Miscellaneous Assembly Units

Section R		-	Right-of-Way Clearing and Trimming Units

# Section W		-	Rearrangement Units

Section XX	-	Nonreusable Materials Removal Units

Section XZ	-	Reusable Materials Removal Units

Each assembly unit includes only the materials listed on the corresponding Installation and Construction Guide Drawings or description of unit where no drawing exists.  The various installation and construction units, which are included in this Proposal and upon which quotations are required, are defined by the following descriptions:

Section A - POLE UNITS

Consists of one (1) pole in place.  It does not include the pole top assembly units or other parts attached to the pole.  Poles shall be of the height and class as designated by the Engineer.  The pole plan, species of timber, kind of preservative and method of treatment are designated in the Proposal.

Example:

A35-7	A 35 foot [10.7 meters (m)] class 7 pole.

Section CFO – SELF SUPPORTING FILLED FIBER OPTIC CABLE

ASSEMBLY UNITS

Consists of one (1) foot (0.305 m) of self supporting filled fiber optic cable in place including all supporting hardware, cable guards, insulating tapes, and bonding of the armor (when present) and supporting member in accordance with the Construction Sheets.

A.	The length of the self supporting cable measured for compensation purposes includes the sum of the cable distances between supporting structures as indicated by the sequential foot markings.

B.	This unit does not include labor and material for fiber splicing, splice closures, housings, or organizers.  The labor and material for these items are provided for in other units.

C.	This unit includes the spiraling of the self supporting cable in accordance with the method shown in the Construction Sheets.

Each self supporting filled fiber optic cable unit is listed in accordance with the number of optical fibers.  Each unit is prefixed by the letters CFO.  The following illustration indicates the method of designating the material required.

CFO16			A self supporting filled fiber optic

cable with 16 fibers.

Section CO - AERIAL FILLED FIBER OPTIC CABLE ASSEMBLY UNITS

Consists of one (1) foot (0.305 m) of aerial filled fiber optic cable in place including supporting messenger of galvanized steel strand, lashing wire, attachments to strand, bonding of the armor (when present) and strand in accordance with the Construction Sheets.

Options designated by the following suffixes apply:

Suffix		Description

A			Aluminum-clad steel strand.

C			Class C galvanized steel utility grade strand for

corrosion areas.

D			Two or more cables are to be initially lashed to

the same suspension strand.

E			Cables are lashed to existing strand and cable(s).

A.	The length of aerial cable measured for compensation purposes includes the sum of the cable distances between supporting structures as indicated by the sequential foot markings.

B.	This unit does not include labor and material for fiber splicing, splice closures, housings or organizers.  The labor and material for these items are provided for in other units.

C.	Class A galvanized steel utility grade strand shall be provided unless another type is specified by the appropriate suffix.

Each aerial filled fiber optic cable assembly unit is listed in accordance with the number of optical fibers.  Each unit is prefixed by the letters CO.  The following illustrations indicate the method of designating the material required.

CO16(6M)		An aerial filled fiber optic cable with 16 fibers,

supported by 6000 pound (lbs) [26,688 Newtons (N)]

Class A galvanized steel utility grade strand.

CO8E			An aerial filled fiber optic cable with 8 fibers,

lashed to existing strand and cables(s).

Section CW - AERIAL FILLED COPPER CABLE ASSEMBLY UNITS

Consists of one (1) foot (0.305 m) of aerial filled copper cable in place including supporting messenger of galvanized steel strand, lashing wire, attachments to strand, bonding of the shield and strand in accordance with the Construction Sheets.

Options designated by the following suffixes apply:

Suffix		Description

A			Aluminum-clad steel strand.

C	Class C galvanized steel utility grade strand is required for corrosion areas.

D			Two or more cables are to be initially lashed to

the same suspension strand.

E			Cables are to be lashed to existing strand and

cable(s).

H			Screened cable designated for T1 carrier systems.

H1C		Screened cable designated for T1C carrier systems.

A.	This unit includes labor and material for installation of the splice closure, and other labor and materials for straight splicing cables of the same size and gauge required only for the purpose of joining such cables in one continuous length (reel ends).

B.	When specified in the Proposal, this unit includes the spiraling of cable around the suspension strand at the locations shown on the Construction Sheets.

C.	The length of aerial cable measured for compensation purposes includes the sum of the cable distances between supporting structures as indicated by the sequential foot markings.

D.	Where aerial cables are supported by separate through-bolts on the same pole, messenger bonds required as shown on the Construction Sheets are included as a part of this unit.

E.	Class A galvanized steel utility grade strand shall be provided unless another type is specified by the appropriate suffix.

Each aerial filled copper cable assembly unit is listed in accordance with the number of pairs and gauge of conductors.  Each unit is prefixed by the letters CW.  The following illustrations indicate the method of designating the material required.

CW50-24(6M)         A 50-pair, 24-gauge aerial filled copper cable supported by 6000 lbs (26,688 N) Class A galvanized steel utility grade strand.

CW50-24(6M)C        A 50-pair, 24-gauge aerial filled copper cable supported by 6000 lbs (26,688 N) Class C galvanized steel utility grade strand.

Section HA - AERIAL SPLICE CLOSURE ASSEMBLY UNITS

Consists of an aerial splice closure and the closure manufacturer’s provided encapsulating material if required, installed in place and the labor and material for setting up in preparation for installing the closure, such as, opening the sheath or jacket of the cable, bonding of cable shields, filling the closure if required, closing the closure, and, when applicable, pressure testing, all in accordance with the manufacturer's instructions.  It also includes all necessary hardware items to support the cable adjacent to the closure and to terminate the lashing wire.  Cable splicing shall be compensated under the appropriate splicing units.

The assembly units are defined as follows:

HAC( )	Aerial Free-Breathing, Nonfilled Closure – A free-breathing, nonfilled splice closure with pair count and gauge for each cable to be spliced.

HAF( )	Aerial Filled Closure – A filled splice closure with pair count and gauge for each cable to be spliced.

HAP( )	Aerial Pressurized Closure – A pressurized splice closure with pair count and gauge for each cable to be spliced.

For Fiber Optic applications use the following suffix:

Suffix		Description

O	Splice closure and organizer for fiber optic cables.  The closure manufacturer shall specify the appropriate organizer.

The following illustrations indicate the method of designating the material required.

HAC(100-24)         Aerial free-breathing, nonfilled splice closure enclosing two cable ends with same pair count and gauge.

HAF(100-24)(50-24)  Aerial filled splice closure enclosing two cable ends with different pair counts.

HACO(24)	Aerial free-breathing, nonfilled fiber optic splice closure and organizer capable of accommodating a minimum of 24 fibers.

HAP(100-24)	Aerial pressurized splice closure enclosing two cable ends with same pair count and gauge.

HAPO(12)	Aerial pressurized fiber optic splice closure and organizer capable of accommodating a minimum of 12 fibers.

Section HC - COPPER SPLICING ASSEMBLY UNITS

HC1	Consists of the labor and material necessary in the wire work and splicing of one (1) cable pair in any cable, including any non-working pair in an existing cable in accordance with RUS Splicing Standard Bulletin 1753F-401 (PC-2) using individual mechanical splicing connectors.  The splice may be straight, bridged, or pieced out and bridged.  Pairs that are to be tested, capped, or tested and capped, when specified by the Engineer are considered to be part of this unit.  Only those pairs on which splicing, testing, and/or capping operations are performed are counted and each pair is counted only once at each location.  On aerial inserts, each end of the fuse link is considered as a splice.

HC3	Consists of the labor and material necessary in the wire work and splicing of one (1) cable pair in any cable, including any non-working pair in an existing cable in accordance with RUS Splicing Standard Bulletin 1753F-401 (PC-2) using splicing modules.  The splice may be straight, bridged or pieced out and bridged.  Pairs that are to be tested, capped, or tested and capped, when specified by the Engineer are considered to be part of this unit.  Only those pairs on which splicing, testing, and/or capping operations are performed are counted and each pair is counted only once at each location.  On aerial inserts, each end of the fuse link is considered as a splice.

HC5  	Consists of the labor and material necessary for terminating one (1) pair on a terminal block within a ready access closure, including a non-working pair in existing cables in accordance with RUS Splicing Standard Bulletin 1753F-401 (PC-2).  Pairs that are to be tested, when specified by the Engineer, are considered to be part of this unit.

Section HO - FIBER OPTIC SPLICING ASSEMBLY UNITS

Consists of all labor and material necessary to splice and/or test one (1) glass fiber in any cable in accordance with RUS Splicing Standard Bulletin 1753F-401(PC-2).  The labor shall include initial measurement, minimizing the attenuation, splicing and stowing the spliced fiber in a fiber organizer.  The labor and material for the fiber organizer is part of the appropriate splice closure unit.

Suffix      Description

HO1		Fusion Splice

HO2		Mechanical Splice

HO3		Connector Splice

### Section HR – READY ACCESS SPLICE CLOSURE ASSEMBLY UNITS

Consists of a ready access closure containing unprotected filled terminal blocks installed in place and includes the labor and material for setting up in preparation for installing the ready access closure, such as, opening the sheath or jacket of the cable, bonding of cable shields, and closing the closure in accordance with the manufacturer's instructions.  It also includes all necessary hardware items to support the cable adjacent to the closure and to terminate the lashing wire.  Cable splicing shall be compensated under the appropriate splicing units.  When protected filled terminal blocks are to be specified, the unit shall be suffixed by the letter "P".

Ready access closures not containing filled terminal blocks shall be suffixed with the letter "U".  Under this option, installation of filled terminal blocks shall be compensated under other units.

The assembly units are defined as follows:

HR1( )( )		A straight splice ready access closure.

HR2( )( )		A branch splice ready access closure.

The first set of parentheses shall indicate the main cable diameter (dia.), in inches (in.) [millimeters (mm)], as shown in the illustration.  The second set of parentheses shall indicate the number of terminals within the ready access closure.  When the unit is suffixed with the letter "U" the second set of parentheses is not applicable.

##### The following illustrations indicate the method of designating the material required.

HR1(2.0)(12)	Ready access closure, accommodating a straight splice with a maximum cable diameter of 2.0 in. (50.8 mm), and equipped with filled terminal blocks with a total of 12 terminations.

HR2(1.0)(6)	Ready access closure, accommodating a branch splice with a maximum cable diameter of

1.0 in. (25.4 mm), and equipped with filled terminal blocks with a total of 6 terminations.

HR1(2.0)U	Ready access closure, accommodating a straight splice with a maximum cable diameter of 2.0 in. (50.8 mm), without any terminal blocks installed.

Section PE - GUY ASSEMBLY UNITS

Consists of strand and hardware; and insulators or ground connection where required.  For guying purposes, when a cable messenger strand is extended one or more spans to a deadend structure, the strand in each such span shall be considered as an overhead guy for the appropriate size of strand used.

The assembly units are defined as follows:

PE1-2    Down Guy for 6M strand

PE1-3    Down Guy for 10M strand

PE1-4    Down Guy for 16M strand

PE1-2G   Down Guy, Ground Connection Type for 6M strand

PE1-3G   Down Guy, Ground Connection Type for 10M strand

PE1-4G   Down Guy, Ground Connection Type for 16M strand

PE2-2    Overhead Guy for 6M strand

PE2-3    Overhead Guy for 10M strand

PE2-4    Overhead Guy for 16M strand

PE2-2G   Overhead Guy, Ground Connection Type for 6M strand

PE2-3G   Overhead Guy, Ground Connection Type for 10M strand

PE2-4G   Overhead Guy, Ground Connection Type for 16M strand

Note:  When the above Guy Assembly Units are to be installed on existing poles, the assembly unit designation is prefixed by the letter "N".

Unless otherwise indicated by an additional suffix, the strand furnished on the Project will be seven-wire, Class A galvanized steel utility grade.  The following suffix may be used:

Suffix		Type of Strand

A			Aluminum - Clad steel

C			Class C galvanized steel utility grade

Section PF – ANCHOR ASSEMBLY UNITS

Consists of the anchor with rod, complete and in place, ready for attaching the guy strand.

The assembly units are defined as follows:

PFl-3	Expanding Anchor	-   6,000	lbs  (26,688 N)

PFl-5	Expanding Anchor	-  10,000	lbs	(44,480 N)

PFl-7	Expanding Anchor	-  16,000	lbs	(71,168 N)

PF2-3	Plate Anchor		-   6,000	lbs	(26,688 N)

PF2-5	Plate Anchor		-  10,000	lbs	(44,480 N)

PF2-7	Plate Anchor		-  16,000	lbs	(71,168 N)

PF3-3	Screw Anchor		-   6,000	lbs	(26,688 N)

PF3-5	Screw Anchor		-  10,000	lbs	(44,480 N)

PF3-7	Screw Anchor		-  16,000	lbs	(71,168 N)

PF5-3	Rock Anchor		-   3/4 in. dia. (19 mm) rod

PF5-4	Rock Anchor		-   1 in. dia. (25.4 mm) rod

PF6-3	Swamp Anchor		-   10 in. dia. (254 mm)

PF6-4	Swamp Anchor		-   12 in. dia. (305 mm)

PF6-5	Swamp Anchor		-   15 in. dia. (381 mm)

Note:  When twineye rods are required for the above anchor assembly units, the unit designation is suffixed by the letter "A".

#### Section PM - MISCELLANEOUS ASSEMBLY UNITS

Consists of all labor and materials to construct and install the units defined individually below required for the installation and construction of the aerial portions of the Project:

PM1			Pole Lightning Protection Assembly

PM2			Pole Ground Assembly

PM2-1		Auxiliary Ground Rod Assembly

PM2A			Ground wire assembly for bonding aerial cable

strand or support wire to electric system neutral

or pole ground assembly.

PM4			Cable Extension Arm (Short)

PM4A			Cable Extension Arm (Long)

PM5			Pole Stepping Assembly

PM6			One Wood Pole Key

PM7			Two Wood Pole Keys

PM8			One Wood Key and One Metal Expanding Key

PM9			Two Wood Keys and One Metal Expanding Key

PM11			Guy Guard

PM12( )	Consists of all labor and material to install a sidewalk guy arm.  The guy, guy guard and anchor assembly units will be specified separately.  The length in feet (meters) of a single piece of

2 in.(50.8 mm) galvanized steel pipe shall be indicated in the parentheses.

PM14			Push Brace Accessories

PM21	Cable Entrance – Consists of the necessary labor and material to terminate copper and/or fiber optic outside plant cables as shown on the detailed drawings as specified by the Engineer.

PM22	Grounding System – Consists of the necessary labor and material to construct a grounding system as shown on the detailed drawings as specified by the Engineer.  This unit shall include all ground electrodes, trenching, backfilling, bonding the auxiliary ground electrodes to each other and to the primary ground electrodes, and bonding to the master ground bar (MGB).

PM25( )	Filled Terminal Block Assembly Unit - Consists of an unprotected filled terminal block, mounted in place in a ready access closure (separately specified) and connected to the conductors of the cable as specified by the Engineer.  Splicing of the cable conductors shall be in accordance with RUS Splicing Standard Bulletin 1753F-401 (PC-2).  The pair count of the terminal block shall be indicated in the parentheses.  When protected filled terminal blocks are to be specified, the unit shall be suffixed by the letter "P".

PM52			Pole Marking, Per Pole, Route and Pole Number.

Section R - RIGHT-OF-WAY CLEARING AND TRIMMING UNITS

Aerial Plant

A.	Clearing Units are defined as follows:

R1-5 	Is one (1) foot (0.305 m) in length and 5 feet (1.52 m) in width (to be measured on one side of the pole line) of actual clearing of right-of-way.  The unit applies to clearing right-of-way along new or existing telecommunications pole lines and along existing power pole lines.  This includes clearing of underbrush, tree removal, and such tree trimming as may be required to leave an unobstructed right-of-way from the ground up on one side of the line of poles carrying wire or cable.  The length of actual clearing shall be measured in a straight line parallel to the line between poles and across the maximum dimension of foliage cleared (not trunk) projected to the ground line.  All trees and underbrush across the width of the right-of-way shall be considered to be grouped together as a single length in measuring the total length of clearing.  Lengths along the right-of-way in which no trees are to be removed or trimmed or underbrush cleared shall be omitted from the total measurement.  This unit includes the removal, or topping (cutting out the top of the tree so that if the remaining portions of the tree fall, they will not endanger the line) at the option of the Contractor, of danger trees outside of the right-of-way when so designated by the Engineer. (Danger trees are defined as dead or leaning trees, which, in falling, would affect the operation of the line.) The Contractor shall not remove or trim shade, fruit, or ornamental trees unless so directed by the Engineer.

R1-10		Identical to R1-5 except that width is 10 feet

(3.05 m).

R2-5	Identical with R1-5, except that width 10 feet (3.05 m); to be measured 5 feet (1.52m) on each side of the pole line.

R2-10 	Identical with Rl-5, except that width 20 feet (6.1 m), to be measured 10 feet (3.05m) on each side of the pole line.

Note:  The letter "M" added as a suffix to the above "R" units designates units for reclearing existing right-of-way.  With the exception of the substitution of the word "reclearing" for "clearing", the remaining description of the "R" assembly units applies for the units suffixed with the letter "M".

B.	The Trimming Unit is defined as follows:

R3-5	Is one (1) foot (0.305 m) in length and consists of the trimming of foliage and branches from trees growing on or adjacent to the right-of-way so as to provide a clearance of not less than 5 feet (1.52 m) in all directions from telecommunications cable.  This unit is measured parallel to the pole line across the maximum width of foliage trimmed.  All trees, underbrush or shrubbery across the width trimmed shall be considered to be grouped together as a single length in measuring the total length of trimming.  Lengths along the right-of-way in which no trimming is performed shall be omitted from the total measurement.  Any trimming included in Rl or R2 right-of-way clearing units, shall not be considered a part of the measurement of the unit.  The Contractor shall not trim any shade, fruit or ornamental trees unless so directed by the Engineer.  When so designated by the Engineer, a tree may be trimmed of its branches with the trunk left extending into the zone to be trimmed.

Section W - REARRANGEMENT UNITS

Specific rearrangement units shall be designated and described by the Engineer on the "List of Special Arrangement Units" table of RUS Form 515.  Existing plant assembly units to be rearranged are designated by a prefix "W".

Section XX - NONREUSABLE MATERIALS REMOVAL UNITS

These units cover the furnishing of all labor for the removal of construction assembly units from existing lines, and transportation of the removed materials for proper disposal.  The Contractor will be permitted to use the most economical method of removing these units.  The removal units are designated by the prefix "XX" followed by the assembly unit designation of the unit to be removed.

Section XZ - REUSABLE MATERIALS REMOVAL UNITS

These units cover the furnishing of all labor for the removal of construction assembly units from existing lines and all labor and transportation of the removed materials to a location designated by the Owner.  The Contractor will be charged by the Owner for the materials removed under this section at the unit material values shown in column 2 of the "Value and Disposition of Units to be Removed" table of RUS Form 515.  The number of units to be charged to the Contractor and the extended value of these units are shown in columns 3 and 4. Such charges will be placed against the Contractor as assembly units are removed and the unit material values will be deducted from the total value of assembly units constructed on this project for determination of the work accomplished for purposes of the monthly progress payments to the Contractor.  Of the assembly units listed in the "Value and Disposition of Units to be Removed" table to be removed from existing lines certain units are to be reused in the construction of the project.  The quantity of such units to be reused is listed in the "Value and Disposition of Units to be Removed" table, column 5. These units where installed in the project will be inventoried as new assembly units and compensated for at the unit bid prices.  The quantity of assembly units listed in column 6 of the "Value and Disposition of Units to be Removed" table is the maximum quantity of removed assembly units that are to be returned to the Owner for credit which will be allowed at the unit material prices in column 2.  Column 7 indicates the extended value of the units to be returned to the Owner.  The Contractor will be allowed credit for assembly units listed in column 6 which, in the opinion of the Engineer, have not been damaged by the Contractor in removal and handling.  Such credits will be allowed the Contractor as the assembly units are returned to a location designated by the Owner and shall be added to the total value of installed assembly units for determination of work accomplished for the purposes of the monthly progress payments to the Contractor.  The removal units are specified by the prefix "XZ" followed by the assembly unit designation of the existing assembly unit to be removed.

### Part II - SPECIFICATIONS FOR MATERIALS

1.	SCOPE

This part of the specification is concerned with the various materials required for the construction of the outside aerial cable plant of the rural telecommunications system as shown on the Plans, Specifications, and Construction Sheets.

2.	GENERAL

All materials used in the construction of the rural telecommunications system except those listed in Paragraph 4 below shall be listed in RUS Informational Publication (IP)

344-2, "List of Materials Acceptable for Use on Telecommunications Systems of RUS Borrowers," unless specific written approval has been granted by the Administrator.

3.	POLES

3.1	The pole plan, method of treatment, kind of preservative and general procedure applying to all poles shall be in accordance with the latest RUS specifications for these items in effect at the time the bids are received.  All poles shall be framed in accordance with the framing guide attached to the specifications.

3.2  Poles shall be of the length and American National Standards Institute, Inc. (ANSI) class specified in the Proposal.

4. 	MISCELLANEOUS

Items which do not appear in RUS IP 344-2, "List of Materials Acceptable for Use on Telecommunications Systems of RUS Borrowers," shall be of a quality suitable for the application for which they are intended.

Part III - SPECIFICATIONS FOR CONSTRUCTION AND INSTALLATION

1.	GENERAL

1.1	All construction and installation work shall be done in a thorough and workmanlike manner in accordance with the Plans, Specifications and Construction Sheets and shall be subject to acceptance by the Owner and the Administrator.

1.2	All material to be used in construction of the Project shall be stored so as to be protected from deteriorating effects of the elements.

1.3	All guy strand, suspension strand, aerial cables, and accessory materials used in the construction of the Project shall be handled with care.  Each reel of aerial cable shall be inspected for damage.  All damage shall be repaired to the satisfaction of the Engineer and in accordance with the methods or other instructions described in the appropriate paragraphs of Part III.  If reel wrap is present, the reel wrap shall remain intact on the reel until the cable is ready to be placed.

1.4	Deviations from the Plans, Specifications and Construction Sheets shall not be permitted except upon written permission of the Engineer.

1.5	The latest revision of the National Electrical Safety Code (NESC) and the National Electrical Code (NEC) shall be followed in every case except where local regulations are more stringent, in which case local regulations shall govern.

1.6	The Contractor shall maintain conductor polarity (tip and ring) identification at the main distributing frame, cable terminals, wire terminals, terminal blocks, and in the service entrance, all in accordance with the Specifications and Construction Sheets (see guide drawing 815).

2.	POLE LINES

2.1  Poles shall be handled carefully.  Damaged poles shall not be used.

2.2  The pole hole shall be of sufficient diameter to permit the pole to settle freely to the bottom of the hole without trimming the butt and still have sufficient space between the pole and the sides of the hole to permit proper tamping of the backfill at every point around the pole, and throughout the entire depth of the hole.

2.3  The setting depth, in feet (or meters), for poles of various lengths shall be as follows:

# Length of			Setting			   Setting

Pole				in Soil			in Solid Rock

20 (6.10)			4.0 (1.22)		3.0 (0.91)

25 (7.62)			5.0 (1.52)		3.5 (1.07)

30 (9.14)			5.5 (1.68)		3.5 (1.07)

35 (10.67)		6.0 (1.83)		4.0 (1.22)

40 (12.19)		6.0 (1.83)		4.0 (1.22)

45 (13.72)		6.5 (1.98)		4.5 (1.37)

50 (15.24)		7.0 (2.13)		4.5 (1.37)

55 (16.76)		7.5 (2.29)		5.0 (1.52)

60 (18.29)		8.0 (2.44)		5.0 (1.52)

2.4  The "Setting in Soil" depth as shown in paragraph 2.3, shall apply where poles are to be set in soil only; where there is a layer of soil more than 2 feet (0.61 m) in depth over solid rock; or where the pole in solid rock is not substantially vertical or the diameter of the hole at the surface of the rock exceeds approximately twice the diameter of the pole at the same level.

2.5  The "Setting in Solid Rock" depth as shown in paragraph 2.3, shall apply where solid rock is encountered at the ground line and where the hole is substantially vertical, approximately uniform in diameter, and large enough to permit the use of tamping bars the full depth of the hole.

2.6  Where there is a layer of soil 2 feet (0.61 m) or less in depth over solid rock, the depth of the hole shall be the depth of the soil in addition to the depth specified in paragraph 2.3 under "Setting in Solid Rock," provided, however, that such depth shall not exceed the depth specified under "Setting in Soil."

2.7  On sloping ground the depth of the hole shall be measured from the low side of the hole.  Where a pole is to be set on the side of a steep grade where soil erosion appears to be a consideration, the hole should be one (1) foot (0.305 m) deeper than specified in paragraph 2.3 under "Setting in Soil."

2.8  When an earth boring machine is employed for holes for guyed poles, the bottom of the hole shall be thoroughly tamped to compact any loose earth that may be present.

2.9  All holes shall be backfilled with soil or small rock and all pole holes in rock shall be inspected and approved by the Engineer before being backfilled.

2.10  Backfill shall be thoroughly tamped the full depth of the pole hole.  Earth must be banked around the pole to a minimum height of 6 in. [15.24 centimeters (cm)] above ground level.

2.11  Holes in soil for poles at unguyed corners where the pole will not be keyed shall be one (1) foot (0.305 m) deeper than the "Setting in Soil" depth as shown in paragraph 2.3.  For holes in solid rock the "Setting in Solid Rock" depth will apply.

2.12  The Contractor shall be responsible for setting poles in alignment according to the staking sheets.  If the Contractor should find stakes out of alignment, the Engineer shall, upon request of the Contractor, realign the stakes according to the construction sheets.

2.13  Poles shall be set plumb except at corners where they shall be set and raked against the load so that the pole top will be in line after the load is applied.  The rake in pole shall not exceed 6 in. (15.24 cm) for each 10 feet (3.05 m) of pole length after the conductors are installed at the required tension.  Deadend shall be set so as to be plumb and in line after the load it applied.

2.14  Pole lightning protection shall be a #6 AWG bare copper wire installed in accordance with assembly unit drawing PM1.

3.	MOUNTING HARDWARE AND GUYS

3.1  All bolts employed for the mounting of hardware items on poles shall be long enough to fully engage the nut (including locknut, where applicable) but shall not extend more than 2 in. (50.8 mm) beyond the nut after the nut is tightened.  The ends of bolts shall not be cut.

3.2  The Engineer shall determine all guy locations and shall specify the type of guy.  Guys shall be installed before conductors or cable suspension strands are placed.

4. 	ANCHORS

4.1  Anchor assembly units shall be installed at locations designated on the construction sheets.

4.2  All anchors and rods shall be in line with the load and shall be so installed that the eye of the rod is above grade.  Not more than 6 in. (152 mm) of rod shall remain out of the ground after the load is applied.

4.3  When an expansion type anchor is used, the anchor shall be fully expanded and shall be expanded into undisturbed earth before backfilling the anchor hole.

4.4  Backfill shall be thoroughly tamped the full depth of all anchor holes.

4.5  Rock anchors shall be placed in accordance with the detailed

instructions of the Engineer.  Where a rock is encountered below the surface of the ground, instructions from the Engineer shall be obtained before placing an anchor at that location.

5.	SELF SUPPORTING FIBER OPTIC CABLE

5.1  Where physical obstructions make it necessary to pull cable along the line from a stationary reel, cable stringing blocks shall be used to support the cable during all placing and tensioning operations.  Ladders, cable cars and other equipment shall not be placed on or against the cable.

5.2  Splicing of the optical fibers shall be performed in accordance with RUS Splicing Standard Bulletin 1753F-401 (PC-2).  Splicing of the support member shall be performed in accordance with the method specified by the Engineer.

5.3  During installation, maximum pulling tension and minimum bending radius of the self supporting fiber optic cable shall not exceed the cable manufacturer's recommendations.

5.4  Initial stringing tension, maximum permissible span length, and sagging shall be in accordance with the cable manufacturer's recommendations.

5.5  Self supporting fiber optic cable shall be spiraled in accordance with the method shown on Construction Guide Drawing 250-1.  Spiraling of the cable shall be performed within 24 hours of the tensioning operation.

5.6  The insulation shall not be removed from the support member except at bonding and ground points; and at points where ends of the support member are terminated in splicing and deadend devices.

5.7  The support member of self supporting fiber optic cable shall be made electrically continuous throughout its entire length.

5.8  At junctions between self supporting fiber optic cable and aerial fiber cable, or buried fiber cable, the support messenger shall be bonded to the aerial cable strand or buried cable armor.

5.9  The support member of self supporting fiber optic cable shall be grounded at locations specified by the Engineer by connecting the support wire to a pole ground wire as shown on the Construction Sheets.

5.10  When specified by the Engineer, the insulation of the support member at deadend fittings, splices and bridged grounding connections shall be restored in accordance with the method shown in Construction Guide Drawing 360.

5.11  Damaged portions of the self supporting fiber optic cable shall be cut out and the support member spliced in accordance with the method specified by the Engineer.

6.	SUSPENSION STRAND

6.1  The cable shall be installed within a reasonable time after the strand is installed and tensioned.  If a delay in installing cable in excess of 24 hours is encountered, temporary dampers shall be installed on the strand.

6.2  When tensioning strand the cable suspension clamps shall be loose enough to allow free movement of the strand.

6.3  Suspension strand shall be placed in accordance with the Construction Sheets and shall be tensioned in accordance with instructions, which shall be furnished, to the Contractor by the Engineer.

6.4  The suspension strand shall be placed on the roadside of the pole line unless otherwise directed by the Engineer.

6.5  In tangent construction, the lip of the suspension strand clamp shall point toward the pole.  At angles in the line, the suspension strand clamp lip shall point away from the load.

6.6  In level construction the suspension strand clamp shall be placed in such a manner that it shall hold the strand below the through-bolt.  At points where there is an up-pull on the strand, the clamp shall be so placed that it shall support the strand above the through-bolt.

6.7  When a thimbleye bolt is used both to mount the suspension strand clamp and to make the guy attachment, the size of the suspension strand clamp shall be governed by the size of the thimbleye bolt required for the guy.

6.8  The air temperature at the time and place of tensioning the strand shall be determined by means specified by the Engineer.

6.9  The suspension strand shall be made electrically continuous throughout its entire length as indicated on the Construction Sheets.

6.10  Suspension strands shall be bonded to other bare cable suspension strands, and guys on the same pole and grounded by connection to ground leads at locations specified by the Engineer and in the manner specified by the Engineer.  Where the strand is to be grounded to a multigrounded neutral on a pole which does not carry a vertical pole ground wire, a #6 AWG bare copper wire shall be left coiled and taped to permit it to be extended up the pole and connected to the multiground neutral by a representative of the power company.

7.	FILLED AERIAL CABLE

7.1  The Contractor and Engineer shall jointly inspect all reels of cable for damage prior to installation.

7.2  Cable ends shall be kept sealed at all times, i.e., during transportation, in storage, and during cable placement to prevent moisture entry into the cable core.  Acceptable cable end caps shall be used for this purpose.

7.3  Cable shall be taken from the reel only as it is placed.    Bends of small radii and twists shall be avoided in handling cable.

7.4  If the jacket is deformed in handling the cable, the Engineer shall be notified.  If directed by the Engineer, the deformed section of the jacket shall be removed; the insulation and conductors shall be examined and if damaged shall be repaired.  The opening in the jacket shall then be closed by means of a suitable enclosure.  Repairs so made shall be done in accordance with appropriate specifications.

8.	FILLED AERIAL CABLE PLACEMENT

8.1  During placing operations, copper cables shall not be bent in a radius less than 10 times the outside diameter of the cable and fiber optic cables shall not be bent in a radius less than 20 times the outside diameter of the cable.  Temporary supports where necessary, shall be placed sufficiently close together and proper tensioning of the cable shall be employed to prevent bending in excess of the above requirements.

8.2  In those instances where spiraling of cable is involved, the mounting of closures for purposes of splicing and distribution shall be accomplished after the spiraling operation has been completed.

8.3  Cable guards shall be applied over the cable at points of potential abrasion such as at supports, and in locations where tree trimming is not permitted.

8.4  Cable shall be lashed with lashing wire to the suspension strand by means of a suitable lashing machine.

8.5  The pitch of the lashing wire may be from 10 to 15 in.

(254 to 381 mm) but must be constant for any section of cable of the same size and gauge.  For cables of 3/4 in. (19 mm) or larger in diameter, the lashing wire shall be placed with a tension of 35 to 40 lbs (156 to 178 N).  Cables having a smaller diameter less than 3/4 in. (19 mm) shall be lashed with a lashing wire tension of 18 to 25 lbs (80 to 111 N).

8.6  During the placing operation, precautions shall be taken to prevent slippage of the cable sheath or jacket over the core.

8.7  The cable shall be snug against the suspension strand throughout the span.  It shall be supported in a position directly below the strand insofar as possible, except where spiraling has been specified.  Where more than one cable is placed on a strand, the cables shall be arranged as shown on the Construction Sheets so that the cables are snug against the suspension strand and against each other.

8.8  The lashing wire shall be terminated at each pole and the cable shall be supported and protected at the suspension clamp in accordance with the Construction Sheets.

8.9  At lashing wire terminating points, the tension placed in the lashing wire by the lashing machine shall be maintained.  No slack in the lashing wire shall be permitted to run into the span.

8.10  When lashing wire is spliced in a span, the splice shall be made by means of a compression type splicing sleeve.  The completed splice shall be placed on the strand in such a position that it shall not result in damage to the cable sheath or jacket.

8.11  Where suspension strand attachments such as suspension strand cross-over, suspension strand pull-offs, etc., are encountered in the span, a positive separation shall be provided between the suspension strand attachment and the cable, and the cable shall be supported and protected in accordance with the Construction Sheets.

8.12  At splices where the cable is not cut, no slack shall be left in the cable.  So that no slack can run into the span, the lashing wire shall be securely clamped to the strand until the splice is completed, at which time the lashing wire shall be terminated in accordance with the Construction Sheets.

8.13  At cut splices in the cable, sufficient overlap shall be provided to permit splicing without piecing out the conductors.

8.14  Spiraling of lashed cable where specified shall be performed in accordance with the method shown on the Construction Guide Drawing 250.  Spiraling of the cable shall be performed within 48 hours of the tensioning operation.

8.15  Where the new cable is to be lashed to existing strand and cable(s), the preceding requirements for placement of lashed cable shall also be adhered to, except as modified and/or supplemented as follows:

8.15.1  The cable shall be lashed to the existing strand and cable(s) so that it and the existing cable(s) shall be as snug against the existing strand as is practicable.

Note:  If the existing cable is spiraled, the spiraling shall first be removed.  The existing cable after unspiraling and the new cable shall then be lashed, without either being spiraled, to the existing strand in the same lashing operation.

8.15.2  The lashing wire shall be terminated on both sides of all splices and devices in/on the existing cable where interference with the lashing operation is encountered.

8.15.3  Cable spacers and cable straps, as required, shall be used at all points of lashing wire termination to maintain proper separation and support for the new cable.

8.15.4  Spacers shall be added to the existing suspension clamp mountings, where required, to maintain proper separation between the cable and the surface of the pole.

8.15.5  Ready-access closures to be installed on the new cable(s) shall be equipped with extension fittings so that they will be located below and separate from the existing cable.

8.16.6  The existing lashing wire, fittings and attachments shall be adjusted as necessary to maintain proper security of the new cable and the existing cable, and to maintain adequate separations and clearances.

9.	CABLE SPLICING AND TERMINALS

9.1  Splicing for copper cable and fiber optic cable shall be in accordance with RUS Splicing Standard Bulletin 1753F-401 (PC-2).

9.2  Aerial cable terminals and ready-access closures equipped with filled terminal blocks shall be installed in accordance with the Construction Sheets and connected in accordance with the cable schematic drawings furnished by the Engineer.  Splicing shall be performed in accordance with RUS Splicing Standard Bulletin 1753F-401 (PC-2).

10.	CLEARING RIGHT-OF-WAY

10.1  In clearing the right-of-way, trees shall be removed or trimmed and underbrush cleared in accordance with the Construction Sheets.  Trees fronting the side of the right-of-way shall be trimmed symmetrically unless otherwise directed by the Engineer.

10.2  Dead trees beyond the right-of-way, which would strike the line in falling, shall be removed.

10.3  Leaning trees beyond the right-of-way which would strike the line in falling and which would require topping if not removed, may be removed or topped at the option of the Contractor; however, the Contractor shall trim and not remove shade, fruit, or ornamental trees unless otherwise directed by the Engineer.

LIST OF CONSTRUCTION DRAWINGS AND PLANS

Assembly Unit Drawings

HR1 	Ready-Access Enclosure, Lashed

Cable Straight Splice

HR2 	Ready-Access Enclosure, Lashed

Cable Branch Splice

# PE1-2, PE1-3, and PE1-4		Down Guy

PE1-2G, PE1-3G, and PE1-4G	Down Guy, Ground Connections

PE2-2, PE2-3, and PE2-4		Overhead Guy

PE2-2G, PE2-3G, and PE2-4G	Overhead Guy, Ground Connections

PF1-3, PF1-5, and PF1-7 		Expanding Anchor Assembly

PF3-3, PF3-5, and PF3-7 		Screw Anchor Assembly

PF5-3 and PF5-4 			Rock Anchor Assembly

PF6-3, PF6-4, and PF6-5 		Swamp Anchor Assembly

PM1						Pole Lightning Protection Assembly

PM2						Pole Ground Assembly

PM2-1					Auxiliary Ground Rod Assembly

PM2A						Ground Wire Assembly

PM4						Cable Extension Arm Assembly (Short)

PM4A						Cable Extension Arm Assembly (Long)

PM5						Pole Stepping Assembly

PM6 and PM7				Pole Key Assemblies

PM8 and PM9				Pole Key Assemblies

PM12						Sidewalk Guy Arm Assembly

PM14						Push Brace Accessories

PM52						Pole Marking

Construction Guide Drawings

201			Suspension Strand Mounting

201-1		Self Supporting Filled Fiber Optic Cable Support

202			Suspension Strand Mounting (Pull Away from Pole)

202-1		Suspension Strand Mounting (Pull Against Pole)

  - Self Supporting Filled Fiber Optic Cable Support,

###### Corner

203			Suspension Strand Mounting (Corners)

  - Self Supporting Filled Fiber Optic Cable Support,

###### Corner

204			Suspension Strand Deadend

206			Branch Suspension Strand

207			Branch Suspension Strand

208			Suspension Strand Pull-Off

209-1		Suspension Strand Bonding

211			False Deadend

212			Strand Layouts

214			Arrangement Details of Cables at Pole Supports

241			Lashed Cable Support at Pole

242			Lashing Wire Terminations

243			Lashing Wire Terminations at Suspension Strand 				  Crossovers

250			Method of Spiraling Aerial Cable

250-1		Method of Spiraling Self Supporting Filled Fiber

Optic Cable (Figure 8 Design)

312-1		Aerial Plastic Cable, Details of Wire

Connections to Terminal blocks

360			Method of Restoring Insulation on

Support Member of Self Supporting Filled

Fiber Optic Cable (Figure 8 Design)

812			Guy Hook, Details of Installation

- Conductor Polarity (Tip and Ring) Diagram

(Aerial Plant)

NOTE:  On the Assembly Unit or Guide Drawings an asterisk (*) in the ITEM column indicates items that are no longer listed in RUS IP 344-2, "List of Materials Acceptable for Use on Telecommunications Systems of RUS Borrowers."

# Text boxes

United States

Department of

Agriculture

Rural

Utilities

Service

RUS Bulletin 1753F-152

RUS Form 515c

September 2001

Specifications and Drawings for Construction of

Aerial Plant