# STATEMENT OF WORK

# FOR

# DRY AND WET CHEMICAL EXTINGUISHING SYSTEMS MAINTENANCE

Peterson AFB

1  February 2009

SECTION I

DESCRIPTION OF SERVICES

1.1  SCOPE OF WORK: The contractor shall furnish all personnel, transportation, tools, equipment, supervision, administration, chemicals, and parts to inspect, test and maintain dry and wet chemical fire suppression systems for the facilities at Peterson AFB, Colorado, as listed in Technical Exhibit 2 (TE-2).  The contractor shall perform to the standards in this contract and to the standards set forth in the current edition of National Fire Protection Association  (NFPA) 17, Standard For Dry Chemical Extinguishing Systems; NFPA 17A, Standard For Wet Chemical Extinguishing Systems; NFPA 70, National Electric Code;  NFPA 72, National Fire Alarm Code;  and NFPA 96, Standard for Ventilation Control and Fire Protection of Commercial Cooking Operations.  The contractor shall comply with local, state, and federal laws and regulations regarding transportation and handling of compressed gasses and extinguishing system chemical agents.

1.2  OPERATIONAL REQUIREMENT AND SPECIFIC TASKS

1.2.1  Chemicals.  For the term of this contract the contractor shall provide all appropriate chemicals to service the systems listed in TE-1.  The contractor shall recharge any system that is below operating range when necessary.  The contractor will not be reimbursed for any chemicals used.

1.2.2  Parts.  For the term of this contract the contractor shall install, when necessary, all replacement parts not exceeding a retail cost of $200.00.  For costs which exceed $200.00 for parts and all additional work not covered in this contract, shall be submitted to the contracting officer for approval prior to work commencing

1.2.3  Inspection, Testing, and Maintenance (ITM).  The contractor shall service all fire suppression systems listed in TE-1.  Service shall be semi-annual and conducted in the months of February and August, during the performance period.  Inspection, testing and maintenance shall be IAW the standards listed in paragraph 1.1.

1.2.4  Discharging of Systems.  If the contractor discharges any system listed in TE-1, the contractor shall be responsible to clean up, re-service and reinstate the system to full normal stand-by operation.  The contractor will not be reimbursed for any lost chemical or labor.

1.2.5  Inspector.  A representative of the Base Fire Department shall be present during selected system inspections and will serve as the inspector for this contract.  Contractor will not leave job site until a Fire Department Representative has verified system is operational.

1.2.6  Conditions of Work.  All work shall be performed with the using agency representative present for the duration of the contract service.  The contractor shall conduct his or her work in a manner, which minimizes disruption of the occupants and normal operations.

1.2.7  Scheduling:  All work will be scheduled through the Fire Prevention Office, telephone number(s) 556-6574; 556-4242 or 556-7774.  Contractor shall schedule maintenance with facility managers and provide schedules to the fire department no later than the 15th of February and 15th of August, for maintenance in February and August.  Variances to the schedule shall be coordinated with the Fire Prevention Office at least 24 hours in advance.

SECTION II

SERVICE SUMMARY

| PERFORMANCE OBJECTIVE | SOW PARAGRAPH | PERFORMANCE THRESHOLD |
| --- | --- | --- |
| 1. Ensure all systems are maintained in an in-service condition. | 1.2.3 | During semi-annual inspection, 90% of systems shall operate function as designed. |
| 2. Must be inspected by fire department before leaving job site. | 1.2.5 | Shall contact fire department 100% of the time. |
| 3. Schedules | 1.2.7 | Schedule 90% of facilities by 15th of the month; variances shall be on time, the remaining 10% by the 20th |

SECTION III

GOVERNMENT FURNISHED PROPERTY AND SERVICES

3.1   RESERVED

SECTION IV

GENERAL INFORMATION

4.1  HOURS OF OPERATION

4.1.1  Duty Hours.  Normal hours to perform all services for Peterson AFB is from 7:00 a.m. to 4:00 p.m., Monday through Friday.  However, the contractor may be required to perform work after normal duty hours or on weekends.  Contract equipment storage is not permitted on Peterson AFB.

4.1.2  Holidays.  Cleaning work will not be required on the following holidays or any holiday observed in lieu thereof:

New Year’s Day (January)			Labor Day (September)

Martin Luther King Day (January)		Columbus Day (October)

President’s Day (February)			Veteran’s Day (November)

Memorial Day (May)				Thanksgiving Day (November)

Independence Day (July)			Christmas Day (December)

4.2  HAZARDOUS MATERIALS/WASTE.

4.2.1  Hazardous Materials.  In the accomplishment of this contract, the contractor shall use non-flammable, environmentally friendly, biodegradable products in accordance with (IAW) Air Force Instruction (AFI) 32-7080, Compliance Assurance and Pollution Prevention and AFI 32-7086, Hazardous Materials Management.  The contractor shall submit AF Form 3952, Chemical/Hazardous-Material Request Authorization and Material Safety Data Sheets (MSDS) for the products they are planning to use for this work to 21 SW HAZMART at least two weeks prior to beginning work.  The contractor is also responsible for obtaining and maintaining MSDS at the work site for any material used. The contractor will report all quantities of each chemical material used which is registered with a AF Form 3952 at least quarterly to the contracting officer or hazardous material pharmacy.  Contractor is responsible for containing, handling, and cleanup of all spills from this operation, e.g., paint, fuel, hazardous materials, etc.  Contractor is responsible for supplying equipment needed to perform the above.  Cost to dispose of spilled material and any other waste items resulting from the spill is the responsibility of the contractor.  All spills shall immediately be reported to the Base Fire Department at (719) 556-7354 or 556-7355.

4.2.2  Hazardous Waste.   Hazardous wastes are hazardous substances as defined in 40 CFR 261, or as defined by applicable state, local laws and regulations.  All hazardous waste generated from contract activities will be disposed of according to all federal and state regulations.  The contractor is responsible for making correct waste determinations for each waste stream.  The contractor is responsible for waste packing, labeling, manifesting, and transportation from accumulation site to ultimate disposal. The contractor will ensure the waste goes to a properly permitted treatment/disposal facility and that all manifests and any other required documentation are available to the Peterson AFB environmental flight.  The contractor will pay all costs associated with hazardous waste management and disposal.  The contractor will pay all fines/penalties assessed by state, local or federal agencies for hazardous waste laws violated by the contractor.  Contact the 21st CES Environmental Flight at 556-8318 immediately upon hazardous waste generation.

4.3  SAFETY.  All work shall be accomplished in accordance with specifications outlined in applicable Occupational Safety and Health Administration (OSHA) and Air Force Occupational Safety and Health Standards (AFOSH).  The Base Safety Office is the point of contact for all safety requirements and may conduct unannounced, periodic, safety inspections during contract service.

4.4  SECURITY REQUIREMENTS:   The contractor and all employees will comply with all Peterson AFB security requirements imposed by the installation commander at all times while on the premises to include not using cell phones while operating a vehicle on base.  Contractor will obtain necessary badge(s) required for access to Peterson AFB.

4.4.1  Badge Requests.

4.4.1.1  Contractor will send a letter to the contracting officer on company stationery which will include address, telephone number and contract number.  Employee(s) will be listed with full legal name(s), social security number(s) and duty hours requiring access to Peterson AFB.  After approval the letter will be on file with security forces squadron (SFS) for 30 days from the date on the contracting officer’s letter, after that it will be discarded.  Each contractor employee must obtain the necessary badge within the 30 day period.  When a badge is requested for a new employee an updated employee list must be sent to the contracting officer and the process starts over.

4.4.1.2  Contractor employee(s) will apply for individual identification badge(s) at the Peterson AFB SFS Visitor’s Center; Bldg. 1334 upon employment after access letter is on file with security forces.  Badges are processed Monday through Friday from 6:00 a.m. to 2:30 p.m.  Upon completion or termination of the contract, or termination of a contractor employee, surrender identification badge(s) to their contract manager who in-turn will surrender the badge (s) to security forces the following workday.

4.4.2  Vehicle Requirements.  Proper state vehicle registration, proof of insurance and a valid driver’s license are required to drive on Peterson AFB.  All commercial vehicles must enter through the East Gate (Marksheffel Road), primary search area for all commercial delivery vehicles.

4.5.  PERFORMANCE OF SERVICES DURING CRISIS DECLARED BY THE NATIONAL COMMAND AUTHORITY OR OVERSEAS COMBATANT COMMANDER.  According to Department of Defense Instruction (DODI) 3020.37, it is detemined that all services to be performed under this contract are essential for performance during crisis unless otherwise directed by an authorized government representative.

SECTION V

TECHNICAL EXHIBITS

TECHNICAL EXHIBIT 1

GOVERNMENT–FURNISHED PROPERTY/EQUIPMENT/SERVICES

| BUILDING NUMBER | ORGANIZATION/FACILITY | *MFG/SYSTEM | DRY/WET | REQUIRED INSPECTION |
| --- | --- | --- | --- | --- |
| 1 | HQ SPACE COMMAND Snack Bar | AN/R-102 | Wet | Semiannual |
| 1 | HQ SPACE COMMAND Snack Bar | AN/R-102 | Wet | Semiannual |
| 2 | NORTHCOM | AN/R-102 | Wet | Semiannual |
| 2 | NORTHCOM | AN/R-102 | Wet | Semiannual |
| 218 | Base Fire Department | AN/R-102 | Wet | Semiannual |
| 406 | Bowling Alley | F/4GS | Wet | Semiannual |
| 685 | HazMart | AN/SPA-50 | Dry | Semiannual |
| 686 | HazMart | AN/SPA-50 | Dry | Semiannual |
| 687 | HazMart | AN/SPA-50 | Dry | Semiannual |
| 688 | HazMart | AN/SPA-50 | Dry | Semiannual |
| 689 | HazMart | AN/SPA-50 | Dry | Semiannual |
| 691 | HazMart | P/MCH | Dry | Semiannual |
| 692 | HazMart | P/MCH | Dry | Semiannual |
| 693 | HazMart | P/MCH | Dry | Semiannual |
| 910 | Range Hood | G/1384-A | Wet | Semiannual |
| 1013 | Officer’s Club | K/HDR-50 | Wet | Semiannual |
| 1013 | Officer’s Club (Systems are combined) | WHDR-900 | Wet | Semiannual |
| 1013 | Officer’s Club | K/HDR-25 | Wet | Semiannual |
| 1054 | Golf Course | AN/R-102 | Wet | Semiannual |
| 1102 | Range Hood (2nd Floor) | G/1384-A | Wet | Semiannual |
| 1154 | Range Hood (2nd Floor) | G/1384-A | Wet | Semiannual |
| 1156 | Range Hood (2nd Floor) | G/1384-A | Wet | Semiannual |
| 1160 | Dining Facility | AN/R-102 | Wet | Semiannual |
| 1160 | Dining Facility | AN/R-102 | Wet | Semiannual |
| 1160 | Dining Facility | AN/R-102 | Wet | Semiannual |
| 1164 | Range Hood *34 Units (what does *34 Units mean?) | SG/PPA27-W | Wet | Semiannual |
| 1166 | Range Hood (1st Floor) | G/1384-A | Wet | Semiannual |
| 1246 | Bio-Environment (Kitchen) | Guardian III Model 6300-A | Wet | Semiannual |
| 1324 | Range Hood System | G/1384-A | Wet | Semiannual |
| 1324 | Range Hood System | G/1384-A | Wet | Semiannual |
| 1324 | Range Hood System | G/1384-A | Wet | Semiannual |
| 1324 | Range Hood System | G/1384-A | Wet | Semiannual |
| 1325 | Range Hood System | G/1384-A | Wet | Semiannual |
| 1330 | CE HazMat | P/MCH | Dry | Semiannual |
| 1332 | CE HazMat | P/MCH | Dry | Semiannual |

TECHNICAL EXHIBIT 1

GOVERNMENT–FURNISHED PROPERTY/EQUIPMENT/SERVICES (CONT’D)

| BUILDING NUMBER | ORGANIZATION/FACILITY | *MFG/SYSTEM | WET/DRY | REQUIRED INSPECTION |
| --- | --- | --- | --- | --- |
| 1410 | Base Chapel | AN/R-102 | Dry | Semiannual |
| 1470 | Services (Cafeteria) | AN/ R-102 | Wet | Semiannual |
| 1525 | Child Development Center (Annex) | P/MCH | Wet | Semiannual |
| 1555 | Youth Center | AN/R-102 | Wet | Semiannual |
| 1041 | MilStar Generator | IN/System | Gas Agent | Semiannual |
| 2017 | Base Exchange, Charlie’s | AN/System | Wet | Semiannual |
| 2017 | Base Exchange, Taco Bell | AN/System | Wet | Semiannual |
| 2017 | Base Exchange, Manchu Woc | AN/System | Wet | Semiannual |
| 2017 | Base Exchange, Anthony’s | AN/System | Wet | Semiannual |
| 2019 | Commissary, Deli | AN/System | Wet | Semiannual |
| 2025 | Cafeteria | AN/System | Wet | Semiannual |

* NOTE:  Spelling for acronyms used under MFG/SYSTEM Column are as follows:

AM	Amerex

AN	Ansul

G	Guardian

IN	Intergen

P	PyroChem Inc.

RG	Range Guard

SG	Safety Gourmet

TECHNICAL EXHIBIT 2

APPLICABLE PUBLICATION, CODES, STANDARDS AND FORMS

Documents applicable to this SOW are listed below.  The contractor is obligated to follow those listed and only to the extent stated in the SOW.  It is the contractor’s responsibility to ensure that all publications in his or her possession are up to date.  Publications are available at http://www.e-publishing.af.mil/  Website will show the most current versions of the publication.

| PUBLICATIONS | TITLE AND APPLICABLE PARAGRAPH(S) | SOW REFRENCE |
| --- | --- | --- |
| AFI 32-7080 | Compliance Assurance and Pollution Prevention | 4.3.1 |
| AFI 32-7086 | Hazardous Materials Management Section 2.5.5. HAZMAT Determination and Authorization Procedures for Contractors Paragraphs 2.5.5.2.; 2.5.5.2.;1; 2.5.5.2.2.; 2.5.5.2.3.; 2.5.5.2.4.; 2.5.5.2.5.; 2.5.5.2.6.; 2.5.5.2.7.; 2.5.5.2.8.; 2.5.5.2.9. | 4.3.1 |
| AFOSH 91-501 | Air Force Consolidated Occupational Safety Standard Section 6.2.2.2.3 | 4.4 |
| American Water Works Association | Standard 601 | 3.1.2 |
| Article 12 | Hazardous Cross-Connection Regulatory Requirements | 3.1.1 |
| OSHA | Occupational Health and Safety Administration | 4.4 |
| NFPA 17 | Standard For Dry Chemical Extinguishing Systems | 1.1 |
| NFPA 17A | Standard For Wet Chemical Extinguishing Systems | 1.1 |
| NFPA 70 | National Electric Code | 1.1 |
| NFPA 72 | National Fire Alarm Code | 1.1 |
| NEPA 96 | Standard for Ventilation Control and Fire Protection of Commercial Cooking Operations Section 11.4 | 1.1 |
| 29 CFR |  | 1.1 |
| 40 CFR |  | 1.1 |