| SOLICITATION/CONTRACT/ORDER FOR COMMERCIAL ITEMS Offeror to Complete Blocks 12, 17, 23, 24, & 30 | 1. Requisition Number | PAGE 1 OF | 61 |
| --- | --- | --- | --- |
|  | S227470A,B,C |  |  |
| 2. Contract No. | 3. Award/Effective Date | 4. Order Number | 5. Solicitation Number | 6. Solicitation Issue Date |
|  |  |  | 843100-03-R-2051 | June 3, 2003 |
| 7. For Solicitation Information Call: | a. Name bweaver | b. Telephone Number (No collect calls) | 8. Offer Due Date/Local Time |
|  | booker.weaver@dc.afrh.gov | 202-730-3558 | Jun 23, 2003 / 12:00 PM |
| 9. Issued By | Code USSAH-1 | 10. This Acquisition is | 11. Delivery for FOB Destination Unless Block is Marked. | 12. Discount Terms |
| AFRH-W/CONTRACTING DIV BLDG #74 3700 N CAPITOL STREET NW WASHINGTON, DC 20317-0002 |  | X | Unrestricted |  |  |
|  |  |  | Set-Aside % for |  | X | See Schedule |  |
|  |  |  | Small Business |  | 13a. This contract is a rated order under DPAS (15 CFR 700) |
|  |  |  | HubZone Small Business |  |  |
|  |  |  | 8(A) | 13b. Rating |
|  | NAICS: | 811310 | 14. Method of Solicitation |
|  | Size Standard: |  |  |  | RFQ |  | IFB | X | RFP |
| 15. Deliver To | Code USSAH-4 | 16. Administered By | Code |
| SEE SCHEDULE |  |
| 17a. Contractor/Offeror | Code Facility Code | 18a. Payment Will Be Made By | Code |
| Telephone No. | TIN: |  |
| 17b. Check if Remittance is Different and Put Such Address in Offer. | 18b. Submit Invoices to Address Shown in Block 18a Unless Box Below is Checked. |
|  |  |  | See Addendum. |
| 19. ITEM NO. | 20. SCHEDULE OF SUPPLIES/SERVICES | 21. QUANTITY | 22. UNIT | 23. UNIT PRICE | 24. AMOUNT |
|  | PROVIDE ALL NECESSARY LABOR, PARTS, AND EQUIPMENT TO PERFORM MAINTENANCE SERVICE FOR INSPECTION, CLEANING, ADJUSTING, TESTING AND CALIBRATING THE HIGH VOLTAGE EQUIPMENT FOR THE PERIOD 1 JULY 2003 THROUGH 30 JUNE 2003. QUESTIONS REGARDING THIS SOLICITATION SHALL BE SUBMITTED TO THE CONTRACTING SPECIALIST ON OR BEFORE JUNE 16, 2003. A SITE VISIT IS SCHEDULED FOR 10:30 AM ON JUNE 18, 2003 AT THE AFRH-W. ATTENDEES WILL MEET IN BLDG #73 CONFERENCE ROOM . PLEASE CONTACT BOOKER WEAVER @ 202-730-3558 WITH THE NAME OF THE ORGANIZATION AND ATTENDEES. |  |  |  |  |
|  | ANNUAL MAINTENANCE ON THE FOLLOWING HIGH VOLTAGE EQUIPMENT FOR THE PERIOD 1 JULY 2003 (OR DATE OF AWARD, IF LATER) THROUGH 30 JUNE 2003 |  |  |  |  |
| 0001 | MAIN SUBSTATION - BLDG. #71 | 1 | JB | ______________ | ______________ |
| 0002 | VAULT T-2 GRANT BLDG.#18, EXCLUDING SIX LOW VOLTAGE BREAKERS. | 1 | JB | ______________ | ______________ |
| 0003 | VAULT T-3 NORTH CONVERTOR BLDG. #28 | 1 | JB | ______________ | ______________ |
| 0004 | VAULT T-6 STOREHOUSE BLDG. #74 | 1 | JB | ______________ | ______________ |
| 0005 | VAULT T-7 SCOTT BLDG. #80 (GROUP A) | 1 | JB | ______________ | ______________ |
| 0006 | VAULT T-7 SCOTT BLDG. #80 (GROUP B) (TO BE PERFORMED IN THE OFF COOLING SEASON) | 1 | JB | ______________ | ______________ |
| 0007 | VAULT T-7 SCOTT BLDG. #80 (GROUP C) (TO BE PERFORMED IN THE OFF COOLING SEASON) | 1 | JB | ______________ | ______________ |
| 0008 | VAULT T-8 PIPES BLDG. #64, EXCLUDING 21 (TWENTY-ONE) LOW VOLTAGE BREAKERS THIS FISCAL YEAR. | 1 | JB | ______________ | ______________ |
| 0009 | VAULT T-9 HEATING PLANT BLDG. #46 EXCLUDING 12 (TWELVE) LOW VOLTAGE BREAKERS THIS FISCAL YEAR. | 1 | JB | ______________ | ______________ |
| 0010 | VAULT T-10 SHERIDAN BLDG. #17, EXCLUDING THIRTY LOW VOLTAGE BREAKERS. | 1 | JB | ______________ | ______________ |
| 0011 | VAULT T-11 SHERIDAN BLDG. #17 | 1 | JB | ______________ | ______________ |
| 0012 | VAULT T-12 AUTOCRAFT PADMOUNT TRANSFORMER, BLDG #69 | 1 | JB | ______________ | ______________ |
| 0012A | VAULT T-12 NO LOAD BREAK FUSED OIL SWITCH | 1 | JB | ______________ | ______________ |
| 0013 | HYPOT CABLES | 9 | JB | ______________ | ______________ |
| 0014 | MAT & GLOVE TESTING, TO BE PERFORMED DURING THE MONTHS OF FEB AND AUG. | 2 | JB | ______________ | ______________ |
| 0015 | VAULT T-14 LAGARD BLDG #56, EXCLUDING TWELVE LOW VOLTAGE BREAKERS. SOME PORTIONS OF WORK LISTED UNDER LINE ITEMS #0001 THROUGH #0015 MAY REQUIRE PERFORMANCE AT OTHER THAN NORMAL WORKING HOURS (OVERTIME). INSERT IN LINE ITEM #0016 THE ADDITIONAL COST COST PER MANHOUR, i.e. the difference between straight time and overtime, THAT WOULD BE APPLICABLE IF SUCH BECOMES NECESSARY | 1 | JB | ______________ | ______________ |
| 0016 | MAINTENANCE RATE FOR SERVICE PROVIDED AFTER 4:00 P.M. MONDAY THROUGH FRIDAY OR ON SATURDAY OR SUNDAY. MUST BE COORDINATED WITH THE COR/ACOR PRIOR TO SCHEDULING (NOT TO EXCEED 48 HOURS) THE FOLLOWING LINE ITEMS ARE TO BE PROVIDED ONLY WHEN CALLED FOR BY THE CONTRACTING OFFICER'S REP (COR) OR THE ALTERNATE COR (ACOR) DURING THE PERIOD 1 JULY 2003 (OR DATE OF AWARD, IF LATER) THROUGH 30 JUNE 2004. PRIOR TO MAKING CALL, COR IS TO ASSURE THAT FUNDS ARE AVAILABLE. | 60 | HR | ______________ | ______________ |
| 0017 | EMERGENCY SERVICES: MONDAY THROUGH FRIDAY, 7:30 A.M. THROUGH 4:00 P.M. (EXCEPT GOVERNMENT OBSERVED HOLIDAYS) TO BE BILLED AT $_______ PER HOUR | 15 | HR | ______________ | ______________ |
| 0018 | EMERGENCY SERVICES: OTHER THAN HOURS/DAY STATED IN CLIN 0017, TO BE BILLED AT $__________ PER HOUR. NOTE: PAYMENT FOR SERVICES UNDER LINE ITEM #0017 & #0018 WILL BE MADE FOR "ON-SITE" LABOR TIME ONLY. HOURLY RATES SHALL INCLUDE ALL OVERHEAD, OFFICE SUPPORT, SUPERVISION AND MANAGEMENT COSTS, FRINGES, TAXES, INSURANCE, NECESSRY VEHICLES AND EQUIPMENT THAT ARE REQUIRED FOR EFFORT. NO ADDITIONAL PAYMENT WILL BE MADE IN CONNECTION WITH LABOR COSTS. CONTRACTOR MUST REPORT TO COR OR ACOR UPON ARRIVAL AND DEPARTURE FROM THE GROUNDS OF THE ARMED FORCES RETIREMENT HOME-WASHINGTON. CONTRACTOR SHALL PROVIDE A LIST OF PERSONNEL WHO WORKED THAT DAY AND INCLUDE THE NUMBER OF ACTUAL HOURS WORKED FOR EACH. | 10 | HR | ______________ | ______________ |
| 0019 | AUTHORIZED EQUIPMENT REPAIRS. CONTRACTOR MUST HAVE APPROVAL FROM COR PRIOR TO MAKING REPAIRS. NOTE: REPAIRS SHALL BE BILLED AT CONTRACTOR'S COST. EVIDENCE OF COST SHALL BE SUBMITTED WITH INVOICE. | 5 | JB | ______________ | ______________ |
| 0019A | PARTS, MATERIALS, AND ANY TRANSPORTATION CHARGES THAT MAY BE REQUIRED TO PERFORM THE ABOVE SERVICES SHALL BE BILLED AT CONTRACTOR'S COST. NOTE: EVIDENCE OF COST SHALL BE SUBMITTED WITH INVOICE. | 5 | JB | ______________ | ______________ |
| 0019B | HOURLY RATE FOR APPROVED MAINTAINENCE REPAIRS DURING OFF HOUR . | 40 | HR | ______________ | ______________ |
| 0019C | HOURLY COST FOR STRAIGHT TIME WORK ON MAINTAINENCE REPAIRS AUTHORIZED BY THE COR/ACOR. | 60 | HR | ______________ | ______________ |
|  | 1ST OPTION YEAR: (1 JULY2004 THROUGH 30 JUNE 2005) ANNUAL MAINTENANCE SERVICE ON THE FOLLOWING HIGH VOLTAGE EQUIPMENT |  |  |  |  |
| 0020 | MAIN SUBSTATION - BLDG. #71 | 1 | JB | ______________ | ______________ |
| 0021 | VAULT T-2 GRANT BLDG.#18, EXCLUDING SIX LOW VOLTAGE BREAKERS. | 1 | JB | ______________ | ______________ |
| 0022 | VAULT T-3 NORTH CONVERTOR BLDG. #28 | 1 | JB | ______________ | ______________ |
| 0023 | VAULT T-6 STOREHOUSE BLDG. #74 | 1 | JB | ______________ | ______________ |
| 0024 | VAULT T-7 SCOTT BLDG. #80, (GROUP A) EXCLUDING 31 (THIRTY-ONE) LOW VOLTAGE BREAKERS, AND 3 (THREE) 13-K OIL JUNCTIONS. | 1 | JB | ______________ | ______________ |
| 0025 | VAULT T-7 SCOTT BLDG. #80 (GROUP B) (TO BE PERFORMED IN THE OFF COOLING SEASON) | 1 | JB | ______________ | ______________ |
| 0026 | VAULT T-7 SCOTT BLDG. #80 (GROUP C) (TO BE PERFORMED IN THE OFF COOLING SEASON) | 1 | JB | ______________ | ______________ |
| 0027 | VAULT T-8 PIPES BLDG. #64 | 1 | JB | ______________ | ______________ |
| 0028 | VAULT T-9 HEATING PLANT BLDG. #46 | 1 | JB | ______________ | ______________ |
| 0029 | VAULT T-10 SHERIDAN BLDG. #17, EXCLUDING THIRTY LOW VOLTAGE BREAKERS. | 1 | JB | ______________ | ______________ |
| 0030 | VAULT T-11 SHERIDAN BLDG. #17 | 1 | JB | ______________ | ______________ |
| 0031 | VAULT T-12 AUTOCRAFT PADMOUNT TRANSFORMER, BLDG #69 | 1 | JB | ______________ | ______________ |
| 0032 | HYPOT CABLES | 9 | JB | ______________ | ______________ |
| 0033 | MAT & GLOVE TESTING | 2 | JB | ______________ | ______________ |
| 0034 | VAULT T-14 LAGARD BLDG #56 SOME PORTIONS OF WORK LISTED UNDER LINE ITEMS #0020 THROUGH #0033 MAY REQUIRE PERFORMANCE AT OTHER THAN NORMAL WORKING HOURS (OVERTIME). INSERT IN LINE ITEM #0036 THE ADDITIONAL COST COST PER MANHOUR, i.e. the difference between straight time and overtime, THAT WOULD BE APPLICABLE IF SUCH BECOMES NECESSARY | 1 | JB | ______________ | ______________ |
| 0035 | MAINTENANCE RATE FOR SERVICE PROVIDED AFTER 4:00 P.M. MONDAY THROUGH FRIDAY OR ON SATURDAY OR SUNDAY. MUST BE COORDINATED WITH THE COR/ACOR PRIOR TO SCHEDULING (NOT TO EXCEED 48 HOURS) THE FOLLOWING LINE ITEMS ARE TO BE PROVIDED ONLY WHEN CALLED FOR BY THE CONTRACTING OFFICER'S (COR) OR THE ALTERNATE COR (ACOR) PRIOR TO MAKING CALL, COR IS TO ASSURE THAT FUNDS ARE AVAILABLE. | 60 | HR | ______________ | ______________ |
| 0036 | EMERGENCY SERVICES: MONDAY THROUGH FRIDAY, 7:30 A.M. THROUGH 4:00 P.M. (EXCEPT GOVERNMENT OBSERVED HOLIDAYS) TO BE BILLED AT $_______ PER HOUR | 15 | HR | ______________ | ______________ |
| 0037 | EMERGENCY SERVICES: OTHER THAN HOURS/DAY STATED IN LINE ITEM # 0036, TO BE BILLED AT $__________ PER HOUR. NOTE: PAYMENT FOR SERVICES UNDER LINE ITEM #0035 & #0036 WILL BE MADE FOR "ON-SITE" LABOR TIME ONLY. HOURLY RATES SHALL INCLUDE ALL OVERHEAD, OFFICE SUPPORT, SUPERVISION AND MANAGEMENT COSTS, FRINGES, TAXES, INSURANCE, NECESSRY VEHICLES AND EQUIPMENT THAT ARE REQUIRED FOR EFFORT. NO ADDITIONAL PAYMENT WILL BE MADE IN CONNECTION WITH LABOR COSTS. CONTRACTOR MUST REPORT TO COR OR ACOR UPON ARRIVAL AND DEPARTURE FROM THE GROUNDS OF THE ARMED FORCES RETIREMENT HOME-WASHINGTON. CONTRACTOR SHALL PROVIDE A LIST OF PERSONNEL WHO WORKED THAT DAY AND INCLUDE THE NUMBER OF ACTUAL HOURS WORKED FOR EACH. | 10 | HR | ______________ | ______________ |
| 0038 | AUTHORIZED EQUIPMENT REPAIRS. CONTRACTOR MUST HAVE APPROVAL FROM COR PRIOR TO MAKING REPAIRS. NOTE: REPAIRS SHALL BE BILLED AT CONTRACTOR'S COST. EVIDENCE OF COST SHALL BE SUBMITTED WITH INVOICE. | 5 | JB | ______________ | ______________ |
| 0038A | PARTS, MATERIALS, AND ANY TRANSPORTATION CHARGES THAT MAY BE REQUIRED TO PERFORM THE ABOVE SERVICES SHALL BE BILLED AT CONTRACTOR'S COST. NOTE: EVIDENCE OF COST SHALL BE SUBMITTED WITH INVOICE. | 5 | JB | ______________ | ______________ |
| 0038B | HOURLY RATE FOR APPROVED MAINTAINENCE REPAIRS, DURING OFF HOURS. | 40 | HR | ______________ | ______________ |
| 0038C | HOURLY COST FOR STRAIGHT TIME WORK ON MAINTAINENCE REPAIRS AUTHORIZED BY THE COR/ACOR. | 60 | HR | ______________ | ______________ |
|  | 2ND OPTION YEAR: (1 JULY 2005 THROUGH 30 JUNE 2006) ANNUAL MAINTENANCE SERVICE ON THE FOLLOWING HIGH VOLTAGE EQUIPMENT |  |  |  |  |
| 0039 | MAIN SUBSTATION - BLDG. #71 | 1 | JB | ______________ | ______________ |
| 0040 | VAULT T-2 GRANT BLDG.#18 | 1 | JB | ______________ | ______________ |
| 0041 | VAULT T-3 NORTH CONVERTOR BLDG. #28 | 1 | JB | ______________ | ______________ |
| 0042 | VAULT T-6 STOREHOUSE BLDG. #74 | 1 | JB | ______________ | ______________ |
| 0043 | VAULT T-7 SCOTT BLDG. #80 (GROUP A) EXCLUDING 31 (THIRTY-ONE) LOW VOLTAGE BREAKERS, AND 3 (THREE) 13-K OIL JUNCTIONS. | 1 | JB | ______________ | ______________ |
| 0044 | VAULT T-7 SCOTT BLDG. #80X(GROUP B) (TO BE PERFORMED IN THE OFF COOLING SEASON) | 1 | JB | ______________ | ______________ |
| 0045 | VAULT T-7 SCOTT BLDG. #80 (GROUP C) (TO BE PERFORMED IN THE OFF COOLING SEASON) | 1 | JB | ______________ | ______________ |
| 0046 | VAULT T-8 PIPES BLDG. #64 EXCLUDING 21 (TWENTY-ONE) LOW VOLTAGE BREAKERS. | 1 | JB | ______________ | ______________ |
| 0047 | VAULT T-9 HEATING PLANT BLDG. #46 EXCLUDING 12 (TWELVE) LOW VOLTAGE BREAKERS. | 1 | JB | ______________ | ______________ |
| 0048 | VAULT T-10 SHERIDAN BLDG. #17 | 1 | JB | ______________ | ______________ |
| 0049 | VAULT T-11 SHERIDAN BLDG. #17 | 1 | JB | ______________ | ______________ |
| 0050 | VAULT T-12 AUTOCRAFT PADMOUNT TRANSFORMER, BLDG #69 | 1 | JB | ______________ | ______________ |
| 0051 | HYPOT CABLES | 9 | JB | ______________ | ______________ |
| 0052 | MAT & GLOVE TESTING TO BE PERFORMED DURING THE MONTHS OF FEB AND AUG. | 2 | JB | ______________ | ______________ |
| 0053 | VAULT T-14 LAGARD BLDG #56, EXCLUDING TWELVE LOW VOLTAGE BREAKERS. SOME PORTIONS OF WORK LISTED UNDER LINE ITEMS #0039 THROUGH #0052 MAY REQUIRE PERFORMANCE AT OTHER THAN NORMAL WORKING HOURS (OVERTIME). INSERT IN LINE ITEM #0056 THE ADDITIONAL COST COST PER MANHOUR, i.e. the difference between straight time and overtime, THAT WOULD BE APPLICABLE IF SUCH BECOMES NECESSARY | 1 | JB | ______________ | ______________ |
| 0054 | MAINTENANCE RATE FOR SERVICE PROVIDEDAFTER 4:00 P.M. MONDAY THROUGH FRIDAYOR ON SATURDAY OR SUNDAY. MUST BE COORDINATED WITH THE COR/ACOR PRIOR TO SCHEDULING (NOT TO EXCEED 48 HOURS) THE FOLLOWING LINE ITEMS ARE TO BE PROVIDED ONLY WHEN CALLED FOR BY THE CONTRACTING OFFICER'S (COR) OR THE ALTERNATE COR (ACOR). PRIOR TO MAKING CALL, COR IS TO ASSURE THAT FUNDS ARE AVAILABLE. | 40 | HR | ______________ | ______________ |
| 0055 | EMERGENCY SERVICES: MONDAY THROUGH FRIDAY, 7:30 A.M. THROUGH 4:00 P.M. (EXCEPT GOVERNMENT OBSERVED HOLIDAYS) TO BE BILLED AT $_______ PER HOUR | 15 | HR | ______________ | ______________ |
| 0056 | EMERGENCY SERVICES: OTHER THAN HOURS/DAY STATED IN LINE ITEM #0055, TO BE BILLED AT $__________ PER HOUR. NOTE: PAYMENT FOR SERVICES UNDER LINE ITEM #0054 & #0055 WILL BE MADE FOR "ON-SITE" LABOR TIME ONLY. HOURLY RATES SHALL INCLUDE ALL OVERHEAD, OFFICE SUPPORT, SUPERVISION AND MANAGEMENT COSTS, FRINGES, TAXES, INSURANCE, NECESSRY VEHICLES AND EQUIPMENT THAT ARE REQUIRED FOR EFFORT. NO ADDITIONAL PAYMENT WILL BE MADE IN CONNECTION WITH LABOR COSTS. CONTRACTOR MUST REPORT TO COR OR ACOR UPON ARRIVAL AND DEPARTURE FROM THE GROUNDS OF THE ARMED FORCES RETIREMENT HOME-WASWHINGTON. CONTRACTOR SHALL PROVIDE A LIST OF PERSONNEL WHO WORKED THAT DAY AND INCLUDE THE NUMBER OF ACTUAL HOURS WORKED FOR EACH. | 10 | HR | ______________ | ______________ |
| 0057 | AUTHORIZED EQUIPMENT REPAIRS. CONTRACTOR MUST HAVE APPROVAL FROM COR PRIOR TO MAKING REPAIRS. NOTE: REPAIRS SHALL BE BILLED AT CONTRACTOR'S COST. EVIDENCE OF COST SHALL BE SUBMITTED WITH INVOICE. | 5 | JB | ______________ | ______________ |
| 0057A | PARTS, MATERIALS, AND ANY TRANSPORTATION CHARGES THAT MAY BE REQUIRED TO PERFORM THE ABOVE SERVICES - SHALL BE BILLED AT CONTRACTOR'S COST. NOTE: EVIDENCE OF COST SHALL BE SUBMITTED WITH INVOICE. | 5 | JB | ______________ | ______________ |
| 0057B | HOURLY RATE FOR APPROVED MAINTAINENCE REPAIRS DURING OFF HOURS. | 40 | HR | ______________ | ______________ |
| 0057C | HOURLY COST FOR STRAIGHT TIME WORK ON MAINTAINENCE REPAIRS AUTHORIZED BY THE COR/ACOR. | 60 | HR | ______________ | ______________ |

SECTION C - DESCRIPTION/SPECIFICATIONS/WORK STATEMENT	11

C.1  STATEMENT OF WORK H:\sow.hvelectric1.wpd	11

SECTION E - INSPECTION AND ACCEPTANCE	21

E.1  52.246-4 INSPECTION OF SERVICES--FIXED-PRICE (AUG 1996)	21

SECTION H - SPECIAL CONTRACT REQUIREMENTS	22

H.1  SPECIAL CONTRACT REQUIREMENTS H:\SOL 03-R-2051, SEC H1.doc	22

SECTION I - CONTRACT CLAUSES	32

I.1  52.202-1 DEFINITIONS (DEC 2001)	32

I.2  52.203-3 GRATUITIES (APR 1984)	32

I.3  52.203-5 COVENANT AGAINST CONTINGENT FEES (APR 1984)	32

I.4  52.203-6 RESTRICTIONS ON SUBCONTRACTOR SALES TO THE GOVERNMENT (JUL 1995)	32

I.5  52.203-7 ANTI-KICKBACK PROCEDURES (JUL 1995)	32

I.6  52.203-10 PRICE OR FEE ADJUSTMENT FOR ILLEGAL OR IMPROPER ACTIVITY (JAN 1997)	32

I.7  52.203-12 LIMITATION ON PAYMENTS TO INFLUENCE CERTAIN FEDERAL TRANSACTIONS (JUN 1997)	32

I.8  52.204-4 PRINTED OR COPIED DOUBLE-SIDED ON RECYCLED PAPER (AUG 2000)	32

I.9  52.209-6 PROTECTING THE GOVERNMENT'S INTEREST WHEN SUBCONTRACTING WITH CONTRACTORS DEBARRED, SUSPENDED, OR PROPOSED FOR DEBARMENT (JUL 1995)	32

I.10  52.215-2 AUDIT AND RECORDS--NEGOTIATION (JUNE 1999)	32

I.11  52.219-6 NOTICE OF TOTAL SMALL BUSINESS SET-ASIDE (JUL 1996)	32

I.12  52.219-8 UTILIZATION OF SMALL BUSINESS CONCERNS (OCT 2000)	32

I.13  52.219-9 I SMALL BUSINESS SUBCONTRACTING PLAN (JAN 2002)--ALTERNATE I (OCT 2001)	32

I.14  52.219-14 LIMITATIONS ON SUBCONTRACTING (DEC 1996)	32

I.15  52.222-1 NOTICE TO THE GOVERNMENT OF LABOR DISPUTES (FEB 1997)	32

I.16  52.222-3 CONVICT LABOR (AUG 1996)	32

I.17  52.222-4 CONTRACT WORK HOURS AND SAFETY STANDARDS ACT--OVERTIME COMPENSATION (SEPT 2000)	32

I.18  52.222-20 WALSH-HEALEY PUBLIC CONTRACTS ACT (DEC 1996)	32

I.19  52.222-26 EQUAL OPPORTUNITY (APR 2002)	32

I.20  52.222-28 {52.222-28}  [RESERVED]	33

I.21  52.222-35 52.222-35 Equal Opportunity for Special Disabled Veterans, Veterans of the Vietnam Era, and Other Eligible Veterans. [Dec 2001]	33

I.22  52.222-36 AFFIRMATIVE ACTION FOR WORKERS WITH DISABILITIES (JUN 1998)	33

I.23  52.222-37 EMPLOYMENT REPORTS ON SPECIAL DISABLED VETERANS, VETERANS OF THE VIETNAM ERA, AND OTHER ELIGIBLE VETERANS (DEC 2001)	33

I.24  52.222-41 SERVICE CONTRACT ACT OF 1965, AS AMENDED (MAY 1989)	33

I.25  52.222-43 FAIR LABOR STANDARDS ACT AND SERVICE CONTRACT ACT--PRICE ADJUSTMENT (MULTIPLE YEAR AND OPTION CONTRACTS) (MAY 1989)	33

I.26  52.222-47 SERVICE CONTRACT ACT (SCA) MINIMUM WAGES AND FRINGE BENEFITS (MAY 1989)	33

I.27  52.223-2 {52.223-2}  [RESERVED]	33

I.28  52.223-3 I HAZARDOUS MATERIAL IDENTIFICATION AND MATERIAL SAFETY DATA (JAN 1997)-- ALTERNATE I (JUL 1995)	33

I.29  52.223-6 DRUG-FREE WORKPLACE (MAY 2001)	33

I.30  52.224-1 PRIVACY ACT NOTIFICATION (APR 1984)	33

I.31  52.224-2 PRIVACY ACT (APR 1984)	33

I.32  52.225-11 BUY AMERICAN ACT--CONSTRUCTION   MATERIALS UNDER TRADE AGREEMENTS (July 2002)	33

I.33  52.227-1 AUTHORIZATION AND CONSENT (JUL 1995)	33

I.34  52.227-2 NOTICE AND ASSISTANCE REGARDING PATENT AND COPYRIGHT INFRINGEMENT (AUG 1996)	33

I.35  52.228-5 INSURANCE--WORK ON A GOVERNMENT INSTALLATION (JAN 1997)	33

I.36  52.229-4 FEDERAL, STATE, AND LOCAL TAXEs (State and Local Adjustments) (April 2003)	33

I.37  52.232-1 PAYMENTS (APR 1984)	34

I.38  52.232-8 DISCOUNTS FOR PROMPT PAYMENT (FEB 2002)	34

I.39  52.232-11 EXTRAS (APR 1984)	34

I.40  52.232-17 INTEREST (JUNE 1996)	34

I.41  52.232-19 AVAILABILITY OF FUNDS FOR THE NEXT FISCAL YEAR (APR 1984)	34

I.42  52.232-23 ASSIGNMENT OF CLAIMS (JAN 1986)	34

I.43  52.232-25 PROMPT PAYMENT (FEB 2002)	34

I.44  52.233-1 DISPUTES (JUL 2002)	34

I.45  52.233-3 PROTEST AFTER AWARD (AUG 1996)	34

I.46  52.237-2 PROTECTION OF GOVERNMENT BUILDINGS, EQUIPMENT, AND VEGETATION (APR 1984)	34

I.47  52.237-3 CONTINUITY OF SERVICES (JAN 1991)	34

I.48  52.242-13 BANKRUPTCY (JUL 1995)	34

I.49  52.243-1 I CHANGES--FIXED-PRICE (AUG 1987)--ALTERNATE I (APR 1984)	34

I.50  52.246-20 WARRANTY OF SERVICES (APR 1984)	34

I.51  52.246-25 LIMITATION OF LIABILITY--SERVICES (FEB 1997)	34

I.52  52.249-2 TERMINATION FOR CONVENIENCE OF THE GOVERNMENT (FIXED-PRICE) (SEP 1996)	34

I.53  52.249-8 DEFAULT (FIXED-PRICE SUPPLY AND SERVICE) (APR 1984)	34

I.54  52.253-1 COMPUTER GENERATED FORMS (JAN 1991)	34

I.55  52.216-18 ORDERING (OCT 1995)	34

I.56  52.216-21 REQUIREMENTS (OCT 1995)	35

I.57  52.216-21 I REQUIREMENTS (OCT 1995)--ALTERNATE I (APR 1984)	35

I.58  52.216-21 II REQUIREMENTS (OCT 1995)--ALTERNATE II (APR 1984)	36

I.59  52.216-21 III REQUIREMENTS (OCT 1995)--ALTERNATE III (OCT 1995)	37

I.60  52.216-22 INDEFINITE QUANTITY (OCT 1995)	37

I.61  52.217-8 OPTION TO EXTEND SERVICES (NOV 1999)	38

I.62  52.217-9 OPTION TO EXTEND THE TERM OF THE CONTRACT (MAR 2000)	38

I.63  52.222-42 STATEMENT OF EQUIVALENT RATES FOR FEDERAL HIRES (MAY 1989)	38

I.64  52.223-9 ESTIMATE OF PERCENTAGE OF RECOVERED MATERIAL CONTENT FOR EPA-DESIGNATED PRODUCTS (AUG 2000)	38

I.65  52.223-11 OZONE-DEPLETING SUBSTANCES (JUN 1996)	39

I.66  52.223-12 REFRIGERATION EQUIPMENT AND AIR CONDITIONERS (MAY 1995)	39

I.67  52.249-4 TERMINATION FOR CONVENIENCE OF THE GOVERNMENT (SERVICES) (SHORT FORM) (APR 1984)	39

SECTION J - LIST OF ATTACHMENTS	40

J.1  WAGE DETERMINATION H:\DBWageDeterm.htm	40

SECTION K - REPRESENTATIONS, CERTIFICATIONS AND OTHER STATEMENTS OF OFFERORS	51

K.1  52.203-11 CERTIFICATION AND DISCLOSURE REGARDING PAYMENTS TO INFLUENCE CERTAIN FEDERAL TRANSACTIONS (APR 1991)	51

K.2  52.204-3 TAXPAYER IDENTIFICATION (OCT 1998)	51

K.3  52.222-21 PROHIBITION OF SEGREGATED FACILITIES (FEB 1999)	51

K.4  52.203-2 CERTIFICATE OF INDEPENDENT PRICE DETERMINATION (APR 1985)	51

K.5  52.209-5 CERTIFICATION REGARDING DEBARMENT, SUSPENSION, PROPOSED DEBARMENT, AND OTHER RESPONSIBILITY MATTERS (DEC 2001)	51

K.6  52.215-6 PLACE OF PERFORMANCE BUSINESS (OCT 1997)	52

K.7  52.215-11 PRICE REDUCTION FOR DEFECTIVE COST OR PRICING DATA--MODIFICATIONS (OCT 1997)	53

K.8  52.219-1 SMALL BUSINESS PROGRAM REPRESENTATIONS (Apr 2002)	54

K.9  52.222-22 PREVIOUS CONTRACTS AND COMPLIANCE REPORTS (FEB 1999)	55

K.10  52.222-25 AFFIRMATIVE ACTION COMPLIANCE (APR 1984)	56

SECTION L - INSTRUCTIONS, CONDITIONS, AND NOTICES TO OFFERORS	57

L.1  52.215-5 FACSIMILE PROPOSALS (OCT 1997)	57

L.2  52.215-7 ANNUAL REPRESENTATIONS AND CERTIFICATIONS--NEGOTIATION (OCT 1997)	57

L.3  52.215-8 ORDER OF PRECEDENCE--UNIFORM CONTRACT FORMAT (OCT 1997)	57

L.4  52.215-9 CHANGES OR ADDITIONS TO MAKE-OR-BUY PROGRAM (OCT 1997)	57

L.5  52.215-10 PRICE REDUCTION FOR DEFECTIVE COST OR PRICING DATA (OCT 1997)	57

L.6  52.215-12 SUBCONTRACTOR COST OR PRICING DATA (OCT 1997)	57

L.7  52.215-13 SUBCONTRACTOR COST OR PRICING DATA--MODIFICATIONS (OCT 1997)	57

L.8  52.215-14 INTEGRITY OF UNIT PRICES (OCT 1997)	57

L.9  52.237-1 SITE VISIT (APR 1984)	57

L.10  52.204-6 DATA UNIVERSAL NUMBERING SYSTEM (DUNS) NUMBER (JUNE 1999)	57

L.11  52.216-1 TYPE OF CONTRACT (APR 1984)	57

L.12  52.233-2 SERVICE OF PROTEST (AUG 1996)	58

L.13  52.252-3 ALTERATIONS IN SOLICITATION (APR 1984)	58

L.14  52.252-4 ALTERATIONS IN CONTRACT (APR 1984)	58

L.15  52.252-5 AUTHORIZED DEVIATIONS IN PROVISIONS (APR 1984)	58

L.16  52.252-6 AUTHORIZED DEVIATIONS IN CLAUSES (APR 1984)	58

SECTION M - EVALUATION FACTORS FOR AWARD	59

M.1  EVALUATION FACTORS H:\HIVOLTAGE SEC M.doc	59

M.2  52.217-4 EVALUATION OF OPTIONS EXERCISED AT TIME OF CONTRACT AWARD (JUN 1988)	60

M.3  52.217-5 EVALUATION OF OPTIONS (JUL 1990)	60

C.1  STATEMENT OF WORK

SCOPE OF WORK HIGH VOLTAGE EQUIPMENT

1. Maintenance

Complete maintenance program of all electric service and

distribution equipment covered under this contract will be performed and completed every year.

2.  Functional Test

A completed functional test of all power and control

systems, electrical and mechanical shall be done every year, as per manufactures specifications and this scope of work but is not limited to either.

3. Liquid Filled Transformers

A. Visual and Mechanical Inspection

1. Inspect for physical damage, cracked insulator, leaks, tightness of connections,

and general mechanical and electrical conditions.

2. Verify proper auxiliary device operations.

3. Check tightness of accessible bolted electrical connections.

4. Verify proper liquid level in all tanks and bushings. 5. Perform specific inspections and mechanical       tests as recommended by the manufacture.

6. Verify proper equipment grounding.

7. Sample for test shall be drawn from the bottom of the tank from all liquid filled

units.

8. Sample insulating liquid in accordance with ASTM-D- 923. Sample shall be laboratory tested for:

a. Dielectric break-down voltage: ASTM D-877 or ASTM D-18l6.

b. Acid neutralization number ASTM D-974.

c. Specific gravity: ASTM D-1298.

d. Interfacial tension: ASTM D-97l or ASTM D- 2285

e. Color: ASTM D-1500.

f. Visual Condition: ASTM D-1524

g. PPM water: ASTM D-1533. Required on 25kv or higher voltages and on all silicone filled units.

Results from all liquid type transformers shall be recorded and included in the

written report.

B. Electrical Tests

1. Performed insulation resistance test, winding - to - winding and windings to ground.

a. Test duration shall be for 10 minutes with resistance=s tabulated at 30 seconds, 1 minute, and 10 minutes.

b. Calculate dielectric absorption ratio and polarization index.

4. Dry Tye Transformers

A. Transformers shall be de-energize, air blown down and

vacuumed out. Visual inspection should be made of all connections and general

maintenance performed as needed,as per manufactures specifications.

B. Results from all dry type transformers shall be recorded and included 1n the written report   C. Perform insulation resistance test, winding-to-winding and windings-to-ground, utilizing a megohmeter with the test.

1. Test duration shall be for 10 minutes with

resistance=s tabulated at 30 seconds, 1 minute, and 10 minutes.

2. Dielectric absorption ratio and polarization index will be calculated.

5. Relay Maintenance

A. Visual and Mechanical Inspection

1. Inspect relays for physical damage, foreign material, and moisture.

2. Inspect, and clean cover gasket, cover glass,

spiral spring, disc clearance, contacts, and case shoring contacts if present.

3. Check mechanically for freedom of movement, proper travel, alignment, and tightness of mounting hardware and tap plugs.

4. Perform all tests in accordance with the existing conditions or as recommended by the USSAH.

B. Electrical Tests

1. Perform the following tests on the nominal settings specified by the USSAH;

2. Pick up parameters on each operating element.

3. Perform timing test at two (2) points on the time delay curve.

4. Pick up target and seal in units.

5. Special tests as required to check the operation

of restraint, directional and other elements shall be performed according to manufactures instruction manual.

C. Adjustments

1. The pick up and contact wipe shall be set as per specifications.

2. Contacts shall be cleaned with only a flexible burnishing tool.

3. All connections shall be checked.

4. Pick up and dropout test shall be performed as well as time tests.

5. Mechanical adjustment and visual inspection shall be performed on all relays.

6. Test results shall be included in written report.

6. Breaker Maintenance

A. All breakers shall be tested, lubricated, adjusted for proper fit, visually inspected for defects.

1. Check for proper tripping at set rating.

2. Trip units shall be tested for long time, short time, instantaneous, ground fault operations.

B. All draw-out breakers shall be checked for contact and insulation resistance.

C. Each breaker shall have its inspection and test results included in the written reports.

*NOTE: Power/Vac Vacuum Circuit Breakers shall be inspected and maintained as per the manufactures specification including but not limited to primary contact erosion, lubrication, insulation and interlock protection.

7. Network Protectors

A. Visual and Mechanical Inspections, Cleaning and Adjusting.

1. Observe clearances and uniformity of withdrawal.

2. Perform the internal inspection of the enclosure.

Visually check insulating components, current carrying parts, and the secondary disconnecting devices.

3. Observe that all protector parts including pins and

springs are properly secures. Check for appropriate

tightness of all electrical and mechanical connections. Follow all manufacture instructions for the adjustments, torque valves, and clearances.

4. Check for the presence, mounting and condition of the insulation barriers.

5. Remove the arc suppression cover and examine for cracks.

6. Inspect the main and arcing contacts for cleanliness smoothness of surface and alignment.

7. Slow close the protector, and observe that the sequence of arcing contacts operations is in accordance with the manufactures instructions.

8. Remove each network relay. Check all electrical

connections and components for appropriate tightness. Perform a friction check by operating each device. Clean contacts in accordance with approved procedures.

9. Inspect, clean, and tighten connections of auxiliary relays.

10. Check electrical connections of the auxiliary

switches, secondary disconnects, current transformers,

voltage transformers, control power transformers, fuse holders, closing motors, and shunt trip units.

B. Electric Test    rform insulation resistance tests at 1000 volts DC for one (1) minute across the contacts of each pole with the protector open, and from pole to pole and from pole to ground with the control wiring connected to the line and load side of the protector. Where applicable, remove solid state relays.

2. Perform a resistance test across the closed contracts of each pole 'or measure the millivolt drop at 1000 amperes.

3. Perform operational and relay calibration test with three phase voltage to the proper terminals of the protector. All settings and adjustments shall be in accordance with instructions from the USSAH.

Set and calibrate the master relay for the specified over voltage close and reverse current trip values.

5. Set and calibrate the phasing relay for the specified over voltage and closing values.

6. Set and calibrate the restraining relay for the specified time delay and instantaneous current trip values.

7. Confirm operating handle positions. In the handle open position, a closed protector shall open and remain open. In the handle closed position, the protector shall close and shall permit the relays to open the protector, but not re-close it. In the handle automatic position, the relays shall control the opening and closing protector operations.

8. After the operational test, record the number of operations registered on the counter.

8. Indicator Lamps

All indicator lamps shall be replace whether burning or not.

This includes but is not limited to, Network Protectors and Switchgear or Switchboard indicators.

9. Volt and AMP Meters

All volt and amp meters shall be tested and calibrated.

10. Infra Red Scanning

All switchboard, switches, conductor assemblies and buss ducts shall be scanned to locate any area of excessive heat on the mechanical connections hardware. All connections shall be tight to not exceed manufactures specifications or not to exceed torque ratings.

11. Hypot Cables

All medium voltage cables shall be hypot as per IEEE Standards. Hypotting shall be done by opening all transformers switches on each feeder breaker and conducting test from most convenient test point. Scheduling will have to be set up for such outages. Cable types are TCIC, Cross Link Poly XLT or EPR. Total of nine outgoing feeders.

Feeder # Approx. Feet Vaults

2 4000 T-9 -200, T-7 -2100, T10 -1700 3 3700 T-12 -600, T-2 -3200

4 1950 T-8 -2000, T-6 -800, T-14 -150 11 1800 T-8 -2000, T-6 -800

12 3100 T-3 -2500, T-12 -600

13 5700 T-7 -2100, T-10 -1700, T-11 -1900 18 1200 T-9 -200, T-12 -1000, T-14 -150 19 5600 T-2 -3100, T-3 -2500 20 2100 T-7 -2100

12. Service Manuals

Instruction and Service Manuals are available for use only, if needed for most of the AFRH-W equipment. If needed they can be obtained from the COR or A1t COR. Availability of Service manuals will not effect contractors ability to perform Scope of Work.

13. Switchgear/Switchboard

All Switchgear and Switchboard cabinets shall be visually

inspected for safety. Loose panels, broken devices, rust or any other deficiencies shall be noted in the report and if such a condition indicates a safety hazard the COR shall be notified immediately. All cabinets and compartments shall be vacuumed and cleaned.

14. Outages

All outages must be scheduled at least 10 days prior to work. Outages will be set up and confirmed with the COR and A1t COR. Due to the mission of the AFRH-W all outages may not be scheduled in order, but all efforts will be made to accommodate a work schedule.

15. Progress Schedule

It is requested that the contractor supply a work progress schedule including dates, and times if necessary as to the start and finish of the maintenance contract. This will

enable internal schedule of outages and inconveniences to all areas involved with the testing.

16. Ground Fault Protection

All breakers, switchboards on Switchgear that have ground fault protection shall be tested as per manufactures recommendation and included in the written report.

17. Standby Power Battery Bank

Maintain standby power battery bank. Eight (8) batteries total of 24 cells. Excide type ICC3; 50 amp HR rating, fully change specific gravity 1205-1220, bank voltage rating 52.3, float voltage per cell 2.17-1.30. During the course of the contract the following shall be completed twice,at six month intervals. Clean, inspect, tighten all interconnecting battery terminals and connections. Clean and inspect all battery casings for cracks and leaks. Check battery fluid levels and maintain fluids. Check specific gravity and volts per cell. Check changing circuit and adjust if necessary floating and equalizing voltages.

Provide results of both inspections in the written report.

18. Mat and Glove Testing

Contractor shall pick up, and return from the AFRH-W Electric Shop two (2) rubber linemen gloves and (1) mat approximate size 36" X 36" and have tested for any leakage. Units shall be labeled as to the test results and date tested and returned to the Electric Shop. Mat and gloves shall be tested two times during the course of the contract, at six month intervals.

19. Fire Alarms

Contractor shall take note of all work areas for fire protections equipment i.e. smoke detectors, flame detectors, pull boxes. If work is taking place that could cause a false alarm, contractor shall bag the smoke heads, and or provide protection in some manner to prevent a false alarm. Contractor shall notify COR or A1t COR when work detail

involves this type of protection. Contractor shall put the equipment back into normal service when hazard has been removed and always at the end of each work day.

20. Reports

Two (2) copies of the test reports shall be submitted to the COR 2 weeks prior to the end of the Fiscal contract.

DESCRIPTIONS & LOCATIONS

MAIN SUBSTATION - BLDG. #71

0001	- 2each - Westinghouse, 13,200 volt Instruction Book #32-190-C352, Date 1946. Switchgear Enclosure and    Buss System which includes:

0002	- 8 each - 15KV, Type 150 HG-250 Air Circuit Breakers 35 - Protective over current relays

0003	- 1each - 15 KV, Type 150 HG-250 Buss Tie Breaker

0004 - 1 each- KV Buss Tie Dummy Breaker

0005 - 1 each- 1200 AMP, 15.5 KV Ground Test Breaker

0006 - 1 Lot of Automatic load transfer relays

0007 - 1 each - General Electric Power, Vac Switchgear, Req. 722- 98123 Sum. 0337A5610, date 8, 1989

0008 - 4 each - Type VB1- 15.8 - 750-2 Vacuum Interrupter Breakers 1200KV

0009 - 17 each - Over current and Voltage Relays 4 - A/C Amp meters

0010 - 1 each - A/C Kilovolt meter

0011 - 1 each - 13.8 KV Ground/Test Breaker

0012 - 8 each - Batteries Maintain a standby power source. Total of 24 cells, Excide type ICC3, 50 amp H.R. rating,                            full charge specific gravity 1205- 1220; bank voltage rating 52.3, float voltage per cell 2. 17- 2.30

0013 - Switchgear structures and Buss System

VAULT T-2 GRANT BLDG. #18

0014 - 2 each - Transformers 75KVA 480 to 208/120, 3 phase, Delta-Y, Serial #9T23B3874, (891215), (890619).

0015 - 2 each - Transformers, Ferranti- Packard Silicone Filled -Serial #4009000600 1 & 2, Class OA- NET - Vault, 3 phase, H.V. 13,200 Delta L.V. 480 y/277.

0016 - 2 each - Network Protectors - General Electric Type MG-14 Serial #0288A4469 1 & 2 UD, 2000 Amp, 277/480 volt, 60 hz, Instruction #GEK-7306C, SS Relay GEK-39809-B

0017 - 2 each - Protective Relays Model #30-SS NPR, 125/216 volt. Includes electrical interlock from Network to Transformer.

0018 - 1 each - Switchgear General Electric Indoor AKD-8, Rated 480V, 3 phase, - 4 wire, 60hz. Includes all

51-5, 51-2, 51-3, 86, 83 Devices, GB relays, GBX relays, CPT and PT fuses, Network trip circuits.

0019 - 6 each - Low voltage power circuit breakers, versa trip AKRU programmer draw out time Switchgear is ground fault protection

VAULT T-3 NORTH CONVERTOR BLDG. #28

0020 - 2 each - Transformers, General Electric Silicone filled Serial #M-

156448 - A & B, Class OA, 3 phase, HV l3,200V L.V. 480Y/277V Instruction Book #GEK 45249 - GEI-68084 100KVA

0021 - 2 each - Switchgear-General Electric AV line 2B tied by common buss, 3 phase, 4 wire, 60 hz, 1600 amp, 480/277 volts. 6 -Type QMRFusible Interrupter Switches, Cat #QMR364 & 5

0022 - 6 each - Phase Directional Relays 2 - 3 Phase Master Relays 2 - Phasing Relays

0023 - 2 each - GE, Motor Operated low voltage Power Circuit Breakers #256A4002-90l- 1 & 2, Type AK-2-50-3, 1600 amp 3 phase, 600 volts, 60 hz

*Includes all switchgear and Buss systems

VAULT T-6 STOREHOUSE BLDG. #74

0024 - 2 each - Transformers, Ferranti Packard Silicone Filled Serial #400890600 1 & 2, class OA- New Vault, 3 phase, H.V. 13,200 Delta, L.V. 2l6y/125v

0025 - 2 each - Network Protectors - General Electric Type MG-9V Serial #0288A4469-7 & 8 UD, 1600 amp, 125/216 bolt 60 hz.

0026 - 2 each - Solid State Protector relays Model #30-ss NPR, 125/216 volt,3 phase

*Includes transformer/Network electrical interlock systems *Includes all switchgear structures and bus systems *Excludes the low voltage breakers

VAULT T-7 SCOTT BLDG. #80

0027 - 1 each - Transformer 300-KVA Challenger, Dry Type, DT-3 Transformer, 3 phase, 60 hz, Class AA, Cont. Degree Rise 150 Pri 600v Delta, Sec. 208/l20Y Design #U33082CH Catalog #303-515, Serial #J95E0640

220-2, Class AA, Temp Rise l50c Step-up 208v to 480v (2)- General Electric 225-KVA, 3 phase, 60 hz, Model #9t23B3877 , #891018, Pri. 480 Delta 208/l20Y

0028 - 2 each - Transformer Fettanti-Packard Silicone filled Serial #4009- 106001 & 2, 100 KVA, 55/65 degrees rise,

Class OA NET Vault, 3 phase, 60hz 13.2 KV, L.V. 216/125 volt X 480y/277 volt

0029 - 2 each - Network Protectors - General Electric Type MG-96, #0288A4469- 3TD, 125/216 volt, 3500 amp, 60hz. Instructions #GEK 39806B

0030 - 2 each - S.S. Relays GEK-39809B

0031 - 2 each - G.E. Solid State Network Protector Relays Model #30 -SS NPR l25/2l6V, 3 phase

0032 - 21 each - Low Voltage Breaders Type General Electric,Trip Units RMS-9

*Includes Transformer/Network electrical interlock systems. *Includes all Switchgear structures and buss system.

VAULT T-9 HEATING PLANT BLDG #46

0033 - 2 each - Transformers Ferranti - Packard Silicone filled, Serial #4008806001 & 2, 500KVA, 3 phase, 60HR, 65 degree C rise, Class OA-NET-Vault, H.V. 13.2 KV, L. V. 2l6Y/125 volts

0034 - 2 each - Network Protectors General Electric Type MG-9U, #0288A4469- 8UD, 125/216 volt, l600amp, 60HZ

0035 - 2 each- SS relays GFK-398 09-B

0036 - 2 each- G.E. Solid State Network Protector Relays Model #30-SS NPR, 125/216 volt, 3 phase

0037 - 12 each - Low Voltage Breakers Type General Electric,Trip Units RMS-9

*Includes Transformer/Network electrical interlock systems. *Includes all switchgear structures and Buss Systems.

VAULT T-10 SHERIDAN BLDG #17

0038 - 2 each - Transformers - 13.2 kv/480-277v, dry

0039 - 2 each - Network protectors 165=00A, 277-480v, Cutler Hammer CMD

0040 - 2 each - GE relays, Model MDP0330000DA

0041 - 8 each- LV breakers GE AKR 600v

0042 - 3 each - Swgr/swb, GE 3ph., 277-480v Spectra Series

0043 - 2 each - LTG Panels 277-48v, 120-208v

0044 - 1 each - GE Transformer 300KVA, 480/208-120v dry type

0045 - 1 each - GE Transformer 45KVA, 480/208-120v dry type

*Includes all switchgear structures and Buss Systems.

VAULT T-11 SHERIDAN BLDG #17

0046 - 2 each - Transformers - 13.2 kv/480-277v, dry

0047 - 2 each - Network protectors 165=00A, 277-480v, Cutler Hammer CMD

0048 - 2 each- GE relays, Model MDP0330000DA

0049 - 7 each - LV breakers GE AKR 600v

0050 - 4 each - Swgr/swb, GE 3ph., 277-480v Spectra Series

0051 - 2 each - LTG Panels 277-48v, 120-208v

0052 - 2 each- GE Transformer 300KVA, 480/208-120v dry type

0053 - 1 each - GE Transformer 45KVA, 480/208-120v dry type

*Inc1udes all Switchgear structures and Buss Systems.

VAULT T-12 AUTO CRAFT PADMOUNT TRANSFORMER BLDG #69 (Non PCB, mineral oil)

0054 - 1 each - Square D Distribution Transformer, 75KVA, H.V. 13,800 L.V. 208Y/120, 3 phase, oil filled, Serial #850475 - A1 MFG Date 9-22-85, Instruction Book #43404-401-38

0055 - 1 each - Sq. D 400amp molded case circuit breaker

0056 - 1 each - Nonload break Fused Oil Switch, 3 position manually operated

0057 - 1 each - Complete wipedown of the H.V. terminations is required.

VAULT T-14 LAGARDE BLDG #56

0058 - 1 each - Transformer I.T.E. Dry Type Siemens 225KVA, 3 phase, 60HZ, H.V. 480 Delta, L.V. 208/120Y, amps 625, Model 36B Type 1 enclosure, 220c insulation, System FH3G, Temp Rise 150c, Ambient 40C max

0059 2 each - Transformers, Dry Type, Manufacture- ASEA Brown Boveri,

Serial No. S 33103-01 & 02, Date 3/91, Total Weight each 11,000lbs., Instruction Book 1B.1.7D, 1500KVA,

2025AA,2700AA-FA H.V. 13,200, L.V. 480Y/277 , Class AA FA,

Type VENT, 3 phase, 60HZ Temp Rise 80-150-150 degree cent. LV amps 1804-2436-3248, BIC HV 95KV, LV 10KV

0060 - 2 each - Network Protectors, Manufacture General Electric, Serial #s0288A-1 & 2 VF, Date 1991, Type MG-14N, Instruction Book GEK-7306B, Parts GEK-398098, 4,500 amps, 277/480 volts, 60HZ W.D. -0156CA533-1 & 2

0061 - 2 each - General Electric Solid State Network Protector Relays, Model #30 SSNPR, 125/216 volt, 3 phase, SO/60HZ

0062 - 2 each - High Voltage Switches - Metal Enclosed Switch and Fuse, 15KV 600amp, 95kv BIC Type-Air Interrupter-FIF, Continuous Amps 600, Interrupting Current Amps 600, Max. Voltage 13.8kv, Fault Closing KA-ASYM-40, Fuse and Holder Type cs3, Continuous Current Amps 200, Interrupting Current KA-40, Max. Voltage KV 15.5, Basic Insulation Level KV BIC-95, Serial #0416

0063 - 2 each - Link Switches, 600 volt ac, 4000amp, non load break

0064 - 2 each - Over current relays, 3 phase, very inverse time 1.5-6a, 120

volt control

0065 - 2 each - Control Transformers - 480/120 vac, 100va,

0066 - 2 each - 286 Device- Lockout relays, series 24, 120 volt

0067 - 1 each - General Electric AV Line Switchboard, Job #359384, Customer Mark #SWBD-ICF, 480u/277 volts ac, 3 phase, 4 wire, 60HZ, product type AV-S Plant Code T1l0, 4000 amps, short circuit rating 100,000 rms, Sym. Amps at 480 volts

0068 - 12 each - General Electric Power Break Circuit Breakers Cat #THP88SS, 3 pole, 480 Volt

*Inc1udes all switchgear, Buss Systems, and meters. The following are to be visually inspected and infra-red scanned; All are located in Vault T-14

0069 - Panel PDP-1 Section 1 & 2 - 6 fused switches and associated buss Panel PDP-2 - 6 fused switches and associated buss Panel PDP-K1 Section 1 & 2 - 9 fused switches and associated buss Panel PDP-KA Section 1 & 2 - 21 circuit breakers (Siemens ITE FD6 Breakers) and all associated buss

0070 - Maintenance rate for service provided after 4:00pm Monday through Friday or on Saturday and Sunday.  Must be coordinated with the COR/ACOR prior to scheduling (not to exceed 60 hours)

**The following line items are to be provided only when called for by the Contracting Officer=s Rep (COR) or the Alternate COR (ACOR) during the period from 1 April 2003 through 31 March 2004.

0071 - Emergency Services: Monday through Friday 7:30am through 4:00pm (except Government observed Holidays)

0072 - Emergency Services: Other than hours/day stated in CLIN 0071

0073 - Emergency Switching required by Pepco

NOTE: Payment for services under line items 0071, 0072, and 0073 will be made for Aon-site@ labor time only.  Hourly rates shall include all overhead, office support, supervision and management costs, fringes, taxes, insurane necessary vehicles and equipment that are required for effort.  No additional payment will be made in connection with labor costs.  Contractor must report to COR or ACOR upon arrival and departure from the grounds of the AFRH-W.  Contractor shall provide a list of personnel who worked that day and include the number of actual hours worked for each.

0074 - Authorized Equipment Repairs:

Contractor must have approval from COR prior to making repairs.

NOTE: Repairs shall be billed at contractor= s cost.  Evidence of cost shall be submitted with invoice.

0074A- Parts, materials and any transportation charges that may be required to perform the above service shall be billed at Contractor=s cost.

NOTE: Evidence of cost shall be submitted with incoice.

0074B - Hourly rate for approved maintenance repairs during off hours.

0074C - Hourly rate for straight time work on maintenance repairs authorized by the COR/ACOR

(End of Section)

E.1  52.246-4  INSPECTION OF SERVICES--FIXED-PRICE (AUG 1996)

(Reference 46.304)

H.1  SPECIAL CONTRACT REQUIREMENTS

H.1  SPECIAL EXPERIENCE & QUALIFICATIONS:

N/A

H.2  INSURANCE REQUIREMENTS:

H.2.1  Insurance coverage in the following types and amounts are required.  NOTE:  Provide insurance certificate(s) showing the following amounts of coverage within ten (10) calendar days after receipt of Notice of Award or after request from the Contracting Officer:

TYPE	AMOUNT

Workmen's Compensation and	Employers' Liability

Insurance	$100,000.00

Comprehensive General Liability

Insurance	$500,000.00

Automobile Liability Insurance	$200,000.00 - Per Person

$500,000.00 Per Occurrence

for Bodily Injury

$20,000.00 Per Occurrence

for Property Damage

H.3  CONTRACT DRAWINGS, AND SPECIFICATIONS:

N/A

H.4  CONTRACTOR'S INSPECTION

H.4.1  PROCEDURES:  N/A

H.4.2  WORK DEFICIENCIES:  The Contractor will not build upon or conceal any work containing defects.  If deficiencies found by the Contracting Officer indicate that the Contractor's work is not adequate or does not conform to the contract documents and produce the desired results, corrective actions in the work shall be taken by the Contractor at no cost to AFRH-W.  If the Contractor does not promptly make the necessary corrections, the Contracting Officer may issue an order stopping all or any part of the work until satisfactory corrective action has been taken.  No part of the time lost, due to any such stop orders or corrective action, shall be made the subject of claim for extension of time and/or excess costs or damages by the Contractor.  Payment for deficient work will be withheld until the work is satisfactorily corrected or other action approved by the Contracting Officer is taken.

H.4.3  WORKMANSHIP:  All work shall be performed in a competent and efficient manner, with tools and equipment that are suitable for the project.  The workmanship shall be subject to  government inspection at all times.

H.5  CONTRACTOR'S USE OF AFRH-W PREMISES:

H.5.1.  REGULATIONS:

H.5.1.1  COMPLIANCE:  All rules and regulations issued by the Armed Forces Retirement Home covering general safety, security, dress, sanitary requirements,  pollution control, traffic regulations and parking, shall be observed by the Contractor.  Information regarding these rules and regulations are available from the Contracting Officer.  The Contracting Officer will provide such information or assist in obtaining same from appropriate authorities.

H.5.1.2  IDENTIFICATION INFORMATION:  ID Badges and Vehicle pass(es) are required.  Comply with the following:

a.  Identification Badges:  The AFRH-W will issue Identification Cards with Photos to all contractor employees performing work under this contract on the AFRH-W grounds.  The Contractor shall submit the following information for each employee who will be working on the AFRH-W grounds ten (10) calendar days prior to start of work on AFRH-W grounds:

1.  Full name (including middle initial)

2.  Social Security Number

3.  Date of Birth

4.  Height

5.  Weight

6.  Hair Color

7.  Eye Color

b.  Vehicle Pass:  Contractor vehicles (as stated elsewhere in the contract) allowed access to the AFRH-W grounds will be issued  a vehicle pass.  The Contractor shall submit the following information for each vehicle that will be driven on the AFRH-W grounds ten (10) calendar days prior to start of work on AFRH-W grounds:

1.  Make of Vehicle

2.  Year of Vehicle

3.  Model of Vehicle

4.  License plate number on Vehicle

c.  The Contractor shall coordinate with the Contracting Officer on the time and date employees will arrive at the Security Building (Building #22) to have photos taken and obtain an ID Badge and Vehicle Pass.  Present vehicle and registration card at this time.

d.  All Identification Cards must be returned to the Contracting Officer or authorized representative upon completion of the work.  Lost Identification Cards will be replaced at Contractor's expense.  Final payment will not be made until all Identification Cards are returned.  Contractor personnel will not be admitted to the AFRH-W grounds without his/her Identification Card.

H.5.1.3  SPEED LIMITS, PARKING, AND SEAT BELTS:  Contractor personnel shall adhere to the authorized speed limits while operating vehicles on the grounds of the AFRH-W.  Park vehicles only in areas as directed by the Contracting Officer, and otherwise conform to rules and regulations of the AFRH-W.  Contractor's personnel are required to comply with District of Columbia laws which require seat belts to be used at all times.  Speed limits on AFRH-W grounds are 15 mph unless otherwise  posted.  Only 5 mph is allowed through the shops and service area.

H.5.1.4  OVERSIZED EQUIPMENT:  The Contractor shall submit a schedule for the arrival time and location of any crane, pile driver, or other such equipment at least fourteen (14) calendar days prior to its arrival and use.

H.5.1.5.  TRASH/WASTE REMOVAL:  The Contractor shall furnish adequate metal containers with lids for the purpose of use as trash containers.  Containers shall be emptied and trash removed by the completion of each work day.  Portable toilet(s) shall be serviced at least weekly, and waste material shall be disposed of off AFRH-W property.

H.5.2  RESTRICTIONS:

H.5.2.1  CONTRACTOR PERSONNEL:  Contractor personnel are prohibited from entering the rooms of AFRH-W residents.  The Contractor shall notify all of its personnel that any contract employee who enters the room of a AFRH-W resident shall be immediately escorted from the AFRH-W grounds by  security  personnel and re-entry will be prohibited.  The Contractor shall also advise his subcontractor(s) to notify their personnel of the requirement of this paragraph.  This clause applies to all rooms except those where entry is required to perform services under this contract.

H.5.2.2.  Contractor's employees movement within the site is restricted to areas as designated by the Contracting Officer.

H.5.2.3  Absolutely no alcoholic beverages and/or illegal drugs of any type may be introduced or consumed on the AFRH-W grounds.  Also, smoking is only allowed in designated areas.  Contractor's personnel shall wear shirt, long pants, and safety shoes at all times.

H.5.2.4  NOISE CONTROL:  As a minimum, the Contractor shall comply with the regulations of the District of Columbia relative to noise control.  The Contractor shall make every effort to keep noise to a minimum to prevent disturbing AFRH-W residents.  [Radios will not be allowed within the building.]

H.5.2.5  SITE ENTRANCE:  The North Capitol Street Gate shall be the ONLY entrance used by the Contractor's trucks and equipment, unless otherwise directed by the Contracting Officer.

H.5.2.6  USE OF LATRINES:  The Contractor may use the toilet facilities in the LaGarde Building.The location within the building shall be at the Contracting Officer's discretion.  Should the Contracting Officer determine latrines are not being kept clean, the Contracting Officer shall have the rooms cleaned at the Contractor's expense.

H.5.2.7  MAINTENANCE OF ACCESS:  The Contractor shall not block passage through sidewalks, roads or entrance ways to any building during performance of work under this contract without the Contracting Officer's prior approval.

H.5.2.8  USE OF AFRH-W TOOLS AND EQUIPMENT:  Contractor's personnel shall not use AFRH-W tools and equipment.

H.5.2.9  DELIVERIES:  The AFRH-W will not accept deliveries of any kind for Contractors.  Contractors are required to have a representative on site to meet deliveries.

H.5.2.10  The Contractor shall maintain at least 50 degrees F. in areas of building where he is working.  Heating methods shall be approved by the Contracting Officer.

H.6  ACCIDENT PREVENTION (AFRH-W Apr 84)

H.6.1  (a)  In performing this contract, the Contractor shall provide for protecting the lives and health of his employees, AFRH-W residents and employees and other persons; preventing damage to property, materials, supplies, and equipment; and avoiding work interruptions.  For these purposes, the Contractor shall-

(1)  Comply with all OSHA Regulations, all regulations of the District of Columbia Safety Code and the AFRH-W Safety Regulations.

(2)  Ensure that any additional measures the Contracting Officer determines to be reasonably necessary for this purpose are taken.

(b)  The Contractor shall maintain an accurate record of exposure data on all accidents incident to work performed under this contract resulting in death, traumatic injury, occupational disease, or damage to property, materials, supplies, or equipment, and shall provide that data to the Contracting Officer.  .

(c)  The Contracting Officer shall notify the Contractor of any observed noncompliance with these requirements and of the corrective action required.  This notice, when delivered to the Contractor or the Contractor's representative at the site of the work, shall be deemed sufficient notice of the noncompliance and corrective action required.  After receiving the notice, the Contractor shall immediately take corrective action.  If the Contractor fails or refuses to take corrective action promptly, the Contracting Officer may issue an order stopping all or part of the work until satisfactory corrective action has been taken.  The Contractor shall not base any claim or request for equitable adjustment for additional time or money on any stop order issued under these circumstances.

(d)  The Contractor shall be responsible for his subcontractor's compliance with this clause.

(e)  The Contractor shall be required to submit a Safety Plan to the Contracting Officer, for approval, within ten (10) calendar days after receipt of award.

H.6.2  The following items as applicable shall be included in the Contractor's submitted Safety Plan:

(a)  Name, telephone number of the Contractor's safety official.

(b)  Arrangements made to provide for the treatment of injuries.

(c)  Material safety data sheets for all chemicals/materials to be used on AFRH-W grounds that have been identified as hazardous by OSHA/EPA.  Examples would be solvents, oils, paints, petroleum products, acids, etc.

(d)  Driver's license qualifications and operator certifications for all employees expected to operate construction equipment, heavy duty trucks, cranes etc.

(e)  Description of measures to be taken to secure the perimeter of the work area to protect AFRH-W residents and employees.

(f)  Where specialized operator/user training is required by law (such as asbestos removal, power actuated tool use, etc.), the Contractor will submit a list of those employees qualified by training and the date the training was given.

H.6.3  EMERGENCY MEDICAL AID:  The Contractor is responsible for transportation of injured employee(s) to a hospital/trauma unit of the Contractor's choice.  In an emergency dial 911 and request an ambulance.  When on-site medical assistance is deemed necessary for a life threatening emergency until the ambulance arrives, dial 3444.

(End of clause)

H.7 N/A

H. 8  PROTECTION OF GOVERNMENT PROPERTY AND PERSONNEL:

H.8.1.  AFRH-W PERSONNEL SAFETY:  Parts of the [building] will be in use by AFRH-W personnel during part of this work.  The contractor shall provide for the Safety of the occupants as described in these specifications.

H.8.2  SUBMITTALS:

a)  The Contractor shall review existing conditions and submit a written list and description of damaged and deteriorated materials and surfaces existing prior to commencement of any work.  Submit written list within thirty (30) calendar days of Notice to Proceed.

.

H.8.3 N/A

H.8.4  The Contractor shall take whatever measures are necessary to prevent water from entering any opening caused by his work.  This may include temporary installation of plywood, polyethylene, etc. as necessary to protect against rain and wind.

H.8.5  All existing Government owned or rented equipment and material within the work area shall be protected by the Contractor from damage caused by construction operations.  As a minimum, the Contractor shall cover all equipment in the work area with dust barriers and protect such items from any damage due to dust, vibration, water, heat or other conditions resulting from construction activities.  Existing work damaged by construction operations shall be promptly repaired by the Contractor at no additional expense to AFRH-W.

H.8.6 N/A

H.8.7  Contractor shall not track mud, adhesives, or blacktop into any building during performance of the work.  Contractor shall hose down his vehicles so as not to truck mud along AFRH-W grounds and roadways.

H.8.8  STREET CLOSINGS:  The Contractor is required to submit a written request to the Contracting Officer when he foresees the necessity for closing any street or roadway on AFRH-W grounds, prior to five (5) working days of requested closure.  The Contractor shall provide appropriate barricades, signs, markers, flares, and other devices as may be required by the Contracting Officer for traffic guides and public safety.

H.8.8.1  Whenever a two way road needs to be limited to only a one lane capacity, there shall be a flag man, hired by the Contractor, to direct traffic during construction hours.  After construction hours a temporary metal plate shall be placed over any trench such that cars can safely use both lanes.

H.8.9    SALVAGE MATERIALS AND EQUIPMENT:  The Contractor shall maintain adequate property control records for all material and equipment  specified to be salvaged. The Contractor shall  be responsible for the adequate storage and protection of all salvaged materials and equipent  and shal replace, at no cost to the Government,  all salvage materials and equipment which are broken ar damaged during salvage operations as the result of this negligence,  or while in this care.

H.8.9.1   N/A

H.8.10   N/A

H.8.11.a.  BARRICADES:  The Contractor shall provide and securely place clearly visible wood or plastic work horses covered with expanded orange plastic safety mesh fastened to the work horses around the perimeter of the construction site and staging area, and anywhere within that area which he deems potentially dangerous.  Close off barricades completely at the end of each work day.  Such barricades shall be required to alert AFRH-W members and personnel not to go inside and shall also be used whenever safe public access to areas such as roads, parking areas or sidewalks is prevented by construction activities or as otherwise necessary to ensure the safety of both pedestrian and vehicular traffic.  Warning signs shall be erected as necessary to indicate construction areas or hazardous zones.

H.8.12  FIRE PREVENTION AND PROTECTION:  The Contractor shall be liable for any loss by fire to AFRH-W property attributable to negligence on the part of the Contractor, including failure to comply with fire prevention measures as outlined in the current N.F.P.A fire codes.  The Contractor or his responsible agent will be required to make a thorough inspection of the job site and each building in which he has performed work at the close of his operations each day to determine that all necessary safeguards relative to potential fire hazards are in effect.

H.8.12.1  Any used rags, waste, empty material containers and the like must be removed from the site every night.  The Contractor shall also be responsible for any costs incurred, in repairs or by levy, from  the results of false alarms, fire alarms, fire and smoke damage or damage caused by fire fighting personnel due to causes by Contractor.  Any damaged material or construction shall be repaired to its original condition at no cost to the AFRH-W.

H.9  PROTECTION OF ENVIRONMENTAL RESOURCES:

H.9.1  GENERAL:  The Contractor shall provide for the environmental protection of AFRH-W as a result of this work.

H.9.2  SUBMITTALS:

a)  PROPOSALS:  Within twenty-one (14) calendar days after Contractor's receipt of Notice to Proceed, the Contractor shall submit in writing for approval his proposed plan for implementing environmental pollution control.

H.9.3  DUST CONTROL:  The Contractor shall maintain all work areas free from dust which would contribute to air pollution.  Approved temporary methods of stabilization consisting of sprinkling where appropriate, or light bituminous treatment where appropriate will be permitted to control dust.  Sprinkling, where used, must be repeated at such intervals as to keep all parts of the disturbed area damp at all times.  Dust control shall be performed as the work proceeds and whenever a dust nuisance or hazard occurs.

H.9.4  CONTAINMENT:  Contain all dust/dirt/debris within the building area where the work is taking place.

H.9.5  MAINTENANCE OF POLLUTION CONTROL FACILITIES DURING CONSTRUCTION:  During the life of this contract, the Contractor shall maintain all facilities constructed for pollution control under this contract as long as the operations creating the particular pollutant are being carried out or until the material concerned has become stabilized to the extent that pollution is no longer being created.

H.9.6  Burning of material and use of explosives is not permitted on AFRH-W property.

H.10  PROTECTION OF LAND RESOURCES:

H.10.1  GENERAL:  It is intended that the land and property resources within the project boundaries and outside the limits of permanent work performed under this contract be preserved in their present condition or be restored to a condition after completion of construction that will appear to be natural and not detract from the appearance of the project.  Insofar as possible, the Contractor shall confine his construction activities to areas defined by the plans and specifications or to be authorized by Contracting Officer for work outside of these areas.

H.11  PROTECTION OF WATER RESOURCES:

H.11.1  GENERAL:  The Contractor shall not pollute ground or surface water with conventional or toxic pollutants, including but not limited to fuels, oils, bitumen, calcium chloride, acids, and organic solvents both on and off the Government premises.  The Contractor shall investigate and comply with all applicable Federal, and municipal laws concerning pollution of surface and ground water.  Special measures shall be taken to prevent chemical, fuels, oils, greases, bituminous materials, herbicides and insecticides from entering public waters.

H.12  UTILITIES:

H.12.1.a.  N/A

H.12.1.b.  AVAILABILITY OF UTILITIES:  It shall be the responsibility of the Contractor to provide all utilities he may require during the entire life of the contract.  He shall make his own investigation and determinations as to the availability and adequacy of utilities for his use for construction purposes and domestic consumption.  He shall install and maintain all necessary supply lines, piping, and meters if required, but only at such locations and in such manner as approved by the Contracting Officer.  Before final acceptance of work under this contract, all temporary supply lines, and piping installed by the Contract shall be removed by him in a manner satisfactory to the Contracting Officer.

H.12.1.1  INTERRUPTIONS OF UTILITIES:  No utility services shall be interrupted by the Contractor to make connections, to relocate, or for any purpose, unless authorized by the Contracting Officer.

H.12.2.  SUBMITTALS:

a.  REQUESTS: Requests for the shutdown of services shall be submitted in writing to the Contracting Officer not less than fourteen (2) days prior to date of proposed interruption.  The request shall give the following information:

(i)  Nature of Utility (Gas, L.P.S., or H.P.S., Water,

etc.)

(ii)  Size of line and location of shutoff.

(iii)  Buildings and services affected.

(iv)  Hours and date of shutoff.

(v)  Estimated length of time service will be

interrupted.

H.12.3.  Services shall not be interrupted until receipt of approval of the proposed hours and date from the Contracting Officer.

H.12.4.  Shutoffs which will cause interruption of AFRH-W work operations as determined by the Contracting Officer shall be accomplished during regular non-work hours or on non-work days of the AFRH-W without any additional cost to the Government.

H.12.5.  Operation of valves on water mains will be by AFRH-W personnel.  Where shutoff of water lines interrupts service to fire hydrants or fire sprinkler systems, the Contractor shall arrange his operations and have sufficient material and personnel available to complete the work without undue delay or to restore service without delay in event of emergency.

H.12.6.  Flow in gas mains which have been shut off shall not be restored until the Contracting Officer's representative has determined that all items serviced by the gas line have been shut off.

H.13  CONTRACTOR'S STORAGE AND OFFICE:

H.13.1  GENERAL:  Protect stored items from all possible damage, including that from other Contractor's vehicles.  Materials which are allowed to be stored outside shall be protected from the weather.  All materials that are kept outside are to be secured to prevent damage or loss due to wind.

H.13.2  CONTRACTOR'S OFFICE:  Contractor's remote office, employee parking, staging, and storage area if required shall be located as coordinated with the Contracting  Officer.

H.13.3.1  No equipment or new materials shall be stored on or in the building except those items that are necessary for same work week  installation.  The exact location will be all existing equipment, materials and debris removed during the work that are not to be reinstalled shall be removed daily by the Contractor from the building.  Job equipment and new material may be stored in the laydown area.  No equipment or materials are to be stored in or on the adjacent buildings.

H.13.4  Hazardous, combustible, and/or contaminated items and equipment designated to be removed shall be stored in a manner and location per applicable codes and laws and as approved of by the Contracting Officer.

H.14.  TEMPORARY CONSTRUCTION ITEMS:

H.14.1  GENERAL:  No separate payment will be made for any temporary construction or services required by this contract, and all costs in connection therewith  shall be included in the overall cost of the work unless specifically stated otherwise.  The work covered by this specification consists of furnishing all labor, materials, equipment, and services and performing all work required for or incidental to the work herein specified.

H.14.2  The Contractor shall carefully coordinate the work of this section with all other work and construct and maintain shoring, bracing and supports, as required.  The Contractor shall insure that structural elements are not overloaded and be responsible for increasing structural supports or adding new supports as may be required as a result of any cutting, removal, patching, or demolition work performed under any part of this Contract.  Upon completion of the project, all temporary construction shall be removed and disposed of by the contractor.

H.14.3  TEMPORARY ELECTRICAL WORK:  All temporary electrical wiring installed during construction shall conform with the latest edition of the National Electrical Code.  Upon completion of the project, all temporary electrical work shall be removed and disposed of by the Contractor.

H.14.3.1  [Interior work which will be visible in the finished project will be executed only under conditions of illumination of an intensity equal to or greater than    foot candles.  If the Contractor fails to maintain the required illumination the Contracting Officer may issue an order stopping all or part of the work until satisfactory corrective action has been taken.  No part of the time lost due to any such stop order shall be made subject of claim for extension of time or for excess costs or damages by the Contractor.]

H.15  DISPOSAL OF EXISTING MATERIAL AND EQUIPMENT:

H.15.1.a.  Construction Materials remaining after completion of the job shall be removed off AFRH-W grounds by the Contractor at his own expense and responsibility.  All debris, trash and other items not designated for Government salvage shall be disposed of off AFRH-W grounds.

H. 15.1.b.   N/A

H. 16 N/A

H. 17 N/A

END OF SECTION

BLANK PAGE

BLANK PAGE

I.1  52.202-1  DEFINITIONS (DEC 2001)

(Reference 2.201)

I.2  52.203-3  GRATUITIES (APR 1984)

(Reference 3.202)

I.3  52.203-5  COVENANT AGAINST CONTINGENT FEES (APR 1984)

(Reference 3.404)

I.4  52.203-6  RESTRICTIONS ON SUBCONTRACTOR SALES TO THE GOVERNMENT (JUL 1995)

(Reference 3.503-2)

I.5  52.203-7  ANTI-KICKBACK PROCEDURES (JUL 1995)

(Reference 3.502-3)

I.6  52.203-10  PRICE OR FEE ADJUSTMENT FOR ILLEGAL OR IMPROPER ACTIVITY (JAN 1997)

(Reference 3.104-9)

I.7  52.203-12  LIMITATION ON PAYMENTS TO INFLUENCE CERTAIN FEDERAL TRANSACTIONS (JUN 1997)

(Reference 3.808)

I.8  52.204-4  PRINTED OR COPIED DOUBLE-SIDED ON RECYCLED PAPER (AUG 2000)

(Reference 4.303)

I.9  52.209-6  PROTECTING THE GOVERNMENT'S INTEREST WHEN SUBCONTRACTING WITH CONTRACTORS DEBARRED, SUSPENDED, OR PROPOSED FOR DEBARMENT (JUL 1995)

(Reference 9.409)

I.10  52.215-2  AUDIT AND RECORDS--NEGOTIATION (JUNE 1999)

(Reference 15.209)

I.11  52.219-6  NOTICE OF TOTAL SMALL BUSINESS SET-ASIDE (JUL 1996)

(Reference 19.508)

I.12  52.219-8  UTILIZATION OF SMALL BUSINESS CONCERNS (OCT 2000)

(Reference 19.708)

I.13  52.219-9 I  SMALL BUSINESS SUBCONTRACTING PLAN (JAN 2002)--ALTERNATE I (OCT 2001)

(Reference 19.708)

I.14  52.219-14  LIMITATIONS ON SUBCONTRACTING (DEC 1996)

(Reference 19.811-3)

I.15  52.222-1  NOTICE TO THE GOVERNMENT OF LABOR DISPUTES (FEB 1997)

(Reference 22.103-5)

I.16  52.222-3  CONVICT LABOR (AUG 1996)

(Reference 22.202)

I.17  52.222-4  CONTRACT WORK HOURS AND SAFETY STANDARDS ACT--OVERTIME COMPENSATION (SEPT 2000)

(Reference 22.305)

I.18  52.222-20  WALSH-HEALEY PUBLIC CONTRACTS ACT (DEC 1996)

(Reference 22.610)

I.19  52.222-26  EQUAL OPPORTUNITY (APR 2002)

(Reference 22.810)

I.20  52.222-28  {52.222-28}  [RESERVED]

(Reference)

I.21  52.222-35  52.222-35 Equal Opportunity for Special Disabled Veterans, Veterans of the Vietnam Era, and Other Eligible Veterans. [Dec 2001]

(Reference 22.1308)

I.22  52.222-36  AFFIRMATIVE ACTION FOR WORKERS WITH DISABILITIES (JUN 1998)

(Reference 22.1408)

I.23  52.222-37  EMPLOYMENT REPORTS ON SPECIAL DISABLED VETERANS, VETERANS OF THE VIETNAM ERA, AND OTHER ELIGIBLE VETERANS (DEC 2001)

(Reference 22.1308)

I.24  52.222-41  SERVICE CONTRACT ACT OF 1965, AS AMENDED (MAY 1989)

(Reference 22.1006)

I.25  52.222-43  FAIR LABOR STANDARDS ACT AND SERVICE CONTRACT ACT--PRICE ADJUSTMENT (MULTIPLE YEAR AND OPTION CONTRACTS) (MAY 1989)

(Reference 22.1006)

I.26  52.222-47  SERVICE CONTRACT ACT (SCA) MINIMUM WAGES AND FRINGE BENEFITS (MAY 1989)

(Reference 22.1006)

I.27  52.223-2  {52.223-2}  [RESERVED]

(Reference)

I.28  52.223-3 I  HAZARDOUS MATERIAL IDENTIFICATION AND MATERIAL SAFETY DATA (JAN 1997)-- ALTERNATE I (JUL 1995)

(Reference 23.303)

I.29  52.223-6  DRUG-FREE WORKPLACE (MAY 2001)

(Reference 23.505)

I.30  52.224-1  PRIVACY ACT NOTIFICATION (APR 1984)

(Reference 24.104)

I.31  52.224-2  PRIVACY ACT (APR 1984)

(Reference 24.104)

I.32  52.225-11  BUY AMERICAN ACT--CONSTRUCTION   MATERIALS UNDER TRADE AGREEMENTS (July 2002)

(Reference 25.1102)

I.33  52.227-1  AUTHORIZATION AND CONSENT (JUL 1995)

(Reference 27.201-2)

I.34  52.227-2  NOTICE AND ASSISTANCE REGARDING PATENT AND COPYRIGHT INFRINGEMENT (AUG 1996)

(Reference 27.202-2)

I.35  52.228-5  INSURANCE--WORK ON A GOVERNMENT INSTALLATION (JAN 1997)

(Reference 28.310)

I.36  52.229-4  FEDERAL, STATE, AND LOCAL TAXEs (State and Local Adjustments) (April 2003)

(Reference 29.401-4)

I.37  52.232-1  PAYMENTS (APR 1984)

(Reference 32.111)

I.38  52.232-8  DISCOUNTS FOR PROMPT PAYMENT (FEB 2002)

(Reference 32.111)

I.39  52.232-11  EXTRAS (APR 1984)

(Reference 32.111)

I.40  52.232-17  INTEREST (JUNE 1996)

(Reference 32.617)

I.41  52.232-19  AVAILABILITY OF FUNDS FOR THE NEXT FISCAL YEAR (APR 1984)

(Reference 32.705-1)

I.42  52.232-23  ASSIGNMENT OF CLAIMS (JAN 1986)

(Reference 32.806)

I.43  52.232-25  PROMPT PAYMENT (FEB 2002)

(Reference 32.908)

I.44  52.233-1  DISPUTES (JUL 2002)

(Reference 33.215)

I.45  52.233-3  PROTEST AFTER AWARD (AUG 1996)

(Reference 33.106)

I.46  52.237-2  PROTECTION OF GOVERNMENT BUILDINGS, EQUIPMENT, AND VEGETATION (APR 1984)

(Reference 37.110)

I.47  52.237-3  CONTINUITY OF SERVICES (JAN 1991)

(Reference 37.110)

I.48  52.242-13  BANKRUPTCY (JUL 1995)

(Reference 42.903)

I.49  52.243-1 I  CHANGES--FIXED-PRICE (AUG 1987)--ALTERNATE I (APR 1984)

(Reference 43.205)

I.50  52.246-20  WARRANTY OF SERVICES (APR 1984)

(Reference 46.710)

I.51  52.246-25  LIMITATION OF LIABILITY--SERVICES (FEB 1997)

(Reference 46.805)

I.52  52.249-2  TERMINATION FOR CONVENIENCE OF THE GOVERNMENT (FIXED-PRICE) (SEP 1996)

(Reference 49.502)

I.53  52.249-8  DEFAULT (FIXED-PRICE SUPPLY AND SERVICE) (APR 1984)

(Reference 49.504)

I.54  52.253-1  COMPUTER GENERATED FORMS (JAN 1991)

(Reference 53-111)

I.55  52.216-18  ORDERING (OCT 1995)

(a) Any supplies and services to be furnished under this contract shall be ordered by issuance of delivery orders or task orders by the individuals or activities designated in the Schedule.  Such orders may be issued from __________ through  __________

(b) All delivery orders or task orders are subject to the terms and conditions of this contract.  In the event of conflict between a delivery order or task order and this contract, the contract shall control.

(c) If mailed, a delivery order or task order is considered "issued" when the Government deposits the order in the mail.  Orders may be issued orally, by facsimile, or by electronic commerce methods only if authorized in the Schedule.

(End of clause)

I.56  52.216-21  REQUIREMENTS (OCT 1995)

(a) This is a requirements contract for the supplies or services specified, and effective for the period stated, in the Schedule.  The quantities of supplies or services specified in the Schedule are estimates only and are not purchased by this contract.  Except as this contract may otherwise provide, if the Government's requirements do not result in orders in the quantities described as "estimated" or "maximum" in the Schedule, that fact shall not constitute the basis for an equitable price adjustment.

(b) Delivery or performance shall be made only as authorized by orders issued in accordance with the Ordering clause.  Subject to any limitations in the Order Limitations clause or elsewhere in this contract, the Contractor shall furnish to the Government all supplies or services specified in the Schedule and called for by orders issued in accordance with the Ordering clause.  The Government may issue orders requiring delivery to multiple destinations or performance at multiple locations.

(c) Except as this contract otherwise provides, the Government shall order from the Contractor all the supplies or services specified in the Schedule that are required to be purchased by the Government activity or activities specified in the Schedule.

(d) The Government is not required to purchase from the Contractor requirements in excess of any limit on total orders under this contract.

(e) If the Government urgently requires delivery of any quantity of an item before the earliest date that delivery may be specified under this contract, and if the Contractor will not accept an order providing for the accelerated delivery, the Government may acquire the urgently required goods or services from another source.

(f) Any order issued during the effective period of this contract and not completed within that period shall be completed by the Contractor within the time specified in the order.  The contract shall govern the Contractor's and Government's rights and obligations with respect to that order to the same extent as if the order were completed during the contract's effective period; provided, that the Contractor shall not be required to make any deliveries under this contract after __________

(End of clause)

I.57  52.216-21 I  REQUIREMENTS (OCT 1995)--ALTERNATE I (APR 1984)

(a) This is a requirements contract for the supplies or services specified, and effective for the period stated, in the Schedule.  The quantities of supplies or services specified in the Schedule are estimates only and are not purchased by this contract.  Except as this contract may otherwise provide, if the Government's requirements do not result in orders in the quantities described as "estimated" or "maximum" in the Schedule, that fact shall not constitute the basis for an equitable price adjustment.

(b) Delivery or performance shall be made only as authorized by orders issued in accordance with the Ordering clause.  Subject to any limitations in the Order Limitations clause or elsewhere in this contract, the Contractor shall furnish to the Government all supplies or services specified in the Schedule and called for by orders issued in accordance with the Ordering clause.  The Government may issue orders requiring delivery to multiple destinations or performance at multiple locations.

(c) The estimated quantities are not the total requirements of the Government activity specified in the Schedule, but are estimates of requirements in excess of the quantities that the activity may itself furnish within its own capabilities.  Except as this contract otherwise provides, the Government shall order from the Contractor all of that activity's requirements for supplies and services specified in the Schedule that exceed the quantities that the activity may furnish within its own capabilities.

(d) The Government is not required to purchase from the Contractor requirements in excess of any limit on total orders under this contract.

(e) If the Government urgently requires delivery of any quantity of an item before the earliest date that delivery may be specified under this contract, and if the Contractor will not accept an order providing for the accelerated delivery, the Government may acquire the urgently required goods or services from another source.

(f) Any order issued during the effective period of this contract and not completed within that period shall be completed by the Contractor within the time specified in the order.  The contract shall govern the Contractor's and Government's rights and obligations with respect to that order to the same extent as if the order were completed during the contract's effective period; provided, that the Contractor shall not be required to make any deliveries under this contract after __________

(End of clause)

I.58  52.216-21 II  REQUIREMENTS (OCT 1995)--ALTERNATE II (APR 1984)

(a) This is a requirements contract for the supplies or services specified, and effective for the period stated, in the Schedule.  The quantities of supplies or services specified in the Schedule are estimates only and are not purchased by this contract.  Except as this contract may otherwise provide, if the Government's requirements do not result in orders in the quantities described as "estimated" or "maximum" in the Schedule, that fact shall not constitute the basis for an equitable price adjustment.

(b) Delivery or performance shall be made only as authorized by orders issued in accordance with the Ordering clause.  Subject to any limitations in the Order Limitations clause or elsewhere in this contract, the Contractor shall furnish to the Government all supplies or services specified in the Schedule and called for by orders issued in accordance with the Ordering clause.  The Government may issue orders requiring delivery to multiple destinations or performance at multiple locations.

(c) Except as this contract otherwise provides, the Government shall order from the Contractor all the supplies or services specified in the Schedule that are required to be purchased by the Government activity or activities specified in the Schedule.

(d) The Government is not required to purchase from the Contractor requirements in excess of any limit on total orders under this contract.

(e) If the Government urgently requires delivery of any quantity of an item before the earliest date that delivery may be specified under this contract, and if the Contractor will not accept an order providing for the accelerated delivery, the Government may acquire the urgently required goods or services from another source.

(f) Any order issued during the effective period of this contract and not completed within that period shall be completed by the Contractor within the time specified in the order.  The contract shall govern the Contractor's and Government's rights and obligations with respect to that order to the same extent as if the order were completed during the contract's effective period; provided, that the Contractor shall not be required to make any deliveries under this contract after __________

(g) The requirements referred to in this contract are for items to be manufactured according to Government specifications.  Notwithstanding anything to the contrary stated in the contract, the Government may acquire similar products by brand name from other sources for resale.

(End of clause)

I.59  52.216-21 III  REQUIREMENTS (OCT 1995)--ALTERNATE III (OCT 1995)

(a) This is a requirements contract for the supplies or services specified, and effective for the period stated, in the Schedule.  The quantities of supplies or services specified in the Schedule are estimates only and are not purchased by this contract.  Except as this contract may otherwise provide, if the Government's requirements do not result in orders in the quantities described as "estimated" or "maximum" in the Schedule, that fact shall not constitute the basis for an equitable price adjustment.

(b) Delivery or performance shall be made only as authorized by orders issued in accordance with the Ordering clause.  Subject to any limitations in the Order Limitations clause or elsewhere in this contract, the Contractor shall furnish to the Government all supplies or services specified in the Schedule and called for by orders issued in accordance with the Ordering clause.  The Government may issue orders requiring delivery to multiple destinations or performance at multiple locations.

(c) The Government's requirements for each item or subitem of supplies or services described in the Schedule are being purchased through one non-set-aside contract and one set-aside contract.  Therefore, the Government shall order from each Contractor approximately one-half of the total supplies or services specified in the Schedule that are required to be purchased by the specified Government activity or activities.  The Government may choose between the set-aside Contractor and the non-set-aside Contractor in placing any particular order.  However, the Government shall allocate successive orders, in accordance with its delivery requirements, to maintain as close a ratio as is reasonably practicable between the total quantities ordered from the two Contractors.

(d) The Government is not required to purchase from the Contractor requirements in excess of any limit on total orders under this contract.

(e) If the Government urgently requires delivery of any quantity of an item before the earliest date that delivery may be specified under this contract, and if the Contractor will not accept an order providing for the accelerated delivery, the Government may acquire the urgently required goods or services from another source.

(f) Any order issued during the effective period of this contract and not completed within that period shall be completed by the Contractor within the time specified in the order.  The contract shall govern the Contractor's and Government's rights and obligations with respect to that order to the same extent as if the order were completed during the contract's effective period; provided, that the Contractor shall not be required to make any deliveries under this contract after __________

(End of clause)

I.60  52.216-22  INDEFINITE QUANTITY (OCT 1995)

(a) This is an indefinite-quantity contract for the supplies or services specified, and effective for the period stated, in the Schedule.  The quantities of supplies and services specified in the Schedule are estimates only and are not purchased by this contract.

(b) Delivery or performance shall be made only as authorized by orders issued in accordance with the Ordering clause.  The Contractor shall furnish to the Government, when and if ordered, the supplies or services specified in the Schedule up to and including the quantity designated in the Schedule as the "maximum."  The Government shall order at least the quantity of supplies or services designated in the Schedule as the "minimum."

(c) Except for any limitations on quantities in the Order Limitations clause or in the Schedule, there is no limit on the number of orders that may be issued.  The Government may issue orders requiring delivery to multiple destinations or performance at multiple locations.

(d) Any order issued during the effective period of this contract and not completed within that period shall be completed by the Contractor within the time specified in the order.  The contract shall govern the Contractor's and Government's rights and obligations with respect to that order to the same extent as if the order were completed during the contract's effective period; provided, that the Contractor shall not be required to make any deliveries under this contract after __________

(End of clause)

I.61  52.217-8  OPTION TO EXTEND SERVICES (NOV 1999)

The Government may require continued performance of any services within the limits and at the rates specified in the contract.  These rates may be adjusted only as a result of revisions to prevailing labor rates provided by the Secretary of Labor.  The option provision may be exercised more than once, but the total extension of performance hereunder shall not exceed 6 months.  The Contracting Officer may exercise the option by written notice to the Contractor within __________

(End of clause)

I.62  52.217-9  OPTION TO EXTEND THE TERM OF THE CONTRACT (MAR 2000)

(a) The Government may extend the term of this contract by written notice to the Contractor within __________  provided that the Government  gives the Contractor a preliminary written notice of its intent to extend  at least  __________ days before the contract expires.  The preliminary  notice does not commit the Government to an extension.

(b) If the Government exercises this option, the extended contract shall be considered to include this option clause.

(c) The total duration of this contract, including the exercise of any options under this clause, shall not exceed __________

(End of clause)

I.63  52.222-42  STATEMENT OF EQUIVALENT RATES FOR FEDERAL HIRES (MAY 1989)

In compliance with the Service Contract Act of 1965, as amended, and the regulations of the Secretary of Labor (29 CFR Part 4), this clause identifies the classes of service employees expected to be employed under the contract and states the wages and fringe benefits payable to each if they were employed by the contracting agency subject to the provisions of 5 U.S.C. 5341 or 5332.

THIS STATEMENT IS FOR INFORMATION ONLY (IT IS NOT A WAGE DETERMINATION):  __________

(End of clause)

I.64  52.223-9  ESTIMATE OF PERCENTAGE OF RECOVERED MATERIAL CONTENT FOR EPA-DESIGNATED PRODUCTS (AUG 2000)

(a) Definitions.  As used in this clause--

"Postconsumer material" means a material or finished product that has served its intended use and has been discarded for disposal or recovery, having completed its life as a consumer item.  Postconsumer material is a part of the broader category of "recovered material."

"Recovered material" means waste materials and by-products recovered or diverted from solid waste, but the term does not include those materials and by-products generated from, and commonly reused within, an original manufacturing process.

(b) The Contractor, on completion of this contract, shall--

(1) Estimate the percentage of the total recovered material used in

contract performance, including, if applicable, the percentage of

postconsumer material content; and

(2) Submit this estimate to __________

(End of clause)

I.65  52.223-11  OZONE-DEPLETING SUBSTANCES (JUN 1996)

(a) Definition.  "Ozone-depleting substance", as used in this clause, means any substance designated as Class I by the Environmental Protection Agency (EPA) (40 CFR Part 82), including but not limited to chlorofluorocarbons, halons, carbon tetrachloride, and methyl chloroform; or any substance designated as Class II by EPA (40 CFR Part 82), including but not limited to hydrochlorofluorocarbons.

(b) The Contractor shall label products which contain or are manufactured with ozone-depleting substances in the manner and to the extent required by 42 U.S.C. 7671j (b), (c), and (d) and 40 CFR Part 82, Subpart E, as follows:

"WARNING:  Contains (or manufactured with, if applicable) ___________*________, a substance(s) which harm(s) public health and environment by destroying ozone in the upper atmosphere."

*The Contractor shall insert the name of the substance(s).

(End of clause)

I.66  52.223-12  REFRIGERATION EQUIPMENT AND AIR CONDITIONERS (MAY 1995)

The Contractor shall comply with the applicable requirements of Sections 608 and 609 of the Clean Air Act (42 U.S.C. 7671g and 7671h) as each or both apply to this contract.

(End of clause)

I.67  52.249-4  TERMINATION FOR CONVENIENCE OF THE GOVERNMENT (SERVICES) (SHORT FORM) (APR 1984)

The Contracting Officer, by written notice, may terminate this contract, in whole or in part, when it is in the Government's interest. If this contract is terminated, the Government shall be liable only for payment under the payment provisions of this contract for services rendered before the effective date of termination.

(R 7-1902.16 1968 FEB)

J.1  WAGE DETERMINATION

GENERAL DECISION DC020001 04/04/2003 DC1

Date: April 4, 2003

General Decision Number DC020001

Superseded General Decision No. DC010001

State: WASHINGTON,D.C.

Construction Type:

HEAVY

HIGHWAY

SEWER AND WATER LINE

County(ies):

WASHINGTON, D.C.

HEAVY CONSTRUCTION PROJECTS (Including Sewer and Water Lines);

HIGHWAY CONSTRUCTION PROJECTS

Modification Number     Publication Date

0             03/01/2002

1             03/08/2002

2             04/12/2002

3             04/26/2002

4             05/03/2002

5             05/24/2002

6             06/07/2002

7             07/05/2002

8             07/12/2002

9             07/26/2002

10             08/23/2002

11             09/27/2002

12             10/04/2002

13             10/18/2002

14             11/29/2002

15             02/07/2003

16             03/14/2003

17             04/04/2003

COUNTY(ies):

WASHINGTON, D.C.

ASBE0024A  03/01/2003

Rates           Fringes

ASBESTOS WORKERS/HEAT AND FROST

INSULATORS

Includes application of all

insulating materials, protective

coverings, coatings and finishes

to all types of mechanical

systems. Also the application of

firestopping material for wall

openings and penetrations in

walls, floors, ceilings and

curtain walls.                      23.35           10.35

----------------------------------------------------------------

ASBE0024B  03/01/2003

Rates           Fringes

HAZARDOUS MATERIAL HANDLER

Includes preparation, wetting,

stripping, removal, scrapping,

vacuuming, bagging and disposing

of all insulation materials,

whether they contain asbestos

or not, from mechanical systems.    12.37           3.91

----------------------------------------------------------------

BOIL0193A  10/01/2001

Rates           Fringes

BOILERMAKERS                          25.57           12.76

----------------------------------------------------------------

BRDC0001A  04/28/2002

Rates           Fringes

BRICKLAYERS                           23.75           5.37

----------------------------------------------------------------

CARP0132A  05/01/2002

Rates           Fringes

CARPENTERS & LATHERS                  21.57           3.76

PILEDRIVERS                           19.95           4.50

----------------------------------------------------------------

CARP0132E  05/01/1999

Rates           Fringes

DIVERS                                27.07           3.95

DIVER TENDERS                         21.10           3.95

----------------------------------------------------------------

CARP1831A  09/07/1998

Rates           Fringes

MILLWRIGHTS                           20.07           3.69

----------------------------------------------------------------

ELEC0026A  11/04/2002

Rates           Fringes

ELECTRICIANS                          28.35           7.77 + 3%

----------------------------------------------------------------

ELEC0026H  07/01/1995

Rates           Fringes

MOTOR REPAIRMEN

Removal and reinstallation

of electrical motors                19.93           2.85+3%+a

a. PAID HOLIDAYS: New Year's Day, Martin Luther King's Birthday,

Inauguration Day, Washington's Birthday,

Memorial Day, Fourth of July, Labor Day,

Columbus Day, Veterans' Day, Thanksgiving

Day, the day after Thanksgiving, and Christmas

Day, or days designated as legal holidays by

the Federal Government.

----------------------------------------------------------------

ELEC0070B  03/31/2002

Rates           Fringes

LINE CONSTRUCTION:

Linemen, Cable Splicers,

Equipment Operators               24.48           2.45+17.5%

Truck with winch                    14.50           2.45+17.5%

Groundmen                           13.99           2.45+17.5%

----------------------------------------------------------------

* ENGI0077A  05/01/2002

Rates           Fringes

POWER EQUIPMENT OPERATORS

(HEAVY AND HIGHWAY CONSTRUCTION):

GROUP 1                               23.29           4.77+a+b

GROUP 2                               22.83           4.77+a+b

GROUP 3                               22.12           4.77+a

GROUP 4                               20.54           4.77+a

GROUP 5                               16.00           4.77+a

GROUP 6                               24.66           4.77+a

POWER EQUIPMENT OPERATORS CLASSIFICATIONS

GROUP 1: 35 ton cranes & above, tower & climbing cranes,

derricks, concrete boom pump, drill rigs (equivalent

to L & Double L), mole.

GROUP 2: Backhoes, cableways, cranes, cherry pickers, elevating

graders, hoists, paving mixers, power shovels, tunnel

shovels, batch plants, shields, tunnel mining machines,

gradalls, front end loaders, 3 1/2 cu. yds. and above,

power driven wheel scoops and scrapers (50 cu. yds.

struck capacity or above), rail tamper, draglines,

boomcat, mucking machines, graders in tunnels, pile

driving engines.

GROUP 3: Front end loaders below 3 1/2 cu. yds, boom trucks,

hydraulic backhoes 1/2 yds. capacity or below rubber or

track mounted, tug boats, power driven wheel scoops and

scrapers, blade graders, motor graders, bulldozers,

trenching machines, concrete mixer, speed swing

pettibone, ballast regulator, concrete pump, mechanic,

welder, mechanic welder, shotcrete machines, Hoeram,

locomotive (standard, narrow gauge), tuggers.

GROUP 4: High lifts above 10 feet, boilers (skelton), asphalt

spreaders, bullfloat finishing machines, concrete

finishing machines, concrete spreaders, fine graders,

air compressors, welding machines, pumps, generators,

well points, deep wells, hydraulic pumps, elevators,

freeze units, tunnel motorman or dinky operator, roller,

conveyors, well drilling machines, grout pump, fireman.

GROUP 5: Fork lifts, ditch witch, bobcat 1/3 cu. yd. and below,

space heaters, sweepers, assistant engineers, oilers.

GROUP 6: Master mechanic.

a. PAID HOLIDAYS: New Year's Day, Inaugural Day, Decoration Day,

Independence Day, Labor Day, Martin Luther

King's Birthday, Veterans' Day, Thanksgiving

Day, Friday after Thanksgiving, and Christmas

Day.

b. PREMIUM PAY:   Tower cranes and cranes 100-ton and over to

receive $1.00 per hour premium over Group One.

----------------------------------------------------------------

ENGI0077B  06/01/2002

Rates           Fringes

POWER EQUIPMENT OPERATORS

(PAVING AND INCIDENTAL GRADING):

GROUP 1                               18.80           4.05

GROUP 2                               16.70           4.05

GROUP 3                               15.65           4.05

GROUP 4                               14.60           4.05

GROUP 5                               13.55           4.05

GROUP 6                               18.80           3.80

POWER EQUIPMENT OPERATORS CLASSIFICATIONS

GROUP 1: Gradall operator, Crane.

GROUP 2: Boom Truck, Milling Machine, Excavator, Rubber Tire

Backhoe, Asphalt Paver, Asphalt Plant Engineer.

GROUP 3: Motor Grader, Track Loader, Rubber Tire Loader,

Track Dozer, Concrete Paver.

GROUP 4: Broom Truck, Asphalt Roller.

GROUP 5: Air Compressor, Grade Rollers.

GROUP 6: Mechanic.

----------------------------------------------------------------

ENGI0077C  07/01/2001

Rates           Fringes

POWER EQUIPMENT OPERATORS

(SEWER, GAS AND WATER LINE CONSTRUCTION):

GROUP  1                            17.48           3.22+a

GROUP  2                            17.08           3.22+a

GROUP  3                            16.93           3.22+a

GROUP  4                            16.85           3.22+a

GROUP  5                            16.74           3.22+a

GROUP  6                            16.57           3.22+a

GROUP  7                            16.67           3.22+a

GROUP  8                            16.57           3.22+a

GROUP  9                            17.11           3.22+a

GROUP 10                            16.46           3.22+a

GROUP 11                            16.34           3.22+a

GROUP 12                            16.25           3.22+a

POWER EQUIPMENT OPERATORS CLASSIFICATIONS

GROUP  1: Backhoes, Cableways, Cranes, Derricks, Draglines,

Power Shovels, Tunnel Shovels, Tunnel Mucking

Machines (1 cubic yard capacity or above).

GROUP  2: Backhoes, Boom Cats, Cableways, Cranes, Derricks,

Draglines, Elevating Graders, Hoists, Paving

Mixers, Pile Driving Engines, Power and Tunnel

Shovels, Tunnel Mucking Machines, Batch Plant,

Concrete Pumps.

GROUP  3: Operators of Hydraulic Backhoes of below 1/2 yard

capacity.

GROUP  4: Trenching machines (above 83")

GROUP  5: Trenching machines (up to and including 83"),

Boilers (Skelton), Well Drilling Machines.

GROUP  6: Air Compressors (Tunnel).

GROUP  7: Front-end Loaders (Hi-Lift) and Bulldozers on Sewer

and Water Line Work.

GROUP  8: Concrete Mixers, Power Driven Wheel Scoops and

Scrapers, Blade graders, Motor Graders, Tunnel

Mechanics, Tunnel Motormen.

GROUP  9: Mechanics.

GROUP 10: Bulldozers, Hydraulic Tamper and Hoe Pack Operators.

GROUP 11: Rollers.

GROUP 12: Air Compressors, Pumps, Welding Machines, Well

Points.

a.PAID HOLIDAYS:New Year's Day, Inaugural Day, Washington's

Birthday, Decoration Day, Independence Day,

Labor Day, Veterans Day, Thanksgiving Day,

Christmas Day and Martin Luther King's Birthday.

----------------------------------------------------------------

IRON0005A  06/01/2002

Rates           Fringes

IRONWORKERS:

Structural, Ornamental

and Chain Link Fence                23.23           8.605

----------------------------------------------------------------

IRON0201A  05/01/2002

Rates           Fringes

IRONWORKERS:

Reinforcing                         22.15           9.05

----------------------------------------------------------------

LABO0074B  06/01/2002

Rates           Fringes

LABORERS, HAZARDOUS WASTE REMOVAL,

(EXCEPT ON MECHANICAL SYSTEMS):

Preparation for, removing and

encapsulation of hazardous

materials from non-mechanical

systems

Skilled Asbestos Abatement

Laborers                           14.62           2.95

Skilled Toxic and Hazardous

Waste Removal Laborers             16.87           2.95

----------------------------------------------------------------

LABO0456D  06/01/2002

Rates           Fringes

LABORERS, PAVING & INCIDENTAL GRADING:

Sand Setter, Form Setter            15.28           3.80

Asphalt Raker, Concrete

Saw Operator                       14.74           3.80

Jack Hammer                         14.65           3.80

Asphalt Tammer, Concrete

Shoveler                           14.48           3.80

Asphalt Shoveler                    14.28           3.80

Laborer                             14.17           3.80

----------------------------------------------------------------

LABO0456E  06/01/2002

Rates           Fringes

LABORERS, TUNNEL, RAISE, & SHAFT (FREE AIR)

(FOR HEAVY AND SEWER & WATER LINES CONSTRUCTION)

GROUP  1                              17.90           2.95

GROUP  2                              18.39           2.95

GROUP  3                              19.67           2.95

GROUP  4                              20.18           2.95

LABORERS CLASSIFICATIONS

GROUP 1:  Brakeman, Bull Gang, Dumper, Trackman, Concrete Man.

GROUP 2:  Chuck Tender, Powdermen in Prime House, Form Setters

and Movers, Nippers, Cableman, Houseman, Groutman, Bell

or Signalman, Top or Bottom Vibrator Operator.

GROUP 3:  Miners, Re-Bar Underground, Concrete or Gunnite

Nozzlemen, Powdermen, Timbermen and Re-Timbermen,

Wood Steel Including Liner Plate or any Other Support,

Material, Motorman, Caulkers, Diamond Drill Operators,

Riggers, Cement Finishers - Underground, Welders and

Burners, Shield Driver, Air Trac Operator, Shotcrete

Nozzleman and Potman.

GROUP 4:  Mucking Machine Operator (Air).

----------------------------------------------------------------

LABO0456F  06/01/2002

Rates           Fringes

LABORERS (HEAVY AND HIGHWAY AND SEWER & WATER LINES CONSTRUCTION)

GROUP 1                               17.35           2.95

GROUP 2                               17.59           2.95

GROUP 3                               17.72           2.95

GROUP 4                               17.83           2.95

GROUP 5                               18.18           2.95

GROUP 6                               18.60           2.95

GROUP 7                               18.82           2.95

GROUP 8                               19.57           2.95

LABORERS CLASSIFICATIONS

GROUP 1:  Carloaders, choker setter, concrete crewman, crushed

feeder, demolition laborers, including salvaging all

material, loading, cleaning up, wrecking, dumpmen,

flagmen, fence erector and installer, including

installation and erection of fence, guard rails,

median rails, reference posts, guide posts and right-

of-way markers, form strippers, general laborers,

railroad track laborers, riprap man, scale man, stake

jumper, structure mover, includes foundation,

separation, preparation, cribbing, shoring, jacking and

unloading of structures, water nozzleman, timber bucker

and faller, truck loader, water boys, tool room men.

GROUP 2:  Combined air and water nozzleman, cement handler, dope

pot fireman (nonmechanical), form cleaning machine,

mechanical railroad equipment (includes spiker,

puller, tie cleaner, tamper, pipe wrapper, power driven

wheelbarrows, operators of hand derricks, towmasters,

scootcretes, buggymobiles and similar equipment),

tamper or rammer operator, trestle scaffold builders

over one tier high, power tool operator (gas, electric

or pneumatic), sandblast or gunnite tailhose man,

scaffold erector, (steel or wood), vibrator operator

up to 4 feet) asphalt cutter, mortar men, shorer and

lagger, creosote material handler, corrosive enamel or

equl, paver breaker and jackhammer operators.

GROUP 3:  Multi-section pipe layer, non-metallic clay and

concrete pipe layer (including caulker, collarman,

jointer, rigger and jacker, thermit welder and

corrugated metal culvert pipe layer.

GROUP 4:  Asphalt block pneumatic cutter, asphalt roller, walker

chainsaw operator with attachment, concrete saw

(walking), high scalers, jackhammer operator (using

over 6 feet of steel), vibrator operator (6 feet and

over), well point installer, air trac operator.

GROUP 5:  Asphalt screeder, big drills, cut of the hole drills,

(1 1/2" piston or larger), down the hole drills (3 1/2"

piston or larger), gunnite or sandblaster nozzleman,

asphalt raker, asphalt tamper, form setter, demolition

torch operator, shotcrete nozzlemen and potman.

GROUP 6:  Powderman, master form setters.

GROUP 7:  Brick paver (asphalt block paver, asphalt block sawman,

asphalt block grinder; hastings block or similar type)

GROUP 8:  Licensed powdermen.

----------------------------------------------------------------

LABO0456G  06/01/2002

Rates           Fringes

LABORERS, TUNNEL, RAISE, AND SHAFT

(COMPRESSED AIR) FOR HEAVY

CONSTRUCTION ONLY:

Gauge Pressure      Work Period

(Pounds)           (Hours)

1-14                7            21.56            2.95

14-18                6            25.46            2.95

On any requirement for air pressure in excess of 18

PSI, work periods and rates should be negotiated at

a pre-bid conference.

----------------------------------------------------------------

LABO0456H  06/01/2002

Rates           Fringes

LABORERS, BRICK MASONRY WORK:

Mason Tenders                      13.28           2.95

Scaffold Builders,

Mortarmen & Small

Equipment Operators               13.93           2.95

----------------------------------------------------------------

MARB0002E  05/01/2002

Rates           Fringes

MARBLE & STONE MASONS (Includes

Pointing, Caulking and Cleaning

of All types of Masonry, Brick,

Stone and Cement structures)        25.92           8.55

----------------------------------------------------------------

MARB0003I  05/01/2002

Rates           Fringes

MOSAIC and TERRAZZO WORKERS,

TILE LAYERS                         19.98           7.48

----------------------------------------------------------------

MARB0003O  05/01/2002

Rates           Fringes

MARBLE, TILE and TERRAZZO

FINISHERS                            16.42           6.52

----------------------------------------------------------------

PAIN0051A  01/16/2003

Rates           Fringes

PAINTERS:

All industrial work, industrial

lead abatement, abrasive blasting,

structural steel, suspended

scaffolding and rigging work of

any type, application of epoxies,

lacquers, and chlorinated rubber

base materials, and the application

of any industrial special coatings

and solvents on any surface         22.63           6.39

New commercial and public

construction, repaint,

remodeling, lead abatement,

spray painters, paperhangers

and drywall finishers               21.21           6.39

----------------------------------------------------------------

PLAS0891A  05/01/2002

Rates           Fringes

CEMENT MASONS (HEAVY CONSTRUCTION

ONLY)                               21.87           3.895

----------------------------------------------------------------

PLAS0891B  06/01/2002

Rates           Fringes

CEMENT MASONS, PAVING AND

INCIDENTAL GRADING:

Cement Masons                       15.50           3.90

Form Setters                        15.50           3.90

Concrete Saw Operators              15.50           3.90

----------------------------------------------------------------

PLUM0005A  08/01/2002

Rates           Fringes

PLUMBERS                              27.67           9.24

----------------------------------------------------------------

PLUM0602E  08/01/2002

Rates           Fringes

STEAMFITTERS, REFRIGERATION AND

AIR CONDITIONING MECHANICS          27.52           9.37+a

a.PAID HOLIDAYS: New Year's Day, Independence Day, Thanksgiving

Day and the day after Thanksgiving, Labor Day

and Christmas Day.

----------------------------------------------------------------

SHEE0100A  07/01/2002

Rates           Fringes

SHEET METAL WORKERS                   26.88           8.06

----------------------------------------------------------------

TEAM0639C  03/07/2002

Rates           Fringes

TRUCK DRIVERS (HEAVY AND

HIGHWAY CONSTRUCTION):

Tandem & Triaxle

(3 or more axles, including

steering axle)                    15.00           5.02+a

Tractor-trailer, Low-boy            18.00           5.02+a

a. VACATION:  Employees will receive one (1) week's paid

vacation after one (1) year of service.

----------------------------------------------------------------

TEAM0639N  04/01/2002

Rates           Fringes

TRUCK DRIVERS (HEAVY AND

HIGHWAY CONSTRUCTION):

Concrete Mixer Drivers              15.95           5.07+a+b

a. PAID HOLIDAYS: New Year's Day, Martin Luther King, Jr. Day,

Memorial Day, July 4th, Labor Day, Thanksgiving

Day, Christmas Day, or any day celebrated

publicly in the District of Columbia as one of

the above holidays.

b. PAID VACATIONS: Employees with one (1) year of service shall

be entitled to a vacation of one (1) week;

five (3) years of service are entitled to two

(2) weeks; fifteen (10) years of service are

entitled to three 3 weeks; twenty (20) years

of service are entitled to four (4) weeks.

----------------------------------------------------------------

TEAM0639O  09/01/2002

Rates           Fringes

TRUCK DRIVERS (PAVING AND

INCIDENTAL GRADING)

All paving projects where

the grading is incidental

to the paving                       13.00           3.09

----------------------------------------------------------------

WELDERS - Receive rate prescribed for craft performing operation

to which welding is incidental.

================================================================

Unlisted classifications needed for work not included within

the scope of the classifications listed may be added after

award only as provided in the labor standards contract clauses

(29 CFR 5.5(a)(1)(ii)).

----------------------------------------------------------------

In the listing above, the "SU" designation means that rates

listed under that identifier do not reflect collectively

bargained wage and fringe benefit rates.  Other designations

indicate unions whose rates have been determined to be

prevailing.

WAGE DETERMINATION APPEALS PROCESS

1.) Has there been an initial decision in the matter?  This can

be:

* an existing published wage determination

* a survey underlying a wage determination

* a Wage and Hour Division letter setting forth a

position on a wage determination matter

* a conformance (additional classification and rate)

ruling

On survey related matters, initial contact, including requests

for summaries of surveys, should be with the Wage and Hour

Regional Office for the area in which the survey was conducted

because those Regional Offices have responsibility for the

Davis-Bacon survey program.  If the response from this initial

contact is not satisfactory, then the process described in 2.)

and 3.) should be followed.

With regard to any other matter not yet ripe for the formal

process described here, initial contact should be with the Branch

of Construction Wage Determinations.  Write to:

Branch of Construction Wage Determinations

Wage and Hour Division

U. S. Department of Labor

200 Constitution Avenue, N. W.

Washington, D. C.  20210

2.) If the answer to the question in 1.) is yes, then an

interested party (those affected by the action) can request

review and reconsideration from the Wage and Hour Administrator

(See 29 CFR Part 1.8 and 29 CFR Part 7). Write to:

Wage and Hour Administrator

U.S. Department of Labor

200 Constitution Avenue, N. W.

Washington, D. C.  20210

The request should be accompanied by a full statement of the

interested party's position and by any information (wage payment

data, project description, area practice material, etc.) that the

requestor considers relevant to the issue.

3.) If the decision of the Administrator is not favorable, an

interested party may appeal directly to the Administrative Review

Board (formerly the Wage Appeals Board). Write to:

Administrative Review Board

U. S. Department of Labor

200 Constitution Avenue, N. W.

Washington, D. C.  20210

4.) All decisions by the Administrative Review Board are final.

END OF GENERAL DECISION

K.1  52.203-11  CERTIFICATION AND DISCLOSURE REGARDING PAYMENTS TO INFLUENCE CERTAIN FEDERAL TRANSACTIONS (APR 1991)

(Reference 3.808)

K.2  52.204-3  TAXPAYER IDENTIFICATION (OCT 1998)

(Reference 4.905)

K.3  52.222-21  PROHIBITION OF SEGREGATED FACILITIES (FEB 1999)

(Reference 22.810)

K.4  52.203-2  CERTIFICATE OF INDEPENDENT PRICE DETERMINATION (APR 1985)

(a) The offeror certifies that--

(1) The prices in this offer have been arrived at independently,

without, for the purpose of restricting competition, any consultation,

communication, or agreement with any other offeror or competitor relating

to (i) those prices, (ii) the intention to submit an offer, or (iii) the

methods or factors used to calculate the prices offered;

(2) The prices in this offer have not been and will not be knowingly

disclosed by the offeror, directly or indirectly, to any other offeror or

competitor before bid opening (in the case of a sealed bid solicitation)

or contract award (in the case of a negotiated solicitation) unless

otherwise required by law; and

(3) No attempt has been made or will be made by the offeror to induce

any other concern to submit or not to submit an offer for the purpose of

restricting competition.

(b) Each signature on the offer is considered to be a certification by the signatory that the signatory--

(1) Is the person in the offeror's organization responsible for

determining the prices being offered in this bid or proposal, and that

the signatory has not participated and will not participate in any action

contrary to subparagraphs (a)(1) through (a)(3) of this provision; or

(2)(i) Has been authorized, in writing, to act as agent for the

following principals in certifying that those principals have not

participated, and will not participate in any action contrary to

subparagraphs (a)(1) through (a)(3) of this provision___________________

________________________________________________________________________

[insert full name of person(s) in the offeror's organization responsible

for determining the prices offered in this bid or proposal, and the

title of his or her position in the offeror's organization];

(ii) As an authorized agent, does certify that the principals named

in subdivision (b)(2)(i) of this provision have not participated, and

will not participate, in any action contrary to subparagraphs (a)(1)

through (a)(3) of this provision; and

(iii) As an agent, has not personally participated, and will not

participate, in any action contrary to subparagraphs (a)(1) through

(a)(3) of this provision.

(c) If the offeror deletes or modifies subparagraph (a)(2) of this provision, the offeror must furnish with its offer a signed statement setting forth in detail the circumstances of the disclosure.

(End of provision)

K.5  52.209-5  CERTIFICATION REGARDING DEBARMENT, SUSPENSION, PROPOSED DEBARMENT, AND OTHER RESPONSIBILITY MATTERS (DEC 2001)

(a)(1) The Offeror certifies, to the best of its knowledge and belief, that--

(i) The Offeror and/or any of its Principals--

(A) Are / / are not / / presently debarred, suspended, proposed for

debarment, or declared ineligible for the award of contracts by any

Federal agency;

(B) Have / / have not / /, within a three-year period preceding

this offer, been convicted of or had a civil judgment rendered

against them for:  commission of fraud or a criminal offense in

connection with obtaining, attempting to obtain, or performing a

public (Federal, state, or local) contract or subcontract; violation

of Federal or state antitrust statutes relating to the submission of

offers; or commission of embezzlement, theft, forgery, bribery,

falsification or destruction of records, making false statements,

tax evasion, or receiving stolen property; and

(C) Are / / are not / / presently indicted for, or otherwise

criminally or civilly charged by a governmental entity with,

commission of any of the offenses enumerated in paragraph

(a)(1)(i)(B) of this provision.

(ii) The Offeror has / / has not / /, within a three-year period

preceding this offer, had one or more contracts terminated for default

by any Federal agency.

(2) "Principals," for the purposes of this certification, means

officers; directors; owners; partners; and, persons having primary

management or supervisory responsibilities within a business entity

(e.g., general manager; plant manager; head of a subsidiary, division,

or business segment, and similar positions). THIS CERTIFICATION CONCERNS A MATTER WITHIN THE JURISDICTION OF AN AGENCY OF THE UNITED STATES AND THE MAKING OF A FALSE, FICTITIOUS, OR FRAUDULENT CERTIFICATION MAY RENDER THE MAKER SUBJECT TO PROSECUTION UNDER SECTION 1001, TITLE 18, UNITED STATES CODE.

(b) The Offeror shall provide immediate written notice to the Contracting Officer if, at any time prior to contract award, the Offeror learns that its certification was erroneous when submitted or has become erroneous by reason of changed circumstances.

(c) A certification that any of the items in paragraph (a) of this provision exists will not necessarily result in withholding of an award under this solicitation.  However, the certification will be considered in connection with a determination of the Offeror's responsibility.  Failure of the Offeror to furnish a certification or provide such additional information as requested by the Contracting Officer may render the Offeror nonresponsible.

(d) Nothing contained in the foregoing shall be construed to require establishment of a system of records in order to render, in good faith, the certification required by paragraph (a) of this provision.  The knowledge and information of an Offeror is not required to exceed that which is normally possessed by a prudent person in the ordinary course of business dealings.

(e) The certification in paragraph (a) of this provision is a material representation of fact upon which reliance was placed when making award. If it is later determined that the Offeror knowingly rendered an erroneous certification, in addition to other remedies available to the Government, the Contracting Officer may terminate the contract resulting from this solicitation for default.

(End of provision)

K.6  52.215-6  PLACE OF PERFORMANCE BUSINESS (OCT 1997)

(a) The offeror or respondent, in the performance of any contract resulting from this solicitation, /__________  intends, / __________ ,  does not intend to use one or more plants or facilities located at a  different address from the address of the offeror or respondent as  indicated in this proposal or response to request for information.

(b) If the offeror or respondent checks "intends" in paragraph (a) of this provision, it shall insert in the following spaces the required information: __________________________________________________________________________

PLACE OF PERFORMANCE (STREET            NAME AND ADDRESS OF OWNER AND ADDRESS, CITY, STATE, COUNTY, ZIP       OPERATOR OF THE PLANT OR FACILITY

CODE)                                 IF OTHER THAN OFFEROR OR RESPONDENT ___________________________________________________________________________ _________________________________       _______________________________ _________________________________       _______________________________ ___________________________________________________________________________

(End of provision)

K.7  52.215-11  PRICE REDUCTION FOR DEFECTIVE COST OR PRICING DATA--MODIFICATIONS (OCT 1997)

(a) This clause shall become operative only for any modification to this contract involving a pricing adjustment expected to exceed the threshold for submission of cost or pricing data at FAR 15.403-4, except that this clause does not apply to any modification if an exception under FAR 15.403-1 applies.

(b) If any price, including profit or fee, negotiated in connection with any modification under this clause, or any cost reimbursable under this contract, was increased by any significant amount because (1) the Contractor or a subcontractor furnished cost or pricing data that were not complete, accurate, and current as certified in its Certificate of Current Cost or Pricing Data, (2) a subcontractor or prospective subcontractor furnished the Contractor cost or pricing data that were not complete, accurate, and current as certified in the Contractor's Certificate of Current Cost or Pricing Data, or (3) any of these parties furnished data of any description that were not accurate, the price or cost shall be reduced accordingly and the contract shall be modified to reflect the reduction.  This right to a price reduction is limited to that resulting from defects in data relating to modifications for which this clause becomes operative under paragraph (a) of this clause.

(c) Any reduction in the contract price under paragraph (b) of this clause due to defective data from a prospective subcontractor that was not subsequently awarded the subcontract shall be limited to the amount, plus applicable overhead and profit markup, by which--

(1) The actual subcontract; or

(2) The actual cost to the Contractor, if there was no subcontract,

was less than the prospective subcontract cost estimate submitted by the

Contractor; provided, that the actual subcontract price was not itself

affected by defective cost or pricing data.

(d)(1) If the Contracting Officer determines under paragraph (b) of this clause that a price or cost reduction should be made, the Contractor agrees not to raise the following matters as a defense:

(i) The Contractor or subcontractor was a sole source supplier or

otherwise was in a superior bargaining position and thus the price of

the contract would not have been modified even if accurate, complete,

and current cost or pricing data had been submitted.

(ii) The Contracting Officer should have known that the cost or

pricing data in issue were defective even though the Contractor or

subcontractor took no affirmative action to bring the character of the

data to the attention of the Contracting Officer.

(iii) The contract was based on an agreement about the total cost of

the contract and there was no agreement about the cost of each item

procured under the contract.

(iv) The Contractor or subcontractor did not submit a Certificate of

Current Cost or Pricing Data.

(2)(i) Except as prohibited by subdivision (d)(2)(ii) of this clause,

an offset in an amount determined appropriate by the Contracting Officer

based upon the facts shall be allowed against the amount of a contract

price reduction if--

(A) The Contractor certifies to the Contracting Officer that, to

the best of the Contractor's knowledge and belief, the Contractor is

entitled to the offset in the amount requested; and

(B) The Contractor proves that the cost or pricing data were

available before the "as of" date specified on its Certificate of

Current Cost or Pricing Data, and that the data were not submitted

before such date.

(ii) An offset shall not be allowed if--

(A) The understated data were known by the Contractor to be

understated before the "as of" date specified on its Certificate of

Current Cost or Pricing Data; or

(B) The Government proves that the facts demonstrate that the

contract price would not have increased in the amount to be offset

even if the available data had been submitted before the "as of" date

specified on its Certificate of Current Cost or Pricing Data.

(e) If any reduction in the contract price under this clause reduces the price of items for which payment was made prior to the date of the modification reflecting the price reduction, the Contractor shall be liable to and shall pay the United States at the time such overpayment is repaid--

(1) Simple interest on the amount of such overpayment to be computed

from the date(s) of overpayment to the Contractor to the date the

Government is repaid by the Contractor at the applicable underpayment

rate effective for each quarter prescribed by the Secretary of the

Treasury under 26 U.S.C. 6621(a)(2); and

(2) A penalty equal to the amount of the overpayment, if the

Contractor or subcontractor knowingly submitted cost or pricing data that

were incomplete, inaccurate, or noncurrent.

(End of clause)

K.8  52.219-1  SMALL BUSINESS PROGRAM REPRESENTATIONS (Apr 2002)

(a)(1) The North American Industry Classification System (NAICS) code for this acquisition is __________

(2) The small business size standard is __________

(3) The small business size standard for a concern which submits an

offer in its own name, other than on a construction or service contract,

but which proposes to furnish a product which it did not itself

manufacture, is 500 employees.

(b) Representations.  (1) The offeror represents as part of its offer that it /_ / is, /_ / is not a small business concern.

(2) [Complete only if the offeror represented itself as a small

business concern in paragraph (b)(1) of this provision.]  The offeror

represents, for general statistical purposes, that it /_ / is, /_ / is

not, a small disadvantaged business concern as defined in 13 CFR

124.1002.

(3) [Complete only if the offeror represented itself as a small

business concern in paragraph (b)(1) of this provision.]  The offeror

represents as part of its offer that it /_ / is, /_ / is not a

women-owned small business concern.

(4) [Complete only if the offeror represented itself as a small

business concern in paragraph (b)(1) of this provision.]  The offeror

represents as part of its offer that it [ ] is, [ ] is not a

veteran-owned small business concern.

(5) [Complete only if the offeror represented itself as a veteran-owned

small business concern in paragraph (b)(4) of this provision.]  The

offeror represents as part of its offer that it [ ] is, [ ] is not a

service-disabled veteran-owned small business concern.

(6) ["Complete only if the offeror represented itself as a small

business concern in paragraph (b)(1) of this provision."] The offeror

represents, as part of its offer, that--

(i) It o is, o is not a HUBZone small business concern listed, on the

date of this representation, on the List of Qualified HUBZone Small

Business Concerns maintained by the Small Business Administration, and no

material change in ownership and control, principal office, or HUBZone

employee percentage has occurred since it was certified by the Small

Business Administration in accordance with 13 CFR part 126; and

(ii) It o is, o is not a joint venture that complies with the

requirements of 13 CFR part 126, and the representation in paragraph

(b)(6)(i) of this provision is accurate for the HUBZone small business

concern or concerns that are participating in the joint venture. [The

offeror shall enter the name or names of the HUBZone small business

concern or concerns that are participating in the joint venture:

__________.] Each HUBZone small business concern participating in the

joint venture shall submit a separate signed copy of the HUBZone

representation.

(c) Definitions.  As used in this provision--

"Service-disabled veteran-owned small business concern"--

(1) Means a small business concern--

(i) Not less than 51 percent of which is owned by one or more

service-disabled veterans or, in the case of any publicly owned

business, not less than 51 percent of the stock of which is owned by

one or more service-disabled veterans; and

(ii) The management and daily business operations of which are

controlled by one or more service-disabled veterans or, in the case of

a veteran with permanent and severe disability, the spouse or permanent

caregiver of such veteran.

(2) Service-disabled veteran means a veteran, as defined in 38 U.S.C.

101(2), with a disability that is service-connected, as defined in 38

U.S.C. 101(16).

"Small business concern," means a concern, including its affiliates, that is independently owned and operated, not dominant in the field of operation in which it is bidding on Government contracts, and qualified as a small business under the criteria in 13 CFR Part 121 and the size standard in paragraph (a) of this provision.

"Veteran-owned small business concern" means a small business concern--

(1) Not less than 51 percent of which is owned by one or more veterans (as defined at 38 U.S.C. 101(2)) or, in the case of any publicly owned business, not less than 51 percent of the stock of which is owned by one or more veterans; and

(2) The management and daily business operations of which are

controlled by one or more veterans.

"Women-owned small business concern," means a small business concern--

(1) Which is at least 51 percent owned by one or more women or, in the

case of any publicly owned business, at least 51 percent of the stock of

which is owned by one or more women; and

(2) Whose management and daily business operations are controlled by

one or more women.

(d) Notice.  (1) If this solicitation is for supplies and has been set aside, in whole or in part, for small business concerns, then the clause in this solicitation providing notice of the set-aside contains restrictions on the source of the end items to be furnished.

(2) Under 15 U.S.C. 645(d), any person who misrepresents a firm's

status as a small, HUBZone small, small disadvantaged, or women-owned

small business concern in order to obtain a contract to be awarded under

the preference programs established pursuant to section 8(a), 8(d), 9, or

15 of the Small Business Act or any other provision of Federal law that

specifically references section 8(d) for a definition of program

eligibility, shall--

(i)  Be punished by imposition of fine, imprisonment, or both;

(ii) Be subject to administrative remedies, including suspension and

debarment; and

(iii) Be ineligible for participation in programs conducted under the

authority of the Act.

(End of provision)

K.9  52.222-22  PREVIOUS CONTRACTS AND COMPLIANCE REPORTS (FEB 1999)

The offeror represents that--

(a) It /_/ has, /_/ has not participated in a previous contract or subcontract subject either to the Equal Opportunity clause of this solicitation;

(b) It /_/ has, /_/ has not, filed all required compliance reports; and

(c) Representations indicating submission of required compliance reports, signed by proposed subcontractors, will be obtained before subcontract awards.

(End of provision)

K.10  52.222-25  AFFIRMATIVE ACTION COMPLIANCE (APR 1984)

The offeror represents that (a) it /_/ has developed and has on file, /_/ has not developed and does not have on file, at each establishment, affirmative action programs required by the rules and regulations of the Secretary of Labor (41 CFR 60-1 and 60-2), or (b) it /_/ has not previously had contracts subject to the written affirmative action programs requirement of the rules and regulations of the Secretary of Labor.

(End of provision)

L.1  52.215-5  FACSIMILE PROPOSALS (OCT 1997)

(Reference 15.209)

L.2  52.215-7  ANNUAL REPRESENTATIONS AND CERTIFICATIONS--NEGOTIATION (OCT 1997)

(Reference 15.209)

L.3  52.215-8  ORDER OF PRECEDENCE--UNIFORM CONTRACT FORMAT (OCT 1997)

(Reference 15.209)

L.4  52.215-9  CHANGES OR ADDITIONS TO MAKE-OR-BUY PROGRAM (OCT 1997)

(Reference 15.408)

L.5  52.215-10  PRICE REDUCTION FOR DEFECTIVE COST OR PRICING DATA (OCT 1997)

(Reference 15.408)

L.6  52.215-12  SUBCONTRACTOR COST OR PRICING DATA (OCT 1997)

(Reference 15.408)

L.7  52.215-13  SUBCONTRACTOR COST OR PRICING DATA--MODIFICATIONS (OCT 1997)

(Reference 15.408)

L.8  52.215-14  INTEGRITY OF UNIT PRICES (OCT 1997)

(Reference 15.408)

L.9  52.237-1  SITE VISIT (APR 1984)

(Reference 37.110)

L.10  52.204-6  DATA UNIVERSAL NUMBERING SYSTEM (DUNS) NUMBER (JUNE 1999)

(a) The offeror shall enter, in the block with its name and address on the cover page of its offer, the annotation "DUNS" followed by the DUNS number that identifies the offeror's name and address exactly as stated in the offer.  The DUNS number is a nine-digit number assigned by Dun and Bradstreet Information Services.

(b) If the offeror does not have a DUNS number, it should contact Dun and Bradstreet directly to obtain one.  A DUNS number will be provided immediately by telephone at no charge to the offeror.  For information on obtaining a DUNS number, the offeror, if located within the United States, should call Dun and Bradstreet at 1-800-333-0505.  The offeror should be prepared to provide the following information:

(1) Company name.

(2) Company address.

(3) Company telephone number.

(4) Line of business.

(5) Chief executive officer/key manager.

(6) Date the company was started.

(7) Number of people employed by the company.

(8) Company affiliation.

(c) Offerors located outside the United States may obtain the location and phone number of the local Dun and Bradstreet Information Services office from the Internet Home Page at http://www.customerservice@dnb.com. If an offeror is unable to locate a local service center, it may send an e-mail to Dun and Bradstreet at globalinfo@mail.dnb.com.

(End of provision)

L.11  52.216-1  TYPE OF CONTRACT (APR 1984)

The Government contemplates award of a Firm Fixed Price contract resulting  from this solicitation.

(End of provision)

L.12  52.233-2  SERVICE OF PROTEST (AUG 1996)

(a) Protests, as defined in section 33.101 of the Federal Acquisition Regulation, that are filed directly with an agency, and copies of any protests that are filed with the General Accounting Office (GAO), shall be served on the Contracting Officer (addressed as follows) by obtaining written and dated acknowledgment of receipt from _Booker Weaver

(b) The copy of any protest shall be received in the office designated above within one day of filing a protest with the GAO.

(End of provision)

L.13  52.252-3  ALTERATIONS IN SOLICITATION (APR 1984)

Portions of this solicitation are altered as follows: __________

(End of provision)

L.14  52.252-4  ALTERATIONS IN CONTRACT (APR 1984)

Portions of this contract are altered as follows: __________

(End of clause)

L.15  52.252-5  AUTHORIZED DEVIATIONS IN PROVISIONS (APR 1984)

(a) The use in this solicitation of any Federal Acquisition Regulation (48 CFR Chapter 1) provision with an authorized deviation is indicated by the addition of "(DEVIATION)" after the date of the provision.

(b) The use in this solicitation of any __________ (48 CFR Chapter   __________  provision with an authorized deviation is indicated by the  addition of "(DEVIATION)" after the name of the regulation.

(End of provision)

L.16  52.252-6  AUTHORIZED DEVIATIONS IN CLAUSES (APR 1984)

(a) The use in this solicitation or contract of any Federal Acquisition Regulation (48 CFR Chapter 1) clause with an authorized deviation is indicated by the addition of "(DEVIATION)" after the date of the clause.

(b) The use in this solicitation or contract of any __________ (48 CFR  __________  clause with an authorized deviation is indicated by the  addition of "(DEVIATION)" after the name of the regulation.

(End of clause)

M.1  EVALUATION FACTORS

SECTION M

The Government intends to award a contract to that contractor who offers the lowest price and has at least a satisfactory history of past performance. The Government reserves the right to perform a trade-off between price and past performance and award to a higher priced contractor who has a past performance rating higher than satisfactory.  The Government reserves the right to consider other projects performed by contractor and identified to the Government through any and all means, including but not limited to customer surveys and comments from other Government agencies.

# PAST PERFORMANCE

Provide at least 3 sources that reflect similar projects in the size and scope  that the contractor has successfully complete.

The contractor shall include:

1.	Program Office Technical Point of Contact (POC):

2.	Telephone/Fax No.

3.            Title of Work

4.	Duration of contract; and

5.	Contract dollar value

Instruction to Contractors:

The contractor shall submit and original and  four copies of the proposal via USPS, FedEx, or hand carried.

Armed Forces Retirement Home-Washington (AFRH-W)

Bldg. #74/Contracting Division

3700 North Capitol Street, NW

Washington, D.C. 20317-0002

202-730-3558

202-730-3589 (Fax)

USSAH13@yahoo.com (e-mail)

Attention: Booker Weaver, Contract Specialist

The Contractor shall provide the following information:

Company Federal Tax ID No.: ______________________________

Company DUNS No.:________________________________________

Company POC:_____________________________________________

Phone No.:_______________________________________________

Fax No.:_________________________________________________

e- mail Address:__________________________________________

M.2  52.217-4  EVALUATION OF OPTIONS EXERCISED AT TIME OF CONTRACT AWARD (JUN 1988)

Except when it is determined in accordance with FAR 17.206(b) not to be in the Government's best interests, the Government will evaluate the total price for the basic requirement together with any option(s) exercised at the time of award.

(End of provision)

M.3  52.217-5  EVALUATION OF OPTIONS (JUL 1990)

Except when it is determined in accordance with FAR 17.206(b) not to be in the Government's best interests, the Government will evaluate offers for award purposes by adding the total price for all options to the total price for the basic requirement.  Evaluation of options will not obligate the Government to exercise the option(s).

(End of provision)