Preservation Note 10

Fire Alarm Installations

Special Construction

August- 91

Detection and Alarm-13850

Include the following guidelines in all scopes of work for the design of fire alarm systems in historic buildings:

--------------------------------------------------------------------------------

V. Special Considerations

Protection of Ornamental Materials: Special care shall be taken to avoid penetration into stone, unpainted wood, unpainted metal, ceramic materials, ornamental plaster, decorative painting, and other ornamental finishes. Use the following rules of thumb for the placement of hardware in ornamental wall finishes:

1. Reuse existing holes for surface mounted or recessed alarm pulls and bells/horns located in stone and other ornamental finishes. This is a accomplished by staging the installation as continuous fire protection:

Install the new system as completely as possible in areas where pull and alarm locations will not be reused prior to exchanging new pulls and horns for old pulls and alarms on ornamental surfaces. Do not remove old hardware and install new until the new equipment has been tested successfully and approved by the Fire Protection Engineering Branch (WPXE).

Interconnect the old and new fire alarm control panels so that pulls connected to either the existing or new system will activate all alarms while the new system is being installed.

Retest the substantially completed new system prior to demolition of the existing system in areas where pulls and alarms will be reused.

Selectively remove and replace existing equipment in accordance with phased installation plan approved by WPXE. Sequence circuit selection to minimize down time.

2.Reuse alarm and pull housings (backboxes), where possible, installing new pulls in place of existing pulls. Reuse original ornamental grilles concealing bells in stone, unpainted wood, and other ornamental materials.

3. Specify fabrication of new metal alarm pulls detailed as similarly as possible to the original pulls. Where original plates do not exist, custom fabricate new metal cover plates for surface mounted hardware, matching the building's original hardware in color and finish.

4. When reuse of existing bells on ornamental surfaces is not possible, leave existing bells in place and install new bells or horns, in flat plaster if possible, at least five feet from the original hardware's location.

5. Retention of abandoned pulls violates GSA fire safety standards concerned with possible confusion between defunct and active hardware during an emergency. Exceptions are granted by WPXE, on a case by case basis only, when all evidence of the pull's original function is removed (e.g. filing off raised lettering, this is a last resort, avoid abandoning pulls in stone by reusing existing backboxes for new pull locations when at all possible.