Attachment 5

FIRE PROTECTION AND LIFE SAFETY
REVISED SFO PARAGRAPHS

# CERTIFICATE OF OCCUPANCY (MAY 2005)

The Lessor shall provide a valid Certificate of Occupancy, issued by the local jurisdiction, for the intended use of the Government and shall maintain and operate the building in conformance with current local codes and ordinances.  If the local jurisdiction does not issue Certificates of Occupancy, the Offeror shall obtain the services of a licensed fire protection engineer to verify the offered space meets all applicable local codes and ordinances to ensure an acceptable level of safety is provided.

# FIRE PROTECTION AND LIFE SAFETY (MAY 2005)

A.	Offered space shall meet or be upgraded to meet prior to occupancy, the applicable egress requirements in the National Fire Protection Association (NFPA) 101, Life Safety Code, or an alternative approach or method for achieving a level of safety deemed equivalent and acceptable by the Government.

B.	Offered space shall provide unrestrictive access to a minimum of two remote exits on each floor of Government occupancy. Scissor stairs shall only be counted as one approved exit. Open air exterior fire escapes shall not be counted as an approved exit.

# AUTOMATIC FIRE SPRINKLER SYSTEM (MAY 2005)

A.	Offered space located below-grade, including parking garage areas, and all areas in a building referred to as "hazardous areas" (defined in NFPA 101) that are located within the entire building (including non-Government areas) shall be protected by an automatic fire sprinkler system or an equivalent level of safety.

B.	For buildings in which any portion of the offered space is on or above the sixth floor, then, at a minimum, the building up to and including the highest floor of Government occupancy shall be protected by an automatic fire sprinkler system or an equivalent level of safety.

C.	For buildings in which any portion of the offered space is on or above the sixth floor, and lease of the offered space will result, either individually or in combination with other Government leases in the offered building, in the Government leasing 35,000 square feet or more ANSI/BOMA Office Area square feet of space in the offered building, then the entire building shall be protected throughout by an automatic fire sprinkler system or an equivalent level of safety.

D.	Automatic sprinkler system(s) shall be maintained in accordance with the requirements of the applicable local codes or NFPA 25, Standard for the Inspection, Testing, and Maintenance of Water-based Fire Protection Systems.

E.	Definitions:

1.	“Automatic sprinkler system” means an electronically supervised, integrated system of underground and overhead piping, designed in accordance with National Fire Protection Association (NFPA) 13, Installation of Sprinkler Systems. The system is usually activated by heat from fire and discharges water over the fire area. The system includes an adequate water supply.

2.	"Equivalent level of safety" means an alternative design or system (which may include automatic sprinkler systems), based upon fire protection engineering analysis, which achieves a level of safety equal to or greater than that provided by automatic sprinkler systems.

# FIRE ALARM SYSTEM (MAY 2005)

A.	A building-wide fire alarm system shall be installed in buildings in which any portion of the offered space is located 2 or more stories above the lowest level of exit discharge. The fire alarm system shall meet the installation and operational requirements of the applicable local codes and ordinances (current as of the date of this SFO) adopted by the jurisdiction in which the building is located.

B.	The fire alarm system shall be maintained in accordance with the requirements of the applicable local codes or NFPA 72, National Fire Alarm Code. The fire alarm system wiring and equipment shall be electrically-supervised and shall automatically notify the local fire department or approved central station. Emergency power shall be provided for the fire alarm system.