NRC INSPECTION MANUAL

INSPECTION PROCEDURE 70325

PREOPERATIONAL TEST RESULTS EVALUATION -

REACTOR PROTECTION SYSTEM

PROGRAM APPLICABILITY:

70325-01	INSPECTION OBJECTIVES

01.01	Assure that test results are being adequately evaluated.

01.02	Assure test data meets acceptance criteria, and that deviations are properly identified and resolved.

01.03	Verify that the review procedures are being followed.

01.04	Evaluate the adequacy of the licensee's administrative practices with respect to test execution and data evaluation.

70325-02	INSPECTION REQUIREMENTS

The inspector shall:

02.01	Review Regulatory Guide 1.68 and FSAR to determine licensee commitments;

02.02	Review the Reactor Protection System Test results per inspection procedure MC 70400.

70325-03	INSPECTION GUIDANCE

03.01	The inspector should review the test requirements and licensee commitments related to this test.  In addition to Regulatory Guide 1.68 and the FSAR, this may include a review of the TS, SER and docketed correspondence with the licensee.

03.02	Items which should be included in the evaluation of test result data include (but are not limited to):

a.	A test verified that each protection sensor is calibrated and the channel trips are properly set, including TIP calibration system.

b.	A test verifies that each combination of required channel trips will scram the reactor.  All possible combinations of logic should be checked during the testing.

c.	The breaker test should demonstrate that those protection systems which have two or more methods of tripping a scram breaker do function in all possible combination for each trip mode.

d.	Scram valve operational test.

e.	A test verifies that a scram occurs on loss of electrical power and on instrument air if applicable (most plants can be safely controlled and shutdown under controlled conditions upon loss of instrument air - review instrument air test to confirm requirements for loss of instrument air).

f.	Integrated test.

g.	Support and auxiliary systems are functional as required.

h.	Verify that the standard test results and review requirements are met.

i.	Results of reactor vessel high pressure, low water level and discharge volume high water level.

j.	The inspector should observe one of the following tests and 10% of the data for the test:

(a)	Containment high pressure

(b)	Condenser low vacuum

(c)	Main steam line high radiation and main steam isolation valve closure.

(d)	Reactor manual scram (scram button should be depressed for short time period only).

k.	Reactor Protection System (RPS) Scram relays test (purpose of these tests is to prove that by de-energizing the scram relays in the proper logic, the reactor will be scrammed).

l.	RPS auxiliary functions test.

m.	RPS Response Time Test (purpose of this test is to measure the system response time from trip to rods inserted to various percentages (examples:  10%, 25%, 50%, 75%, and 90% - measurements may be taken at only one or two of these points).

END