NRC INSPECTION MANUAL	CPNB

INSPECTION PROCEDURE 73757

PART 52, PRESERVICE INSPECTION - DATA REVIEW AND EVALUATION

PROGRAM APPLICABILITY:  2504

73757-01	INSPECTION OBJECTIVES

To ascertain, whether the reported data covers the scope of examination required for the Preservice (PSI) Inspection of general components listed in the tables of IWB-2500, IWC-2500, and IWD-2500 of ASME Section XI, as described in: the applicable ASME Code, Section III and Section XI; the technical requirements manual (TRM) and/or site director procedures manual (SDPM); and the PSI program filed with the NRC.

To ascertain whether the reported data covers the scope of examination required for the PSI of critical ASME Class 1 components as described in: the applicable ASME Code, the TRM/SDPM, and PSI program filed with the NRC.

73757-02	INSPECTION REQUIREMENTS AND GUIDANCE

General Guidance:	The inspections of interest in this procedure are those nondestructive examinations of Class 1, 2, and 3 components performed to meet the requirements of the TRM/SDPM, and the PSI program filed with the NRC.  Inservice testing of pumps and valves as described in ASME Code, Section XI is not included within the scope of this procedure.

Examination data, test results, and other NDE data and records are essential to establish a baseline for comparison with future examinations as part of the history of findings and indications.  Evaluation of the previous growth rate of flaws and other indications permits a realistic prediction of expected further growth based on valid examination data.  It is, therefore, essential to have complete, reliable, and clear NDE data, and records for each examination.

This inspection procedure will review examination findings to assure that corrective measures are taken on adverse findings, and to ensure that the licensee has utilized an Authorized Nuclear Inservice Inspector (ANII), as required by regulation.  If the situation arises wherein the authorized inspector appears to have neglected to perform his assigned activities, the matter should be referred to the NRC Headquarters.

For the purpose of this inspection procedure, the term, "PSI/ISI program," includes the PSI/ISI plan, the repair/replacement plan, and the administrative, technical, and quality assurance programs/procedures required to implement the plan.

Pursuant to 10 CFR 50.55a(g)(3)(i), components (including supports) which are classified as ASME Code Class 1 must meet the preservice examination requirements set forth in the editions and addenda of Section XI of the ASME Boiler and Pressure Vessel Code incorporated by reference in paragraph 10 CFR 50.55a(b) (or the optional ASME Code cases listed in NRC Regulatory Guide 1.147, incorporated by reference in paragraph 10 CFR 50.55a(b)) applied to the construction of the particular component.

Components which are classified as ASME Code Class 2 and Class 3 and supports for components which are classified as ASME Code Class 1, Class 2, and Class 3...must meet the preservice examination requirements set forth in the editions and addenda of Section XI of the ASME Boiler and Pressure Vessel Code incorporated by reference in paragraph 10 CFR 50.55a(b) (or the optional ASME Code cases listed in NRC Regulatory Guide 1.147, incorporated by reference in paragraph 10 CFR 50.55a(b)) applied to the construction of the particular component.

02.01	General Records Review.	Perform the following:

a.	Obtain and Review at least three site preservice NDE inspection records from each examination category of tables IWB-2500 (B-F through B-O, not addressed in 02.02), IWC-2500 (C-A through C-G), and IWD-2500 (D-A) of ASME Section XI.  Ascertain whether the reported extent of examinations for those Class 1, 2, and 3 components and areas subject to examination meet the minimum examination requirements specified in the applicable addenda of the ASME Code, Section XI.

b.	Verify the selected records are consistent with the TRM/SDPM, and PSI program and contain or provide reference to the following:

Guidance:  Use the following listing of required information as a "checklist" during the review of the selected sets of NDE records for completeness and technical adequacy.

1.	Examination results and data sheets;

2.	Examination equipment data;

3.	Calibration data sheets;

4.	Examination evaluation data;

5.	Records on extent of examination;

6.	Records on deviation from program and procedures including justification for deviation;

7.	Records on disposition of findings.  Evaluation of indications complies with the criteria of the NDE procedure and ASME Code Section XI;

8.	Re-examination data after repair work;

9.	Identification of NDE material such as penetrant, penetrant cleaner, couplant, films, tapes, etc;

10.	Evaluation of examination data is performed by a Level II or Level III examiner;

11.	Design and access provisions are sufficient to enable the performance of preservice examinations including the coverage specified by ASME Section XI;

12.	Incomplete examinations and results were repeated to permit full evaluation, if applicable; and

13.	Review by the ANII.

c.	For preservice inspections of components for which shop or field examinations serve as the preservice examinations in lieu of on-site preservice examinations, verify:

1.	For vessels, the examination was performed after the hydrostatic test - which is required by the construction code - was completed.

2.	Examinations are conducted under conditions and with equipment and techniques equivalent to those expected to be employed for subsequent inservice examinations.

3.	Records are, or can be, documented and identified in a form consistent with the requirements in ASME Section XI, IWA-6000.

02.02	ASME Class 1 Records Review.	Perform the following:

a.	Obtain and Review at least one site preservice NDE inspection record from each item number in examination categories B-A through B-D in tables IWB-2500, preservice NDE inspection records for one-half to one percent of the SG tubes (Category B-Q, pressurized water reactors (PWRs) only)  and all dissimilar metal butt welds NPS 10 and larger in categories B-F and B-J.

b.	Verify that the following requirements are met:

1.	The method, extent, and technique of examination comply with ASME Section XI, the licensee's preservice inspection program requirements, and applicable NDE procedure.

2.	The examination data are within the acceptance criteria as outlined in the applicable NDE procedure and applicable Code requirements.

3.	The recording, evaluating, and dispositioning of findings are in compliance with the applicable NDE procedure and applicable Code requirements.

4.	The method used for NDE was sufficient to determine the full extent of indication or acceptance.

73757-03	RESOURCE ESTIMATE

Total resource estimate is between 400 and 500 hours, depending on the type of unit inspected, the type of construction materials used and the size of the unit.

Review of the general components under 02.01 would involve approximately 60 NDE reports.  This is estimated to take approximately 200 hours

Review of the Class 1 components would involve approximately 30 NDE reports for a PWR (less for a boiling water reactor since there is no pressurizer or separate steam generator) plus the NDE reports associated with the dissimilar metal welds, which could be on the order of 12 to 36, depending upon the construction materials used.  These reviews are anticipated to be more involved than those of 02.01.  One-half to one percent of steam generator tubes could be as much as 350 tubes for a large 4 loop PWR.  In total, these reviews are estimated to take between 200 hours to 300 hours.

73757-04	REFERENCES

ASME Code Section XI, “Rules for Inservice Inspection of Nuclear Power Plant Components.”

Regulatory Guide 1.147, "Inservice Inspection Code Case Acceptability - ASME Section XI Division 1."

10 CFR 50.55a, “Codes and Standards”

10 CFR 52.83, “Applicability of Part 50 Provisions”

10 CFR 52.99, “Inspection During Construction”

73757-05 	PROCEDURE COMPLETION

The procedure is considered complete when the plant transitions to the ROP.

END

Attachment 1:	Revision History for IP 73757

Attachment 1

Revision History for IP 73757

| Commitment Tracking Number | Issue Date | Description of Change | Training Needed | Training Completion Date | Comment Resolution Accession Number |
| --- | --- | --- | --- | --- | --- |
| N/A | 04/18/08 CN 08-012 | Initial issue to support inspections of operational programs described in IMC 2504, NON-ITAAC INSPECTIONS Completed 4 year search of historical CNs, no commitments found. | None | N/A | ML070920429 |