Veterans Health Administration Warning System

Published by VA Central Office

AL05-06		                          					      February 28, 2005

Item:  			Louvered heating, ventilating and air conditioning (HVAC) grilles in locked 		Behavioral Health Units.

General Information: 	Louvered grilles covering HVAC openings (Photo 1) located in locked mental health units may be used as an anchor point for a noose made from clothing or other flexible material.

Specific Incident:  		A mental health patient in a locked Behavioral Health Unit used an article of 	clothing to hang from a louvered grille and the grille supported the full weight 	of the patient.

Action:			By March 31, 2005:

1. Survey all locked Behavioral Health Units to determine if louvered grilles are 			present that may be used as an anchor point.

2. If louvered grilles are present in these Behavioral Health Units upgrade 		them by installing a woven wire cloth grille (Photo 2) or replace them with a 		suitable grille that cannot be used as an anchor point.  Breakaway grilles 			should not be used as the broken parts may be used for other purposes.

Source:  		VISN 15

Addl Information:  	A grille cover such as the one shown in photo #2 may be fabricated on site by 			engineering service personnel.  Woven wire cloth (e.g. stainless steel type 304) may 		be placed over the existing grille, riveted in place with the frame secured with tamper 		proof screws. Some manufacturers sell suicide deterrent supply grilles (e.g. Carnes 		Company, Models RSPA41 or RSPA42 or Anemostat Products Model SV2, 			http://www.anemostat.com/a-catalog/sec_sv2.htm); however others may also be 			available. These examples are provided for information only and are not intended to 		represent an endorsement of any one product.

Contact: 			Joe DeRosier, Program Manager, VA National Center for Patient Safety, 			telephone:  (734) 930-5888

| Photo 1: Louvered HVAC grille mounted using standard slotted screws. | Photo 2: Mesh grille, fabricated in-house, mounted with tamper resistant screws. |
| --- | --- |