PERFORMANCE WORK STATEMENT

FACILITY OPERATION AND MAINTENANCE SUPPORT SERVICES

AT THE

EASTERN REGIONAL RESEARCH CENTER (ERRC)

WYNDMOOR, PA

## UNITED STATES DEPARTMENT OF AGRICULTURE

AGRICULTURAL RESEARCH SERVICE

Eastern Regional Research Center (ERRC)

Wyndmoor, PA

### INDEX

SECTION						FUNCTION

- SCOPE OF WORK

- Background

  - Description of Work

- PROJECT MANAGEMENT

2.1								Work Management

2.2								Hours of Operation

2.3								Supervision and Staffing

2.4								Materials and Supplies

2.5								Quality Control

2.6								Preventive Maintenance

2.7								Emergency/Disaster Contingencies

2.8								Project Management Reporting Requirements

- MAINTENANCE, ALTERATION, AND REPAIR

OF BUILDINGS AND STRUCTURES

3.1								Carpentry

3.2								Painting and Refinishing

3.3								Masonry

3.4								Electrical

3.5								Electronics

3.6								Plumbing and Pipefitting

3.7								Heating, Ventilation, Air Conditioning

3.8								Refrigeration

- GENERAL MAINTENANCE

4.1								Grounds Maintenance

4.2								Pest Control

4.3								Moving

4.4								Janitorial/Housekeeping

- ADMINISTRATIVE SUPPORT SERVICES

5.1								Word Processing

5.2								Photography

5.3								Reception and Switchboard

5.4								Mail

5.5								Duplicating/Facsimile

5.6								Chemical and Stationery Storerooms

5.7								Shipping and Receiving Operations

5.8								Vehicle Dispatching and Scheduling

5.9								Snack Room Vending Machines Maintenance

5.10							Miscellaneous Administrative Support

- SECURITY PROTECTION SERVICES

6.1								Security Protection

6.2								Asbestos Abatement

- MODERNIZATION SUPPORT

7.1								Utility Outage Support

7.2								Relocation Support

7.3								Swing Space Renovation

APPENDICES

Appendix No.											Item

I			Glossary

II			Reporting Requirements

III			Facility Location Maps

IV			Collective Bargaining Agreement, Local No. 115

V		 	   Historical Workload Data

VI		 	Subcontracted Services

VII		 	Preventive Maintenance

Equipment Listing

VIII		  	Government Furnished Equipment

IX			Quality Assurance Surveillance Plan

X			Award Term Plan

STATEMENT OF WORK

# 1.0	Scope of Work

## 1.1	Background

The Eastern Regional Research Center, hereinafter referred to as the Center, located in Wyndmoor, Pennsylvania, is part of the Agricultural Research Service (ARS), United States Department of Agriculture (USDA). One of four regional research centers in the United States, authorized by the Federal Government in 1938 to conduct basic and applied research on agricultural commodities including: milk, meat, animal hides, wool, fats, oil, fruits, vegetables and forage to promote better utilization of American farm products. The complex consists of 12 buildings, utilities systems, sophisticated environmental controls, and a variety of specialized laboratories and rooms, allocated on 18 acres. The complex presently contains approximately 222,000 square feet of floor space. Basic utilities are purchased from public utility companies.

Six research units, comprised of government scientists with the aid of research technicians and assistants, conduct this research to benefit both the producer of agricultural goods and the consumer. The research units are Dairy Processing and Products; Crop Conversion Science and Engineering; Food Safety Intervention Technologies; Fats, Oils and Animal Co-Products; Microbial Food Safety; and Microbial Biophysics and Residue Chemistry and Core Technologies. To support this research, extremely complex and expensive test equipment is used which requires closely controlled environments to function properly. Responsiveness and skill to repair and restore operation and control of the facilities is critical for the protection of the integrity of the research programs conducted at the Center.

The North Atlantic Area Office resides as a tenant at the Center. This management structure includes the Area Director, an Administrative Office, Safety & Health, Budget and Fiscal, Procurement and Property, Personnel, Engineering and Computer Services.

A major laboratory modernization project is planned in the Center's pilot wing and service building. Operation support will be required during the renovation phase.

## 1.2	Description of Work

The Eastern Regional Research Center requires a full range of facilities operations and maintenance services to support its mission. The Contractor shall provide all labor, supervision, equipment, spare parts, and materials, except those specified as Government-furnished, to perform all work described in the performance based work statement (PBWS). All Federal, State, and local laws, regulations, codes, technical manuals, manufacturers’ guidelines, and USDA and ARS directives are applicable to performance of these services as identified in each Section of this PBWS. Facilities and operations and maintenance support includes, but not limited to, building maintenance, alteration and repair of building structures, general maintenance management, administrative support,  security and modernization support. All work requirements are considered routine. Exceptions are modernization support and facility renovations that will exceed a total firm-fixed-price amount of $2,500. The cost for this work will be negotiated between the Project Manager and ACO and will be performed during non routine business hours so not to affect routine operations.

# 2.0	Project Management

2.1	Work Management to assure all services are accomplished in such a manner that will have a minimal affect or result in interference with the proper execution of the research mission of the Center. This includes, but not limited to, measures for quality control, preventive maintenance, compilation of accurate performance historical data, technical libraries and reporting requirements. Strict compliance with environmental standards, such as the National Energy Conservation Policy Act of 1978 (NECPA) and Executive Order (E.O.) 12902 as implemented by FAR 23.203 and ARS Directive 134.2 are required in the performance of all services. Noncompliance issues shall be resolved among the ACO, CO, Area Engineer, Center Safety & Health Manager and the issuing office, EPA (Environmental Protection Agency) or PADER (Pennsylvania Department of Environmental Resources). Payment of fines or penalty charges associated with citations issued by the Federal, State or local officials shall be paid by the party against whom the fines or penalties are assessed. The Government will pay the fines or penalties for any citations issued without the fault of the Contractor. At no additional cost to the Government, the Contractor will pay the fines or penalties for any citations issued due to faulty operation, neglect, or maintenance practices of the Contractor. This may occur when a fine is levied for failure to switch fuels from gas to oil in a timely manner.

## 2.1.1	Work Management System

The Contractor shall use and support the Government-owned automated work management system, generated on the software package Maximo (or its equal) to record all work requests. Support will include but not limited to daily backups of the database, support and run updates, manage the server if it is not operating on the Center’s Local Area Network, problem solving MMS tech support. Work requests are required to prioritize, plan, and schedule work to assure availability of labor, materials, facilities and equipment, assure timely completion of preventive maintenance, and estimate and order material. This work management tool, accessible to the Government and operates on the Center's Local Area Network (LAN), is to be managed to report work requests initiated and completed to show timely performance, quality control management, and compilation of historical data to identify number of work orders received, performed, and actual hours worked in each function.

## 2.1.2	Work Requests

The Contractor shall use the work request system to generate routine services, additional work requests within contract scope and preventive maintenance. When work requests are received, they are to be reviewed for completeness, understanding and clarity. Vague and incomplete work requests shall be returned to the requester for clarification. A work schedule report shall be submitted weekly to QAS and is to include routine and additional work by assigned priority, date of receipt of work request, estimated date for completion, and personnel, material and equipment requirements. The project manager’s quarterly report will include information to show backlog of work per quarter for each function. Refer to Attachment VIII for Government furnished equipment furnished to support this system.

## 2.2		Hours of Operation

The Contractor shall perform the majority of the work required by this PBWS during normal business hours from 7:00 a.m. to 4:00 p.m., Monday through Friday, excluding Federal holidays and other day(s) designated by Federal statute, Executive Order or Presidential Proclamation. Federal policies concerning administrative leave for Federal employees shall be applied to contractor employees during the Christmas holidays. Exceptions to performance during normal business hours are:

- Boiler plant operations:  Manned on a 24 hour, 7 day per week schedule when high pressure steam is required. High pressure steam is defined as boiler operations greater than 15 psi.

- Security:  24 hours a day, every day.

- Utility Outage Support: Shutdown of facilities may require performance during non business hours. Utility outages occur approximately 7 times per year and usually occur on weekends.

## 2.2.1	Emergency Operations & Maintenance Support

A 24 hour per day emergency response plan is to be developed for rapid initiation of onsite emergency services. . Emergency operations and support services are defined as any necessary operations, maintenance, and/or repair services required to be performed to protect or prevent loss of Government property, endangerments to human life, and to research experiments and animals. This includes repairs and services necessary to continue normal operation of the Center's facilities during periods of other than regular working hours. Emergency onsite response time shall be within 5 minutes during normal business hours and within 30 minutes at all other times unless otherwise specified. Procedures outlined in the ERRC Facility Self Protection Plan shall be followed and necessary action taken to alleviate the emergency and pursue the work to completion. Submit a Malfunction Report to the ACO, Quality Assurance Specialists, and Area Engineer upon completion of repair to equipment. This report shall include the description of the malfunction, date and time notified, date and time of arrival, type and model number(s) of the equipment, serial number(s) of the equipment, craft time spent on repair, and parts replaced/repaired.

# 2.3	Supervision and Staffing

## 2.3.1	Supervision

Prior to commencement of services, an onsite employee shall be designated to be responsible for supervision of all contractor employees. This employee shall be the contractor's primary representative having full authority to act on matters pertaining to the performance of services required under the contract. This representative shall be on-site or on-call whenever work is performed by the contractor's work force. An acting employee will be designated to fulfill these duties when the primary representative is not available on site. Within 1 day of an occurrence, report to the ACO personal injuries, damage to Government property, loss of keys and/or access cards, hazardous conditions. Working groups assigned to a particular area shall have adequate supervision.

## 2.3.2	Staffing

A list of all employees employed for performance of the PBWS requirements is to be submitted within 30 days of contract award. This list is to include required employee certifications for boiler and equipment operations (tractor, forklift etc). Watchperson personnel must have received a National Agency Check (NAC) clearance not later than 10 working days from initial work performance start date. During the course of the contract, submit names and qualifications of any new employee(s) to the ACO within five (5) days of reporting for work.

## 2.3.3	Staffing Identification

Personnel shall present a neat appearance and be easily recognizable by a prominently displayed photo identification badge worn during all work hours.

## 2.3.4	Conduct

Strict adherence to standards of competency, conduct, appearance and integrity are required that will reflect credit to the employee, the contractor, and the Government. Compliance with traffic and safety rules, regulations and instructions pertaining to conduct of persons on Government facilities are required. Entry into restricted areas is not permitted and there shall not be disturbance of papers on desks, open desks or cabinets, or the use of office telephones or equipment if not required for the performance of duties. Serious infractions may be grounds for permanent removal from Government property. All employees, including watchperson staff, shall not carry any instrument that could be considered a lethal weapon and is not essential to the performance of their work on ERRC property or have any such weapons in their possession or under their control while performing services under this contract.

## 2.3.5	Safety

Work shall be performed in a safe manner and in compliance with OSHA, Federal, State and USDA requirements. If there is refusal or failure to comply with safety requirements, the ACO may issue a stop work order on all or part of the work until satisfactory corrective action is taken. All personnel will receive initial safety orientation/briefing on all ERRC's safety requirements within 3 days of starting work. Personnel shall wear protective equipment such as gloves, safety glasses, safety shoes, etc. in accordance with Federal, State and local regulations.

## 2.3.6	Strike Contingency

A plan for the continuation of services is required in the event of a work stoppage, slowdown, or similar action by contractor and/or subcontractor employees. The plan shall include how subcontracted services will continue in the event a subcontractor is unable to satisfactorily implement his strike contingency plan. This plan is to be furnished to the ACO 30 days after contract award.

# 2.4	Materials and Supplies

Materials and supplies must meet Federal specifications, applicable safety requirements of Occupational Safety and Health Agency (OSHA), and environmental regulations of the EPA and PADER (Pennsylvania Department of Environmental Resources). Materials shall not be used that would be unsuitable or harmful to the facility, its personnel or research. New parts and replacement parts shall be of like quality to those removed and procured at a price comparable to the current market value without a delay in repairs. Only new parts will be used unless otherwise approved by the ACO.

## 2.4.1	Major Repairs or Replacement

Notify the ACO not later than the next work day of repairs or replacement to equipment that would exceed the cost of $1,000. If these repairs affect life safety, research, security, or utility costs/energy conservation, then notification will be the same day by direct contact. If the ACO is unavailable, notify the NAA Engineer of the needed repair for concurrence. No government funding approval will be required. The Government reserves the right to determine whether such equipment will be repaired, replaced or abandoned. If it is determined equipment is beyond economical repair, a written recommendation shall be provided to the ACO justifying equipment replacement. The documentation shall include age of failed item, cost of repair parts, replacement cost and availability, rationale for replacement rather than repair and if replacement equipment will fit in available space, performed the required function and operate on existing utility services.

## 2.4.2	Reconditioning

Information regarding reconditioning of equipment, components or machines must be submitted in writing to the ACO and shall identify the need for and details of the nature of reconditioning, cost effectiveness of reconditioning versus replacement, and life cycle costing.

## 2.4.3	Warranties

Establish a computerized system (i.e. bar code) to track all equipment and software under warranty acquired for maintenance services, research, or administration. Establish a schedule and job plan for performing preventive maintenance as noted by the manufacturer when the equipment requires maintenance. The process shall include but not limited to warranty registration, equipment tagging, and email notification one month prior to warranty expiration.

## 2.4.4	Fuel

The Government purchases and pays for all fuel used for heating plants and boilers. Notification will be given to the Center’s Purchasing Agent when reordering is required.

## 2.5	Quality Control

Establish and maintain a Quality Control Program to assure the requirements of the contract are satisfied to meet the customer’s level of expectation. This plan must be submitted to the ACO for approval within 30 days after contract award and put into place within 30 days of receiving ACO approval. The plan shall be reviewed and updated annually by November 1. No changes to the plan shall be implemented prior to review and approval by the ACO. At a minimum, the plan shall include:

- Methods of sampling techniques and means to identify deficiencies in the quality of services performed before the level of performance becomes unacceptable and corrective actions need to be taken.

- Methods of documenting and enforcing quality control operations including subcontracted work. Include inspection and testing methods, names and qualifications of those performing inspections, there extent of authority, and an organizational chart depicting function roles.

- Methods of documenting and enforcing safety in all jobs. This could mean but not limited to use of safety glasses, safety shoes, harnesses for fall and extraction, asbestos identification, and safety of government employees when performing maintenance that may present hazards.

2.5.1	Maintain a file of all inspections and document required corrective action if taken.

# 2.6	Preventive Maintenance

The Government-furnished automated work order system is furnished for the timely completion of preventive maintenance services. Preventive maintenance shall be performed as scheduled in the existing preventive maintenance plan for all equipment and systems historically maintained as listed in Appendix VIII. Services performed shall be based on manufacturer's recommendations and standards, national and state trade codes, and industry standards. The Preventive Maintenance Plan shall be maintained to include items and components to be maintained, schedule, frequencies, and description of scheduled work, inspection and record of maintenance performed with recommendations regarding future PM work to occur during the next frequency cycle. The PM program shall be updated monthly to reflect equipment changes and be readily available to the Government. These changes could include adding/deleting equipment, changing frequencies, or updating job plans. Notification to the government is required for documented changes that may affect contract costs.

## 2.6.1	Preventive Maintenance Schedules and Accomplishments

Included in the weekly work schedules submitted to the QAS, planned preventive maintenance work shall be included. If work was not completed as scheduled, annotate on the next planned work schedule why performance was delayed.

2.6.2	Preventive maintenance work is done during normal business hours. If system shutdowns are required, performance will be done off hours, and scheduled and coordinated with the ACO. The Government reserves the right to defer preventive maintenance tasks at any time due to scheduling conflicts or in response to period of equipment inactivity.

# 2.7	Emergency/Disaster Contingencies

In the event of a natural disaster or major disruption at the Center, an Emergency/Disaster Contingency Plan will be activated so operations and maintenance support services included in the PBWS continue and/or expand to continue the research mission objectives of the Center. Such circumstances that would impact ability to perform are defined as a national or local emergency (national epidemic or localized outbreak of disease) or a natural disaster (i.e. fire, flood, and other acts of God). In such circumstances, it is to be assumed that the Government will continue to need the same performance requirements. If increased work beyond the scope of the PWS is required to continue such performance, the increased work and cost shall be subject to the Changes Clause, FAR 52-243-2 and negotiated with the ACO.

## 2.7.1	Emergency/Disaster Contingency Plan

Develop a plan for implementation in response to such circumstances which shall include: initial mobilization and contingency plan outlining methods for continuation of all services. The plan shall also include how subcontracted services will be implemented. A comprehensive plan shall be submitted to the ACO 30 days after contract award. Any changes must have written approval of the ACO prior to implementation.

# 2.8	Project Management Reporting Requirements

In addition to the reporting requirements noted in Appendix II, the following data item deliverables are required:

## 2.8.1	Facility Condition Survey

Conduct a condition survey of all the Center's facilities to document structural deficiencies not later than April 1 of each year of the contract. Using the Facilities Condition Survey Form, ARS-12, compile a recommended project list for the next fiscal year based on this survey. Information shall be furnished in numerical priority order with prioritization done by taking into consideration the immediate need and long range up to 5 years. Items are to be listed by design, design and construct, alteration and betterment, repair and maintenance and energy savings. Each item shall show approximate/estimated dollar value, with the minimum threshold being $5,000. No Cost estimate is required for work under $5,000, Cost estimates shall be coordinated with the Area Engineer and each item shall have a project name and location.

## 2.8.2	Equipment Inventory

The Contractor and the ACO, or the designated representative, shall prepare an inventory to be used as the basis for turning over Government-furnished items within 30 days after contract award. Thereafter, an annual inventory shall be conducted by the contractor and submitted no later than December 1 to the ACO.

## 2.8.3	Functional Cost Breakdown

This report is required to provide assistance to the NAA Budget and Fiscal Officer in tracking actual costs spent to maintain the Center so to prepare for the annual budget preparation process. This report shall be submitted annually by April 30.

## 2.8.4	Quarterly Statistical Workload Data Report

Submit, by the 15th calendar day following the end of the quarter, to the ACO and PCO, a quarterly work summary report. This report will be used to gather workload data and shall include the following:

- Employee Productive Time Analysis. Report total number of routine and preventive maintenance hours performed for the current and previous quarter, plus overtime hours (time and one half and double time); less vacation, holiday, sick, bereavement, jury duty, paid and unpaid absences and vacancy hours.

- Project Work Order Activities. Number of work orders generated, completed and outstanding per function for routine, preventive maintenance and additional tasks.

- Subcontracting. Number and total costs for subcontracts issued during the quarter and total costs awarded to small, small disadvantaged, women owned and hubzone businesses.

- Administrative Services. Workload data shall include number of: conference room set ups completed, incoming and outgoing packages, gas cylinder requests and cylinder inventory on hand, government vehicle reservations, photo copying, facsimile request, reprint request, mail pieces and costs for mail handling for the Center, NAA, and ADO, express mail packages, Government purchase orders prepared, and completion of photographic and word processing request. Number of card access and key requests processed.

- The Quarterly Workload Data Report will be used to determine the allow ability of incentives as described in the Incentive Payment Plan and to assist in budgetary planning for future ERRC support.

## 2.8.5	Energy Conservation

The Contractor shall assist the Center in all endeavors of energy conservation/ recycling. The Government follows the usage trend and costs for all utilities. If excessive utility charges occur the O&M Contractor shall be notified of this problem immediately and will evaluate all major systems within the Center to ensure the systems are properly working.  If systems are identified to be operating inadequately due to maintenance not being performed, the O&M Contractor shall correct these problems immediately and in accordance with the provisions of the PBWS.  If the O&M Contractor fails to correct the problems the Schedule of Deductions shall be utilized to penalize the O&M Contractor for inadequate performance of maintenance.

# 3.0	Maintenance, Alteration, and Repair of Buildings and Structures

Maintenance, repair, preventive maintenance and alterations following all industry, trade and OSHA standards in the performance of services to support facility operations which include: carpentry, painting, masonry, electrical, electronic, plumbing and pipefitting, HVAC, and refrigeration. All Government Furnished Equipment and Material required for the performance of services within each function is identified in Appendix VIII.

# 3.1	Carpentry Services

Maintain, repair, alter/modify, install and fabricate wood and wood substitute portions of the Center as described in this section. Repairs shall meet the following quality standards: modification of straight walls must conform to existing conditions, structures and appurtenances are horizontally straight and vertically plumb, the repaired portion of a structure must visually match closely in style and texture to the undamaged portion of the structure, touch up painting shall be done to changes to existing equipment or structures and the soundness of the repaired structure is not to be affected. Wood and non-wood structure items included but are not limited to:

- Windows and louvers, including all hardware

- Exterior and interior doors (including room and closet doors), including hardware, such as locks, latch mechanisms, etc.

- Building insulation

- Caulking (including building expansion joints)

- Screens, insect, and bird coverings on all building openings

- Acoustical and suspended ceilings

- Window shading, including horizontal and vertical slat "venetian" blinds shades, curtains and external shading screens

- Furniture, including cabinets, desks, bookcases, laboratory furniture, and all hardware

- Maintenance, repair and installation of cabinet and furniture locks, hardware, and closures, etc.

- Lubricating and repairing chairs and other furniture

- Mounting and remounting cabinets to the wall

- Inspection of buildings, roads, sidewalks, walls, windows, locks, latches, ceilings, and roofs

## 3.1.1	Floor Tile

Install, repair and/or replace damaged vinyl composition tile. There is approximately 89,000 square feet of tile of which 25,000 square feet is vinyl asbestos tile (VAT). This tile shall be replaced with vinyl composition tile when repairs or alterations are required. Remove and cut this material in accordance with the regulations for handling asbestos and the planned procedures submitted to the Center’s Safety Officer for approval before replacement. Encapsulation of VAT is permitted. A floor plan of the space where VAT is to be encapsulated is to be sketched and forwarded to the Area engineer for review and approval prior to any work being done. Transition to different type and/or level flooring shall be carried out with appropriate transition materials or thresholds. A sufficient stock of floor tile shall be maintained so that spot damage can be repaired.

## 3.1.2	Carpet Tile

Maintain and install carpet tile in administrative offices, selected corridor spaces and service areas, lobbies etc. There is approximately 3,000 square yards of carpet tile and 1600 square yards of broadloom carpet. All carpet tile shall be treated for non-static and fire resistant characteristics and be of heavy duty commercial type construction. Carpet tile shall be adhered to the floor with a low release adhesive to facilitate replacement and repair. Transition to different type and/or level flooring shall be carried out with appropriate transition materials or thresholds. A sufficient stock of carpet tile shall be maintained so that spot damage can be appropriately repaired.

## 3.1.3	Roofing

Perform routine maintenance, and take action to mitigate any leaks (i.e. fill pitch pockets, repair flashing, etc.). Damaged roofs shall be closed before the end of the work day when such an event occurs, and properly repaired within 14 calendar days unless otherwise authorized by the ACO. Roofing repairs estimated to be in excess of $1000 to correct are to be reported within 96 hours of discovery to the Area Engineer and ACO for review and approval before the work is performed. A condition survey of all buildings, including flashing, building joints, and all appurtenances, shall be accomplished by April 30 of each year. The report showing the condition of the roofs and recommended action shall be forwarded to the Area Engineer through the ACO by May 30 each year. Roofing materials vary between the various buildings and appropriate measures shall be taken to maintain the surface.

- Building 4 (Main Building): The main roof is covered with Sarnafil, single ply and is approximately 16,640 sq. ft. chemical wing, 16,828 sq. ft. pilot wing, and 13,587 sq. ft. admin wing for a total of 47,055 sq. ft. Hypolon roofing (over stair tower) shall be coated in years ending in 3. (i.e. 2013). There are about 1.5 squares of hypolon roofing.

- Building 6 (Mechanical Building) and Building 16 (Leather Research Building): Metal roofing shall be caulked or soldered annually at cracks and openings. There are about 430 squares of metal roofing and siding. Building 6 has about 8 sq. of Firestone membrane roofing on the high roof.

- Building 7 (Meat Processing Building): Corrugated cementatious roofing and siding which shall be re-coated with protective cementatious materials in years ending in 4. (i.e., 2014). There are about 400 squares of cementatious roofing and siding and the corrugated wall and roofing materials may contain asbestos. Some roofing materials contain non friable asbestos materials. Repairs shall be made in accordance with applicable regulations.

- Building 4: Laboratory 0213 - 750 square feet of Ethylene PropyleneDiene Terpolymer (EDPM) membrane roofing which shall be inspected and maintained with a ballest covering.

- Building 3 (Hazardous Operations)  Sarnafil 1500 sq ft

- Shingle roofing, membrane roofing and built-up roofing shall be inspected and spot repairs completed when needed. The extent of the repairs will be coordinated with the Area Engineer for the long range roofing service plan. There are about 1,000 squares of shingle roofing, membrane roofing and built-up roofing.

## 3.1.4	Doors and Door Hardware

Doors are of various construction and rating and shall be maintained at the present configuration. All interior and exterior, including room and closet doors, shall be maintained to assure their current fire rating. Repair, lubricate, service or replace, as required, door latches, locks, jams and trim, trim hardware, closers, and actuators. There are approximately 2,500 latches and 1,500 locks of various types. Door latches and locks shall be identical to or, on approval, be compatible with existing equipment. Pad locks for securing facilities equipment, etc., as lockout devices and locks on equipment, furniture and cabinets shall not be keyed to the Center’s Key Control.

## 3.1.5	Windows and Window Hardware

All windows, window hardware, and internal and external envelope or wall closures shall be maintained to function as designed. All exterior windows shall have double glazed insulation (thermal) pane type glazing. All south and east exposure windows shall additionally have heat and shading absorbing qualities. Glass substitutes shall be glazing quality thermoplastic or equal and can be used in propriety areas of high breakage. Replacement glass window material is not to be cracked, chipped, or otherwise defective and shall be properly seated and caulked/sealed to prevent leakage, breakage, wind drafts, and rattles. Damaged window repairs are to be done before the end of the work day unless otherwise authorized by the ACO.

## 3.1.6	Ceilings and Walls

Maintain, modify and repair the suspended ceilings, drywall and acoustical wall coverings as required to maintain the acoustical value of the material, the appearance of the spaces and minimize the dusting and flaking of the materials. There is about 54,000 square feet of acoustical ceiling and 7,000 square feet of other type suspended ceiling, not including the masonry drop ceilings. Walls and suspended ceilings (acoustical and otherwise) are to be installed and repaired using proper materials that are true, plumb, and level.

## 3.1.7	Modular Furniture, Partitions and Portable Walls and Partitions

Maintain the finish and appearance of modular furniture and partitions in laboratories and offices, including the paint and fabric. There is about 2,000 lineal feet of portable partitioning and 8,750 square feet of modular furniture work surface. Modifications and changes to the existing equipment must be compatible with what is in place. Changes to the modular equipment shall be in accordance with the plans and sketches provided by the requestor or the manufacturer. Such equipment is to be installed tight to floors and walls, including ceilings, where required. Space closure panels, taping, etc., is done to provide a finished look. Follow up is made to assure the work of other functional areas of work (i.e. electrical, electronics) are complete to assure full project completion. Acoustic portable partitions shall be serviced and maintained as required by the manufacturers. Partition maintenance shall include door openings and hardware.

### 3.1.7.1	Install and/or relocate new modular furniture and partitions in laboratories and offices. Modifications and changes to the existing equipment should be compatible with that in place. Due to the specialized nature of shapes and attachment practices of the components an installations of such equipment, assistance from the manufacturers' representatives may be necessary to make modifications and changes to the modular equipment. Partition installation shall include door openings and hardware.

## 3.1.8	Furniture

Maintain, assemble, dismantle, and move office, laboratory furniture and equipment as required. Assembly of furniture shall be accomplished utilizing the directions furnished by the manufacturer (if available); and be level, secure and stable. Some laboratory equipment may be constructed of asbestos-containing materials, such as transite. When working with laboratory equipment containing asbestos material, ensure all work is performed in accordance with OSHA regulations.

## 3.1.9	Signs and Engraved Labels

Signs and laminated engraved labels shall be made in accordance with Center policies and applicable regulations. They are to be level, uniform in format, location, and height; and, are suitable for visually impaired persons. This will included, but not limited to: room door signs (Personnel names, etc.), safety and directional signs, and equipment and control panel labels

- Personnel name signs shall be uniform in size, lettering size and appearance. Name signs shall be installed in a uniform format, location and height throughout the facility.

- Safety and directional signs shall comply with OSHA, NFPA, BOCA, etc., and be uniform in appearance and placement. Safety and directional signs and labels for general visitor use shall be suitable for use by visually impaired persons. Safety signs shall include fire zone numbers and emergency call numbers.

- Equipment and control panel labels shall comply with Center policy, OSHA and related codes and be uniform in application and appearance.

## 3.1.10	Bulletin Boards and Cabinets

Install bulletin boards and white boards (approximately two or three annually) and mount purchased cabinets, shelves, bookcases, award plaques and pictures on walls (approximately 5 to 10 hours per month). Installations must be level and securely mounted using proper wall anchors, taking care not to damage surrounding areas and finishes. Damaged areas discovered, and those areas that are damaged incidental to installation are to be repaired.

## 3.1.11	Preventive Maintenance

The items to be included on the Preventive Maintenance Program are:

- Exterior and interior doors (including room and closet doors), including hardware, such as locks, latch mechanisms, etc.

- Caulking (including building expansion joints)

- Screens, insect and bird coverings on all building openings.

- Inspection of  buildings, roads, sidewalks, walls, windows, locks, latches, ceilings and roofs.

- Fire extinguishers

## 3.1.12	Cost and Time Estimates

Estimates of the cost of work for office and laboratory renovations may be required. Estimates reported shall include all labor hours and burden, profit, materials, and subcontract costs (if applicable). Time estimates shall include the number of days for completion and supporting justification if performance of work is proposed to be completed during routine working hours.

3.1.13	Government furnished equipment/material is noted in Appendix VIII.

# 3.2	Painting and Refinishing Services

Paint and refinish a variety of interior and exterior surfaces of wood frame, concrete, metal, and masonry buildings, including offices, laboratories, storage buildings, and other structures, including their furnishings and equipment. Special effect finishes, such as graining, may be required. All surfaces are painted to show a uniform appearance and color coordination. The finish shall conform to established industry standards and all work is free of finish defects such as misses and runs. Touch up work shall color coordinate such that the surface is restored to resemble as closely as possible the original appearance. All materials are to be high quality and stored in accordance with manufacturer’s recommendations. Catalog and manufacturer’s data sheets (including MSDS) are maintained for all paint, cleaning and preparation materials used. Exterior and interior painting such as walls, ceilings, floors, ducts/grilles, exposed ductwork, trim, etc. shall be painted as defined in Exhibit 3.2.

## 3.2.1	Painting Schedule

Inspect the interior and exterior surfaces of the buildings and equipment to determine painting and glass replacement needs and schedule restoration activities on an annual painting plan. The painting plan shall be submitted in accordance with the criteria in Exhibit 3.2.1 for approval to the ACO not later than 90 days after award and revise and review the plan annually by October 10 each year. The status of the last painted date for areas and spaces will be provided by the ACO during the start up of the contract. Schedule work in relation to the condition of the protective or decorative coatings in place, the criteria schedule and the major work schedule planned by the Area Engineer. Prepare a specific prioritized painting schedule for each year showing the areas slated to be painted and the dates the work is planned to begin and be complete. This plan constitutes the yearly revision to the 5-year plan. This plan shall be submitted to the ACO by October 10 of each year. Include in this plan any work which was scheduled in the previous year but not completed in accordance with the plan. Changes to the approved plan in response to customer requests must be approved by the ACO.

## 3.2.2	Roadway and Curb Markings

Restore the painted parking space lines, roadway directional lines and signs, and curb markings at the facilities every 5 years during the spring season in accordance with drawings available in the Area Engineering Office and Exhibit 3.2.1.

## 3.2.4	Special Coatings

Apply special coatings on refrigeration equipment, cold rooms, and air conditioning cooling towers. Special coatings are to be resistant to acids, chemicals, heat, and corrosion for use on laboratory and Pilot Plant equipment. Examples of special and protective coatings (paints) to be used at the ERRC are:

- Chlorinated rubber for BSL2 and above Labs.

- Epoxy enamel for Food Engineering Areas, machine rooms, floors

- Vinyl enamel for Exterior Equipment

- Alkyd for Laboratory walls and Machine rooms

- Acrylic Latex for Office Walls

- Urethane for Door finishes

- Latex for Service Areas

- Lacquer and shellac for special items

- Varnish for exposed wood

## 3.2.5	Lettering and Stenciling

Stencil surfaces with lettering or decorations and paint signs on various types of surfaces, including road signs. (See Exhibit 3.2)

## 3.2.6	Surfaces Not To Be Painted

Refinishing/restoration of old wooden furniture such as tables, chairs, desks, shelves etc., SHALL NOT be done. The following surfaces and materials are not to be painted. Care shall be taken to prevent these surfaces from paint damage by masking, removal and reinstallation, or other means specifically approved by the ACO and Area Engineer.

Brass and bronze			Fire equipment			Formica

Stainless steel			Tile						Fabric

Glass					Plastic					Cork

Rubber

Stone tables/countertops

Natural wood grain varnished or shellac finishes

Valve stems and packing glands or nuts

Valve tags and nameplates

Baked enamel finishes such as on electrical receptacles and switch bodies

Moving parts of equipment

Pipe and duct identification tags

Nickel or chrome-plated surfaces

Finished and anodized aluminum surfaces

Office and laboratory equipment and some furniture as specified

Exhibit 3.2

Color Code Identification

| Service | Color | Lettering |
| --- | --- | --- |
| Sprinkler & fire espousing lines | Red | Black |
| Steam | Orange | Black |
| Hot water for heating | Light Orange | Black |
| Gas | Yellow | Black |
| Air | Dark Blue | White |
| Cold water (Potable) | Green | Black |
| Distilled water | Green with light purple band | White |
| Itemized water | Green with dark purple band | White |
| Softened water | Green with white band | White |
| Hot water (Potable) | Green with orange band | White |
| Nitrogen | Light Blue | Black |
| Vacuum | Blue with white band | Black |
| Drain, waste | Black | White |
| Vent piping | Black | White |
| Electrical conduit in offices | Wall color | None |
| Electrical conduit (up to 220 volts) | Light Grey | None |
| Electrical conduit (220 to 600 volts) | Dark Grey | None |
| Electrical conduit (over 600 volts) | Red with grey band | Black |
| Electrical apparatus (up to 220 volts) | Dark Grey or wall color | Black |
| Electrical apparatus (220 to 600 volts) | Dark Grey | Black on Yellow |
| Electrical apparatus (above 600 volts) | Dark Grey | Black on Red |
| Chilled Water | Grey with green band | White |
| Chilled Medium (Methanol) | Brown with grey band | White |
| Chilled Medium (Glycol) | Brown with yellow band | White |

Piping Identification

| Item Size | Lettering Size |
| --- | --- |
| 6 inches or larger | A minimum of 2 inches height and 0.375 in thickness |
| 2 inches to 6 inches | A minimum of 1 inch height and 0.187 in thickness |
| 3/4 of an inch to 2 inches | A minimum of half an inch in height and 0.125 in thickness |
| 3/4 of an inch or less | Tagged with color coded engraved tag at valves, inlets, and outlets |

Exhibit 3.2

Protective Coating Materials

1.	Paints for walls, ceilings, and duct work.

Primer, walls, ceilings, and ducts. Primer shall be the same as finished coat with a lighter tint.

Finish, walls, ceilings, and ducts

- Flat acrylic latex sealer with mildew preventive additive

- Finish:  satin gloss

- Active ingredients:

2-(4-thiazolyl) benzimidazole .10%

benzyl bromacetate .10%

- Inert ingredients:

water 38.5%

vinyl epoxy copolymer 27%

titanium dioxide 18.9%

propylene glycol 9.10%

calcium carbonate 4%

surfactants 2.3%

2.	Additional materials shall conform to the following:

- Paint remover:  Fed. Spec. TT-R-251

- Spackling compound:  Fed. Spec. SS-P-00450

- Varnish:  Clear non-yellowing furniture quality; semi-gloss for doors:  Fed. Spec.TT-V2-109

- Asphalt varnish to fill exposed cork insulation:  Fed. Spec. TT-T-51C

- Pretreatment of metals recommended by the coating manufacturer

- Glazing compound:  Fed. Spec. TT-Q-401-E

Exhibit 3.2.1

Painting Schedule Criteria

|  |  | Last |
| --- | --- | --- |
| Space | Cycle | Painted |
| Laboratories & associated utility | 12 years | Varies |
| rooms (approximately 100 labs) | 8 labs per year |  |
| Administrative/general offices/lab offices | 12 years | Varies |
| (approximately 100 offices) | 8 offices per year |  |
| Corridors | 8 years | Varies |
| (approximately 16) | 2 per year |  |
| Stairways | 8 years | Varies |
| (8 stairways) | 1 per year |  |
| Conference rooms, auditorium, | 5 years | Varies |
| Cafeteria, interaction areas | 2 per year |  |
| (approximately 10 areas) |  |  |
| Lobby door (exterior) | yearly | 2003 |
| Service areas & machine rooms | 10 years | Varies |
| (approximately 10 areas) | 1 per year |  |
| Outside equipment and switch gear | 8 years; | 2004 |
| touch up annually |  |  |
| Flag pole | 10 years; | 1992 |
|  | touch up base annually |  |
| Parking lot sealing and relining | 5 years; | Varies |
| 4 lots and front of building | 1 per year |  |
| Boiler house (interior) | 10 years | Varies |
| (as example; floors, piping, equipment, handrails) | 10 % per year |  |
| Lightpoles | 10 years | 1995 |
| Restrooms | 6 years | Varies |
| 23 restrooms | 4 per year |  |

| AREA | LAST PAINTED |
| --- | --- |
| Phase #1 | 1999 |
| Phase #2 | 2002 |
| Phase #3 | 2001 |
| Phase #4 | 2001 |
| Phase #5 | 2003 |
| Phase #6 | 2003 |
| Phase #7 | 2004 |

# 3.3	Masonry Services

Maintain and repair structures and surfaces made of brick, stone, plaster, concrete, concrete masonry units (standard and glazed), asphalt surfaces, ceramic clay-based tiles, and other related materials. All repairs shall be made to ensure the structural soundness of the repaired structure. Materials to be used are to match as closely as possible the repaired portion of the structure or surface to the undamaged portion of the structure or surface. Since the batch materials used for repairs are often particular to that material, a small supply of the replacement materials shall be maintained in inventory. Mortar joints will be of uniform width. Repairs to walkways, driveways and parking lots shall maintain the existing proper pitch. All debris associated with masonry repairs and maintenance shall be removed from the site immediately. Routine work which includes:

- Removing damaged areas of walls, floors, ceilings and roofs and patching the holes

- Repairing and closing openings in walls, floors, ceilings, and roofs

- Patching walkways and curbs

- Grouting new or existing areas

- Cutting joints in brickwork and pointing

- Patching blacktop areas

# 3.4 	Electrical Services

Repair, maintain, modify, adjust, and install electrical systems, facilities distribution, power generating equipment and components in accordance with equipment specifications, manufacturers' instructions, and all applicable Federal, state, and local codes, and the National Electrical Code (NEC). Electrical distribution equipment is noted in Exhibit 3.4. All industry and trade standards shall be followed. All transformers and devices which formerly contained PCB materials have been replaced or have had the PCB material removed to allowable levels. Repairs and adjustments shall be made without causing disruption to electrical service; however, if necessary service interruptions are required, prior ACO approval must be given before taking action. In the event routine repairs can not be accomplished, the ACO shall be provided a written explanation of the problem with recommended solutions by close of business on the following workday. The equipment to be maintained includes, but is not limited to:

- Transformers

- Breakers

- High voltage and secondary distribution systems

- Fire Alarm System

- Exterior building lights

- Electrical substations

- Related equipment, such as cabling, conduits, braces and brackets, guy wires and/or anchors, poles, cross arms, insulators, breakers, fuses, conductors, switch gear, transformer racks and hangers, circuits, etc.

- Building wiring and lighting systems

- Electrical controls

- Electric motors and fans

- Lighting fixtures, ballasts, lighting tubes and luminaries

- All wiring, outlets, and receptacles

- All related equipment, such as main disconnect devices, cables, raceways, ducts, capacitors, regulators, grounding equipment, lamps, clocks and all accessories necessary to distribute electricity

- All standby emergency generating plants, lighting, and equipment

3.4.1	Electrical service to assure uninterrupted service to the facility and its research mission includes, but not be limited to:

- Troubleshooting and repair of power circuits, controls, switches, thermostats, and relays

- Connecting wires to outlets, switches, receptacles, and power sources

- Testing circuits and equipment

- Maintaining and repairing elevators, lifts, hoists and other lifting equipment

- Replacing, testing, maintaining, and repairing electric motors and fans

- Checking controls and components of motor controls and circuits

- Repairing electrical equipment and machinery

- Troubleshooting and repairing electrical controls for HVAC equipment, such as flow meters, temperature and pressure recorders, magnetic starters, pump controls, individual heating unit systems, and electrical components of air conditioning and refrigeration equipment

- Maintaining emergency generators, substations, and transformers

- Cleaning light fixtures upon replacement of bulbs, luminaries, ballasts, etc.

## 3.4.2	Emergency Electrical System

Responsible for maintaining, repairing, operation testing, and utilizing when needed, the emergency electrical system. Emergency lighting and entire emergency system power shall be functionally tested in December and June each year.

## 3.4.3	Electrical Troubleshooting

Identify control malfunctions or problems as required. Identification shall include a method of reviewing the operating systems, discovering and recording irregularities, troubleshooting the systems and equipment, diagnosing and recording the findings, and repairing the system in the most effective manner to restore proper control in the shortest time after malfunction.

## 3.4.4	High Voltage System

Maintain and repair the high voltage system which includes all the cable, conductors, grounding, raceway, equipment and protection from the incoming switches (15 KV) at the power company pole through the transformers (15KV/5KV) and distribution equipment to the using voltage (5KV/480 - 277, or 5KV/208 - 120). (Systems 600 Volts and above.). Repairs to this system can only be made by those qualified personnel licensed/certified to perform such work.

## 3.4.5	Switch Gear and Transformer Inspection

Inspection of the high voltage (15KV and 5 KV) switch gear and transformers, outlined in Exhibit 3.4, shall be made annually in July with a report submitted by September 1 to the ACO describing the condition and deficiencies found. Confirm the electrical coordination of all voltage protection devices from the entrance service to, and including, the distribution switches in the low voltage distribution switch gear. Test and record the resistance values and condition of the cables and switches rated at 600 volts and above annually.

## 3.4.6	Low Voltage Systems

Operate and maintain all low voltage facility equipment, cables, raceway, etc., including all components such as panels, motors, timers and controllers, and appliances and extension cords.

## 3.4.7	Elevator, Hoist and Lift Equipment

Maintain and repair all vertical transportation, elevators, lifts, cranes, etc. Elevator equipment is noted in Exhibit 3.4.7. Maintenance, repair, inspection and component evaluation and replacement shall be completed only by electricians and mechanics qualified in elevator and lift maintenance and installation and shall be experienced in mechanism and device evaluation. Replacement of parts and equipment valued in excess of $1,000 per item shall require the approval of the ACO prior to any work being done.

### 3.4.7.1	Elevator, hoist and lift equipment inspection. Conduct an annual certified elevator inspection in March by an independent professional engineer and electrician qualified in elevator and vertical lift installation and evaluation and provide a copy to the ACO by April 30. Load tests, safety, and performance evaluations shall be carried out in accordance with the applicable Federal, State and local codes and regulations and national recommendations of recognized standards entities. Results of the inspection and copies of the certificates shall be forwarded to the ACO 30 days after the inspection for review and filing by the Area Engineer. Originals of the certificates shall be publicly posted in or near the equipment in an appropriate framed display. Negative evaluations or noted deficiencies shall refer to the applicable code, regulation or recommendation by paragraph and citation by the inspector in writing.

## 3.4.8	Master Time System

Responsible for operating and maintaining the Center’s clocks. There are numerous electrical and battery powered clock devices and timers in the facility.

## 3.4.9	Control Voltage Systems

Responsible for operating and maintaining control voltage systems dedicated to the control of equipment and devices. Control voltages shall be less than 100 volts, unless otherwise specified. Equipment controlled by control voltage systems include but are not limited to:

- Motor starters

- Visual and audible alarms and warning equipment

- Fire alarm and suppression equipment

## 3.4.10	Lighting

Facility lighting units shall be maintained at maximum effectiveness. Fluorescent fixtures shall be lamped with alto low mercury volume lamps. Group re-lamping practices shall be employed when practicable. Incandescent fixtures shall be replaced where practical with fluorescent or high efficiency lighting of the same output. Where lighting levels can be lowered, the best approach to fixture or lamp replacement is to be applied. High intensity discharge lighting is used in several locations. Metal halide, high pressure sodium, low pressure sodium, mercury, and quartz lamps shall be replaced in kind, unless otherwise approved by the ACO. Lighting criteria for the facilities is as follows:

- Corridors -- 40 fc

- Storage, warehousing, mechanical spaces -- 20 fc

- Offices, shops and pilot plants -- 75 fc

Supplement with task lighting

- Laboratories -- 100 fc

Supplement with task lighting

- Rest rooms -- 20 fc

Supplement with mirror lighting

- Stair wells -- 75 fc

- Exterior and parking  -- 20 fc

- Building perimeter -- 10 fc

## 3.4.11	Electrical Service on Research Equipment

Maintenance and minor repairs on research equipment which includes, but not be limited to:

- Centrifuges and Autoclaves

- Dishwashers

- Freezers and Refrigerators

- Electric cords

- Lamps

- Manual motor starters

- Switches

- Lab furniture

- Fume hoods

## 3.4.12	Power Disruptions

Unscheduled power outages/disruptions, response time during normal duty is within 15 minutes and within 60 minutes during non-duty hours. Action must be taken to restore service as soon as possible. If unable to resolve the problem within 30 (thirty) minutes, notify the appropriate personnel and arrange for electrical service through an alternate energy source to minimize disruption of service. Temporary power shall be place into operation as required to keep essential equipment and lighting in operation and within 60 minutes of unscheduled/unexpected outage.

3.4.13	Scheduled power outages, coordination and arrangements are required with the research and operating staff to keep required essential equipment and lighting in operation. Arrangement for scheduled outages shall be made as far in advance as practical, and should not schedule power shutdowns with less than 14 calendar days notice. After power is restored, service shall be resumed, reset electrical system components in the affected areas, and notify the appropriate personnel.

## 3.4.14	Preventive Maintenance

Establish and implement a preventive maintenance program for the cleaning, adjustment, and calibration of the building electrical equipment, systems, and controls.

### 3.4.14.1	Ceiling light fixtures. Clean all light fixtures during bulb replacement or annually, which ever occurs first. Each fixture shall be opened, loose dirt, bugs, grease and other foreign matter removed, and glass covering washed. Damaged or malfunctioning fixtures and/or lenses shall be repaired or replaced.

Exhibit 3.4

Electrical Equipment Main

| Quantity | Description | Voltage |
| --- | --- | --- |
| 2 | Main Transformer | 15KV/5 KV 2000KVA |
| 4 | Control Transformer | 5KV -120 75KVA |
| 6 | Disconnects | 15 KV |
| 12 | Disconnects Fused | 5 KV |
| 6 | Double ended Secondary Distribution | 5 KV |
| 11 | Secondary Transformers | 5 KV |
| 12 | Secondary Disconnects | 600 V |
| 6 | Double ended Secondary Distribution |  |
|  | Switch Boards |  |
| 8 | Metering Sections |  |
| 1 | Automatic Transfer Switch | 5 KV |
| 1 | Buss Tie | 5 KV |
| 2 | Buss Tie | 15 KV |
| 1 | Emergency Generator | 2000 KVA |

Exhibit 3.4.7

Elevator Equipment List

| Type | Manufacturer | Year |
| --- | --- | --- |
| Main Building |  |  |
| Passenger | General Elevator | 1968 |
| Service | General Elevator | 1968 |
| Dumbwaiter | Atlantic Elevator | 1940 |
| Passenger | Dover Elevator | 1984 |
| Passenger Handicapped | National Wheel-O-Vator Co. | 2003 |
| Pilot Plant |  |  |
| Freight | Otis Elevator | 1967 |
| Mechanical Services Building (MSB) |  |  |
| Freight | Otis Elevator | 1967 |

# 3.5	Electronic Services

Utilizing the latest state-of -the-art techniques for electronic diagnosis, repair, calibration and installation to maintain, modify, adjust, and repair electronic systems, and all controls and components such as wiring, cables and electronic door sensors in accordance with equipment specifications, manufacturers' instructions, and all applicable Federal, state, and local codes. Maintain an adequate bench stock of electronic parts, including discrete components, integrated circuits, fuses, telephones, speakers, cable, and mechanical equipment necessary for routine repair and maintenance of electronic facilities and research equipment. Installation of electronic equipment and associated hardware and software electronically interfaces between new or existing equipment and computer systems. Prompt diagnosis of malfunctioning electronic equipment is accomplished with a maximum down time allowance for any system or component not to exceed 48 clock hours. Maintain and update a library of technical literature including device specifications, data, books, substitution books, and catalogs. Equipment to be maintained includes but no limited to:

- Telecommunications System

- Voice Mail System

- Satellite Receiver Dish

- Voice Amplification and Public Address System

- Radio Systems

- Electronic Door Sensor

- Building Access and Security System

- Closed Circuit Television System

- Office Printers

- Audio/Visual Equipment

- Fire Alarm System

## 3.5.1	Telecommunications Systems

Adjust, calibrate, program, maintain, and repair the Center's telecommunications system, manufactured by Mitel Incorporated, and, described in Exhibit 3.5.1. This system is an electronic digital voice and data communications system and works in conjunction with the voice mail system manufactured by Active Voice. The communications cabling is a distributed system radiating from the digital switchboard and cable entrance. All maintenance, repair, programming and calibration of the system and peripheral or auxiliary devices shall be carried out by a qualified technician trained in the operation, maintenance and adjustment of the equipment. No repairs or alterations to the equipment source code may be made without the express authorization of the Area Engineer.

### 3.5.1.1	Program and upgrade changes to the central switch as required by the manufacturer. Install, move and remove communications cable (metallic, shielded or fiber) as authorized. Upgrades, changes, reprogramming, and equipment and cable installations, relocations, and removals shall be performed as approved by the Area Engineer. All shifts, moves and changes shall be recorded and maintained as up-dates to the system address register. Update the master record to reflect any shifts moves or changes. The master program disc shall be updated and backed up after each change. A current backup disc and an archival backup disc shall be maintained at the main switch and in the Project Management office.

### 3.5.1.2	Maintenance and repairs. Monitor the system and components and perform the maintenance and calibration required by the system which includes filter changes, equipment cleaning and splice maintenance. Repairs shall be performed by personnel trained and certified by the equipment manufacturer, Mitel, Inc., as being qualified to perform work on the system. This requires the manufacturer's factory training of the key person designated to work with the main telecommunications equipment. Equipment failures shall be repaired within 4 hours of notification for all central switch and station equipment, and within 2 hours for all other trouble calls. The system is equipped with a modem access to the certified manufacturer's representative (Mitel) for system support. Remove and place in stock any device no longer required by the user. Removed equipment shall be serviced before placing into stock. Devices may only be added to the telecommunications system after the type, location, and arrangement of the equipment and service have been approved by the Area Engineer.

### 3.5.1.3	Cabling in use is multi-conductor copper cable in thermoplastic insulation cover, and braided shielded thermoplastic covered conductors and optical fiber cable. All cabling shall be in raceway or cable trays. Cabling is distributed from the incoming cable distribution center to the switch gear and dedicated terminals. From the switch gear, the cabling is distributed to local distribution panels (LDP). Further distribution is made from the LDP to a service block ("can"). From the "can" to the device, local cabling is used. No change, addition or deletion of cabling in the main distribution system (service entrance to "can") may be made without approval of the Area Engineer. Install such cable as required by the users or the system, and from the "can" to the device, as approved by the Area Engineer. All telephone wiring and cable shall be run in plastic or metallic (wiremold or equal) raceway, conduits or power poles, partition conduits, etc.

## 3.5.2	Building Automation System

Adjust, calibrate, program and repair the Center’s electronic building automation and control system. This system, as defined in Exhibit 3.5.2, includes the fire alarm, building access (key card) system, and building security system. All maintenance, repair, programming, and calibration of the BAS and peripheral or auxiliary devices, with exception to the fire alarm system, shall be carried out by a qualified technician trained in the operation, maintenance and adjustment of such equipment. No repair or alteration of the equipment source code shall be performed without the express authorization of the ACO and the NAA Engineer. Cabling presently in use is American Wire Gauge (AWG) 18 cooper single, multiple conductor and twisted pair impedance balanced conductors in thermoplastic insulation cover. Various services have a braided shielded cable covering. Fiber optic cabling shall be interference-isolated from adjacent devices or cables. All optic cabling shall be in raceway or cable trays. All cabling shall be marked to identify the service, destination, function or origin of the service. Cable color code conventions shall be followed. Cable and raceway route shall be made parallel to building lines and be approved by the NAA Engineer before installation. Copies of installation plans shall be maintained with appropriate work order documentation

### 3.5.2.1	Monitor the system and components and perform maintenance and calibration required to maintain reliability and accuracy. Changes to the system shall be accomplished only after review and approval of the ACO and NAA Engineer. Maintain and update the system master records to reflect any changes to the system. Make backup copies of programming at each of the Central Processing Unit (CPU) and Metasys or equivalent programming points. Backup discs or tapes shall be stored at the main CPU location (Room 0016). First and second generation backup disks shall be stored in a location other than Room 0016, such as the electronics shop and/or the Project Manager’s office. Deletions shall be completely removed to the control source and all programming revised. Reusable equipment shall be refurbished and placed in stock and properly inventoried only with the approval of the ACO. Additions approved by the NAA Engineer shall be properly recorded on building as-built documents and transmitted to the NAA Engineer for archival information update. All new equipment and connections shall be completely compatible with the existing equipment and be capable of accepting and transmitting information between the various operating components of the system, and input/output and controlled devices. Maintenance shall include, but not limited to:

- Filter changes in the CPU and field units

- Equipment wipe down and cleaning

- Confirmation of point and transmitter continuity/accuracy

## 3.5.3	Voice Mail System

Adjust, program, maintain and repair the Center’s voice mail system and its database, manufactured by Active Voice. This includes:

- Add, delete and/or modify customer files

- Maintain system message groups for proper operation

- Complete monthly backup of database and messages

- Install special routing instructions

- Quarterly update of voice mail subscribers

- Conduct annual voice mail computer system backup

- Maintain phone line connections to system

## 3.5.4	Satellite Dish System

Maintain operational services for the Galaxy 9 Satellite which includes updating the satellite receiver/check system in May and November of each year and the renewal of annual subscription satellite services for CNN, ESPN, and CNN Headline News.

## 3.5.5	Voice Amplification and Public Address Systems

Repair as needed and maintain in good working order the voice amplification and public address systems. The voice amplification system, located in the auditorium, is locally controlled and equipped with teleconference capabilities. The public address system consists of a central, emergency, and fire system public address system. Test monthly, perform troubleshooting, and repair these systems as necessary. New outlets/speakers shall be placed in spaces that are unable to hear general announcements. Cable and raceway shall be installed as required.

## 3.5.6	Radio Systems

Repair and maintain in good working order the radio/electronics equipment as follows:

- Base Station

- Remote Console

- Two-way Radios

- Pagers

- Battery Chargers

- Two-way Radio/Telephones

## 3.5.7	Electronic Door Sensor

Repair and maintain electronic door entrance located in the chemical wing. Annual maintenance includes partial disassembly to clean, lubricate, inspect, and perform returning and adjustment for proper operation.

## 3.5.8	Building Access and Security System

Repair as needed and maintain in good working order the building security and access system. The system is computer-based central access control with a 24 entry latches and interior doors equipped with electrical controls to unlatch the door based on the appropriate electronic signal. The systems consists of a Central CPU with interpretive data, distributed card readers, security shunt devices and intrusion detection devices. The present system is manufactured by Northern Computer.

## 3.5.9	Closed Circuit Television System

Repair and maintain a Diginet closed circuit television system located in room 0016. Routine services require DVD operations are verified monthly to assure proper operation and playback. Preventive maintenance, to be performed semiannually for the cameras includes cleaning of lenses and glass and verify the proper operation of heaters and compartment fans.

## 3.5.10	Office Laser Jet Printers are to be Repaired as Required.

There are approximately 200 printers to be maintained.

## 3.5.11	Audio/Visual

Setup and maintain sound, video, and projection equipment for meetings, seminars, and special events, and when requested, provide an operator. Ready to be put into operation for seminars and special events with 1 day's notice. Equipment shall be maintained so to put into operation for seminars and special events with 1 day=s notice. This equipment includes, but is not limited to, slides, movies, overhead projectors, microphones, amplifiers, tapes, televisions and VCR/DVD recorders. Provide instructions to personnel for use and operation of audio/visual equipment when requested. Such instructions should include all modes of operation of equipment and possible steps to take in emergency situations or if problems should arise.

### 3.5.11.1	Facility/equipment usage. Maintain a system of control for the loan of portable audio/visual equipment that Center personnel may use on a temporary basis. Instruction on use and operation of such equipment shall also be provided. Loaned equipment should be checked out for proper operation before and after each use to insure proper operation.

### 3.5.11.2	Audio/visual tape or DVD. Provide duplicated copy service as needed.

## 3.5.12	Maintenance and Repair of Scientific Equipment

Troubleshoot, calibrate, repair, and maintain scientific equipment. All safety requirements shall be observed when working in laboratories and other restricted areas. Maintenance and repair services shall not interfere with research activities or laboratory operations. Equipment shall not be removed from its location without the approval of the requestor. If it is determined the equipment is not serviceable, the requestor shall be notified with recommended solutions. Acquisition of new parts or equipment shall be approved by the ACO. The types of equipment covered could include but not limited to:

- Spectrophotometers

- Meters

- Dataloggers

- Oscilloscopes

- Chromatographs

- Amino acid analyzers

## 3.5.13	Fire Alarm System

Operate and maintain a Class A fire alarm system networked through the multiplexed central annunciator system and networked with the central Building Automation System. The system consists of, but not limited to:

- A mix of addressable and conventional devices (pullstations/heat detectors/smoke detectors)

- Siemens MXL main panel in room 0014 main building with( 4) fiber interconnects to MXL panels in outbuildings with( 2) annucators(1) at the front desk and (1) located in the guard s station.

- Pyrotronics system 3 panel linked to Siemens MXL main panel located in room 0014.

- Electronic offsite annuciator for alerting offsite subcontracted monitoring.

3.5.14   Fire Suppression Systems

Establish a schedule and perform the inspection and preventive maintenance of all fire suppression equipment and systems which include:  fire extinguishers (hand type Class A, B, C and D), automated CO2 systems water sprinklers, etc.  These systems shall be maintained for use at all times in accordance with NFPA and OSHA regulations. Conduct an annual inspection of these systems and equipment and furnish a report to the QAS with a copy to the Center Safety Officer by June 30 of each year.  This report shall indicate the number of units on hand, number of units inspection, type of inspection performed, maintenance required and number of units replaced.  All fire suppression equipment and systems shall be included in the Preventive Maintenance Program.

Exhibit 3.5.1

Telecommunication System

The telecommunication system is a multi-tasking digital system with voice and data capabilities. The system consists of, but is not limited to, the following:

º	Central computerized electronic switch with redundant operating plane.

º	Central uninterruptable AC UPS power supply

º	Modem remote maintenance connections

º	Two unit digital communication modem pools

º	Data communications network (32 data-capable voice data handsets)

º	Central control VS220 work station

º	Cable distribution system

º	Main and distributed distribution and connection panels

º	Handset connection outlets and cabling

º	Single-line and multiple-line handsets

º	Data transmission handsets and PC data transmission units

NOTE: The Federal Telecommunications System (FTS2000) consists of a CPU and T1 switch with a maintenance modem connected to the Center Switch. The Contractor shall provide interface with the  representative who is responsible for the operation and maintenance of the FTS2000 system under contract with the General Services Administration (GSA). The Area Property Management Office is the Government contact for FTS2000 and Verizon for interface issues.

Exhibit 3.5.2

Building Automation System

The Center is operated by the action and interaction of a combination of control systems. One portion of the Center's operation controls is the Building Automation System (BAS). The BAS is a melding of a number of generational developments. The BAS consists of:

1.	Electronic field panel measurement and central electronic controls by Siemens.

2.	Distributed digital electronic measurement and controls networked with the central electronic control by Siemens.

7.	Unitary mini- and micro-computer controls on a distributed bus system networked with the central electronic controls by Siemens.

8.	Central fire and security systems networked with the central control.

Building System Equipment

The system includes, but is not limited to, the following equipment:

Room 0014/0016	Main Control Center Siemens BAS with Johnson Control interface.

º	Output Printer

º	Deionized water alarm

º	BAS Monitoring Interface

º	MXL Fire Alarm Panel

º	Security System i.e., CCTV System & DVD Recorder with Various Cameras throughout the Campus

º	Card Access System Computer.

º	Central Telephone System

º	Voice Mail System

º	Center Badge Processing Equipment

# 3.6	Plumbing and Pipefitting Services

Monitor, replace, modify, adjust, and repair all plumbing, piping, steam and water distribution systems and equipment in accordance with equipment specifications, manufacturers' instructions, Federal, state, and local codes and regulations, and the Uniform Plumbing Code. Responsibility for the water supply and sewer piping starts at the main connections to the City water and sewer located at the property lines of the Center. Repairs and adjustments are required to correct observed or reported deficiencies. Piping services shall run parallel to building lines with proper plumb and pitch. Pipe leaks are to be repaired or replaced within 72 hours of discovery. If plumbing service is to be interrupted, Center personnel shall be notified at least 5 work days in advance. In the event repairs on equipment cannot be performed, the ACO shall be notified in writing of the problem with recommended solutions by close of business on the next work day.

Plumbing and pipefitting work includes but not limited to:

- Water mains and distribution systems

- Drain lines including glass piping.

- Steam distribution and return lines, including regulating devices

- Natural gas distribution and fuel oil distribution lines, systems, and associated components

- Water distribution and sewage collection systems

- Plumbing fixtures and equipment

- Fire hydrants and building fire protection systems

- Underground sanitary and storm sewer lines

- Compressed air lines

- Compressed gas lines

- Liquid nitrogen lines

- Installation of new water lines

- Installation of new pumps and related equipment

- Laboratory equipment

- All pipe insulation

3.6.1.	Equipment and System Maintenance requirements includes monitor, repair, replace, maintain, test, modify, and adjust all plumbing equipment, fixtures, piping and systems for the following equipment but not limited to:

- Stills

- Demineralizers

- Vacuum pumps (facilities related)

- Air compressors (facilities related)

- Water closets, urinals, lavatories, personnel showers, etc.

- Safety showers and eye wash stations

- Sinks, including stone sinks and plastic sinks for laboratory use

- Service to outlet valves for various gases

- Faucets and other fixtures

- Dealkylizers, softeners, pumps, valves, traps, regulators, and pressure reducing stations

Repair and maintenance activities include, but are not limited to:

- Inspecting equipment, systems, and piping to ensure proper operation and prevention of leaks

- Lubricating plumbing-related machinery and equipment

- Insulating new plumbing lines and reinsulating repaired piping systems

- Unclogging drains and sewage lines

- Adjusting or repairing leaking joints, faucets, pipes, etc.

- Repairing pumps and valves

- Replacing seals and couplings

- Resetting loose commodes and sinks; unclogging, repairing, and replacing commodes and sinks

- Installing, connecting and/or replacing steam, gas, and water lines to laboratory equipment

- Cleaning storm sewers and catch basins

- Maintaining and repairing plumbing waste lines and valves

- Cutting or drilling holes and openings in walls and floors to set sleeves, thimbles or inserts to provide passage and support for pipe and fittings

- Checking meters and gauges, replacing when necessary

- Painting replaced piping services to ensure color consistency and proper coding/identification

- Replacing valve seats and washers

## 3.6.2	Insulation

Install insulation on piping and equipment whenever repairs or new installations are made. Insulation and method of installation shall be in accordance with OSHA standards. Insulation value shall be at least equal to the material removed or as noted on drawings. Alternative insulation selected shall be appropriate for the conditions, shall reduce heat transfer to the maximum degree feasible, and shall be approved by the Area Engineer prior to installation. Insulation shall be color coded by banding or painting the insulation and stenciled as to service and flow direction.

## 3.6.3	Deionized, Demineralized and RO Water Systems

Maintain and repair deionized, demineralized, and RO water systems which includes changing filter banks, cartridges, and sanitizing systems as required. Maintain the monitoring system to ensure adequate water supplies. The pH, conductivity, and water quality shall be monitored daily and deficiencies in the water quality shall be reported to the research leaders, ACO and Area Engineer within 2 hours of the time the deficiency is noted or reported. The central water systems are monitored at the treatment stations. Repairs and adjustments as required are to be corrected once observed or when deficiencies are reported. If service is to be interrupted, Center personnel shall be notified at least 5 work days in advance via the E-mail system and shutdowns are to be posted in writing on the designated bulletin boards. Notification must also be accomplished through the public address system. In the event repairs to these systems cannot be performed the ACO shall be notified in writing of the problem with recommended solutions by close of business on the next work day.

## 3.6.4	Maintenance and Repair of Steam and Water Distribution Systems

Maintain, test, modify, adjust and repair all steam and water distribution systems to correct observed or reported deficiencies which may include:

- Insulating all lines in accordance with OSHA regulations

- Installing and connecting air, natural, or manufactured gas, sewage lines and water fixtures, such as hydrants, water lines and mains, and water softening and demineralizing equipment

- Measuring, cutting, and threading pipe and assembling pipe sections

- Excavating and repairing underground water, storm, sewer and sanitary sewer lines

- Repairing and replacing steam condensate lines and equipment

- Cutting and welding medium and high pressure system lines

- Replacing worn belts and hoses

- Regenerating various water systems

## 3.6.5	Pipe Identification

All piping shall be color coded and identified to indicate the service and direction of flow by stencil or tags. Each valve shall be tagged as to the service and be given an identifying number. Valve charts shall be provided for all new work and be maintained. Access to these records shall be provided to the ACO, Area Engineer, and other designated personnel immediately upon request.

## 3.6.6	Preventive Maintenance

Alarms and controls involving the piping systems are tested regularly and deficiencies are corrected within 24 hours of discovery. Typical systems with critical alarms are deionized and RO water quality and supply, fire sprinkler system flow and readiness alarms.

# 3.7	Heating, Ventilation, Air Conditioning

Heating, ventilation, and air conditioning require constant and continuous services to maintain an acceptable temperature, humidity, and pressure ranges as identified in Exhibit 3.7, and in accordance with applicable Federal, state, and USDA requirements. Maintain all systems to assure that airflows and pressure gradients are sustained and continuous and comply with all Federal, Agency and Center regulations and policies. Responsible for recognizing malfunctions in the HVAC systems and equipment, troubleshooting the problems, and correcting them before they adversely impact the operations of the facility. Service requirements include but are not limited to:

- Operating heating, cooling, and ventilating systems

- Performing preventive maintenance and other scheduled inspections of heating, cooling, and ventilating systems

- Maintaining and repairing heating, cooling, and ventilating equipment

- Performing water tests

- Treating water with chemical additives

## 3.7.1	Boilers and Chilled Water System

Install, maintain, modify, adjust, and repair to ensure continuous service is provided 24 hours a day, 7 days a week. Steam pressures, water temperatures and levels are to be maintained at all times, and all piping, electrical and control systems are to be serviced and maintained. Make all necessary repairs and adjustments to boiler and chiller equipment to correct reported or identified deficiencies so to maintain required operations. All repairs and adjustments shall be made in accordance with equipment specifications and manufacturers' instructions. The ACO shall be notified of inability to perform repairs on equipment by a written explanation of the problem and recommended solutions by close of business the next work day. Standby/backup equipment shall be available immediately for operation upon the discovery of problems with the primary equipment. Typical maintenance and repair tasks include, but are not limited to:

- Recording systems operating conditions daily

- Repairing and replacing components

- Cleaning nozzles and oil filters

- Repacking valves

- Greasing and oiling motors and other equipment

- Performing general housekeeping of equipment and spaces

- Checking and maintaining motors

- Checking and cleaning traps

- Adjusting controls for safe and economic operation

### 3.7.1.1	Boiler plant operations are to be maintained by licensed operator/mechanics. The plant shall be staffed 24 hours a day 365 days a year. Steam generating equipment consists of three (3) automatic oil/gas fired boilers. Two (2) boilers are rated at a nominal 8,000 pounds per hour at 120 psig, and one (1) boiler rated at 8,000 pounds per hour at 120 psig. Plant capacity is 16,000 pounds per hour. The plant operates at high pressure (120 psi, +/- 5 psi) 24 hours a day 365 days a year. One boiler shall be in operation at all times to meet the services requirements of the Center. The second boiler shall be on standby as backup or to supplement when needed for additional steam generation or during periods of extreme cold. The third boiler shall be available for use as backup when the other two boilers malfunction or out of service for maintenance or repairs. Boiler plant controls are included in the components of the Building Automation System (BAS). Types of fuel used in the plant operations are natural gas from the local utility company, No. 6 low-sulphur oil, and No. 2 heating oil. Activities required to operate and maintain all the boilers include, but are not limited to:

- Blowing down boilers, deaerators, air tanks, and makeup water tanks

- Testing boiler water chemistry for alkalinity, sulfide, calcium, hardness, pH, and total dissolved solids

- Adding boiler water treatment chemicals

- Monitoring fuel oil and water levels

- Monitoring/maintaining boiler panels for proper operation

- Monitoring/maintaining feed water pumps, sump pumps, and condensate return pumps

- Maintaining water softeners and tanks

- Regenerating water softeners

- Monitoring/maintaining safety valves, pressure controls, low gas pressure cutoffs, low oil pressure interlocks, and boiler controls

- Visually inspecting the cooling tower at least twice daily when operating

- Maintaining logs of boiler plant operating characteristics daily

- Recording daily fuel readings and water usage

### 3.7.1.2	Auxiliary steam generation plant at Building 3 consists of an oil-fired boiler and is to be operated and maintained to service satellite buildings and their functions. The electric-fired steam generation plant in Room 0207 and the clean steam, steam-fired generators in the first floor mezzanine area in Building 4 provides services to the Engineering Science Research Unit (ESRU). The Contractor is NOT responsible for this equipment, except for pressure vessel inspection and the piping system to the main valves at the using equipment being served.

### 3.7.1.3	Chiller Plant Operations consists of a 500-ton and 300-ton centrifugal water chillers and a nominal 290-ton steam absorption-chilling unit. Plant capacity is 1090 tons, presently operating at 1,200 gpm at 10oF temperature rise; 42oF to 52oF. Fuel used for chilled water generation is electricity and low-pressure steam. The absorber, which is controlled by the Building Automation System (BAS), shall operate 24 hours a day, 7 days a week to ensure continuous service. Operation and maintenance activities include, but are not limited to:

- Maintaining proper levels and quantities of makeup water and glycol (20% to 35% concentration).

- Maintaining and adjusting unit generation load balances

- Replacing air filters regularly

- Inspecting and lubricating all fans, including cooling towers

- Flushing and cleaning condensers, evaporator tubes and heat exchangers

- Inspecting, testing, and maintaining pressure relief valves, control valves, filters, strainers, traps, air compressors, line regulators, gauges and pumps, etc.

- Eddy current testing the tubes of units having removable headers and a capacity of 45 tons or more every 3 (three) years. More current test was completed in 2003.

- Observing and recording data, and maintaining the operation and accuracy of meters, measuring and controlling devices to assure proper water control, levels, and chilled medium output.

## 3.7.2	Dedicated Cooling Units

There is (1) dedicated cooling unit:  for Rooms 3208 and 3210 in Building 4, The unit consists of a primary and secondary or backup cooling unit to maintain special environmental conditions at all times. The units for Rooms 3208-3210 are connected to the glycol system in Building 4. System operations are 24 hours a day, 7 days a week.

## 3.7.3	Water Testing and Treatment

Monitor water conditions and provide treatments as needed. Perform daily water quality tests of boiler water, cooling tower water, feed water, condensate return, and water softeners. Provide a continuous supply of treatment additives to maintain water quality for boiler and chiller systems in accordance with equipment manufacturers specifications and instructions. Comply with all environmental regulations as they pertain to the use and maintenance of chemicals for these operations. The MSDS sheets for all chemicals shall be obtained from the manufacturer and maintained. Maintain records of daily and weekly water tests performed. Interpret test results and apply the appropriate water treatment required to bring the water tests within the specified ranges as specified in the boiler operations manual.

## 3.7.4	Boiler and Other Pressure Vessel Inspections

Conduct and witness annual inspections of all boilers and pressure vessels (fired and inferred) not later than December 1 in accordance with the Commonwealth of Pennsylvania regulations and the American Society of Mechanical Engineers (ASME) code for fired and inferred pressure vessels by an independent licensed and certified inspector. Pressure vessels with a rating of 15 psi or more, a tank size of 6 inches in diameter or more, regardless of size, and vessels with a working pressure of 150 psi or more, regardless of size shall be inspected. Document the results and provide this documentation and a copy of the inspector’s report to the ACO and the NAA Engineer within five (5) working days after receipt of the inspector’s report.

## 3.7.5	Fuel Oil

Establish and implement a schedule for inspecting and stocking all fuel oil tanks and levels. Monitor and record fuel oil levels of bulk tanks weekly to ensure that the supply does not fall below 25% of any tanks' capacity at any time. Measure the volume of fuel in the tanks by "sticking" the tanks on a regular basis. When any of the tanks' levels reaches 25%, provide the Government Purchasing Agent with the amount and type of fuel needed and the required delivery date in writing not less than 48 clock hours notice of a requirement for fuel oil purchases.

## 3.7.6	Ventilation Systems

Maintain, modify, adjust, and repair all ventilating systems and related equipment in accordance with all applicable Federal, state, local and Agency regulations, equipment specifications, and manufacturers' instructions. These systems, which are connected to the Building Automation System, are used for maintaining the indoor air quality, cooling, heating, and humidifying of various spaces, and evacuating or exhausting spaces for maintenance of relative air and space pressures and flows. Maintain all buildings at proper ventilation, air flow, and temperature year round. Maintain operations and repair of equipment shall include, but not be limited to:

- Controls

- Filters

- Blowers, intakes/exhaust

- Air supply units

- Pumps

- Heating/cooling coils

- Dehumidifiers and humidifiers

- Insulating ducts, pipes, and fittings for heat

- Conservation

- Steam distribution lines

- Return condensate lines

- Exhaust hood systems and associated air systems

Perform repairs and adjustments to correct observed or reported deficiencies as scheduled. Repairs requiring the shutdown of a HVAC system shall be approved by the ACO at least 5 working days in advance of the shutdown. Notification to ERRC personnel of shutdowns are to be accomplished via E-mail, posting notices on designated bulletin boards and a voice announcement through the public address system. Response to emergencies involving the HVAC systems shall occur within 15 minutes after notification during duty hours and within 60 minutes during non-duty hours.

Maintenance tasks include, but are not limited to:

- Performance testing and balancing

- Changing filters

- Adjusting air, heating, cooling, and humidifying controls, flows, and load balances

- Maintaining and checking proper operation of seals, gauges, regulators, pumps, flow measuring and indication devices, cooling towers and related equipment

- Testing and maintaining motors, drives, and fans

- Adjusting and adding lubricants to bearings and motors, as needed

- Repairing air handlers and systems and related equipment, such as pumps, blowers, fans, pulleys, belts, pneumatic and electrical controls, switches, relays, etc.

- Adjusting drives and fan or blower speeds

- Maintaining and replacing air and water filtration units

## 3.7.7	Heating and Air Conditioning Systems

Maintain, modify, adjust, balance and repair all heating and air conditioning equipment in accordance with applicable Federal, state, and local regulations, equipment specifications, and manufacturers' instructions to retain appropriate cooling, heating and humidification of various spaces. Check and record daily various temperature and humidity readings to document buildings are maintained at proper temperatures year-round and controlled environmental rooms are maintained in accordance with the scientists' specifications. Repairs and adjustments to correct observed or reported deficiencies are to be accomplished as scheduled. Repairs requiring the shutdown of a system shall be approved by the ACO at least 5 working days in advance of the shutdown. Notifications regarding shutdowns are to be sent to ERRC personnel via E-mail, posted notices on designated bulletin boards and voice announcements through the public address system. Emergency responses involving these systems are to be accomplished within 15 minutes after notification during duty hours and within 60 minutes during non-duty hours. Operations, maintenance, and repair includes, but not limited to, the following equipment:

- Controlled temperature and/or humidity rooms

- Air compressors

- Air- or water-cooled condensers

- Packaged air conditioning units

- Packaged heating units

- Furnaces, space heaters, heating coils, etc.

- Window air conditioning units

## 3.7.8	Logs and Records

Prepare and maintain logs and records necessary to manage the entire HVAC system, utilizing the capabilities of the Building Automation System. The following logs shall be maintained and available for review and approval by the ACO and other designated Government personnel:

- Fuel (oil and gas) consumption log

- Electricity consumption log

- Water consumption log

- Chemical additives log

- Boiler data log (from BAS)

- Water treatment logs

- Temperature and humidity profiles of controlled spaces (from BAS)

## 3.7.9	Building Automation System

The Center is operated by the action and interaction of a combination of control systems. One portion of the Center’s operation controls is the Building Automation System (BAS). The BAS is a melding of a number of generational Developments. The BAS consists of but is not limited to:

- Basic room sensors, static pressure regulators, electrically operated valves, etc.

- Basic single and two-pipe pneumatic controls

- Advanced pneumatic controls, fluidic technology, etc.

- Networked electronic and pneumatic points through the central control room 0014 with satellite stations at the MSB and service building

- Electronic field panel measurement and central electronic controls

- Distributed digital electronic measurement and controls networked with the central control

- Unitary mini-and microcomputer controls on a distributed bus system networked with the central electronic controls

## 3.7.10	Preventive Maintenance Equipment Listing and Job Plans

See Appendix VII.

## 3.7.11 Building Automation System Equipment

See Exhibit 3.7.

Exhibit 3.7

Building Automation Equipment

The system includes, but is not limited to the following equipment:

Room 0014	Main Control Center Siemens Main Server interfaced with JC-85/40 and Metasys system.

Output Printer

BAS interface

| Area | 210 | DSC Control Panel |
| --- | --- | --- |
| Room | 0010 | Pneumatic Control Panel |
| Room | 0021 | Pneumatic Control Panel |
| Room | 0026 | Pneumatic Control Panel |
| Area | 0224 | Pneumatic Control Panel |
| Area | 4209 | Pneumatic Control Panel |
| Area | 4211 | Pneumatic Control Panel |
| Area | 4212 | Pneumatic Control Panel |
| Area | 6010 | Pneumatic Control Panel |
| Area | 6314 | Pneumatic Control Panel |
| Area | 6414 | Pneumatic Control Panel |
| BLDG 3 | Rm 201 | Pneumatic Control Panel |
| BLDG 5 | Rm 001 | BAS Monitoring Interface |

Center Temperature Policies

Heating Season Temperatures

Not more than 70oF, plus or minus 2oF during the day and 55oF after normal work hours.

Cooling Season Temperatures

Not less than 76oF, plus or minus 2oF.

Research Laboratories

Shall be kept constant at 72oF, plus or minus 2oF, with a relative humidity of 45% to 65%, 24 hours a day, 365 days per year.

Processing Rooms

Building 6 (2nd Floor) shall be kept at 50oF, plus or minus 2oF during processing. During nonprocessing, these areas shall be kept at 65oF, plus or minus 2oF.

Food Engineering Area, Diary Processing Area (Pilot Plant Wing) and Solvents

Processing Room 2226

These areas require 100% fresh air and shall be kept at 72oF, plus or minus 2-1/2oF during processing.

Storage and Unoccupied Areas/Spaces

These areas shall be kept between 45oF and 90o

Special Environmental Areas

Rooms 3208 - 3210 (Bldg. 4)		Low Temperature Room

Rooms 6200 - 6210 (Bldg. 6)		Special Biological Rooms (BSL2)

Room 2226 (Bldg. 4) 				Solvents Processing

Rooms 2212 - 2225 (Bldg. 4)

Rooms 3212 - 3225 (Bldg. 4)		Food Engineering Labs

Rooms 0218 - 0230 (Bldg. 4)		Dairy Processing Lab

Rooms 0215 - 0217 (Bldg. 4)

Rooms 1215 - 1217 (Bldg. 4)		Bio-Engineering Area (BSL2)

Room 0217 (Bldg. 4)				Pathogen Challenge Suite

# 3.8	Routine Refrigeration Services

Maintain and repair refrigeration equipment and systems including, but not limited to:

- Chillers

- Compressors

- Air and Water Coiled Condensers

- Evaporators

- Refrigerators and freezers

- Air conditioning units, including split systems, window units, and commercial units

- Drinking fountains

- Ice-making machines

- Cold rooms

- Controlled temperature rooms

## 3.8.1	Refrigeration Equipment

Maintain, adjust, balance, and repair all refrigeration equipment in accordance with applicable Federal, state, and local guidelines, equipment specifications, manufacturers' instructions, and the preventive maintenance schedule. Respond to emergencies involving building refrigeration systems, walk-in freezers and cold rooms, incubators, deep freezers, and all other equipment that might jeopardize ongoing research work within 15 minutes after notification during duty hours and within 60 minutes during non-duty hours. Locate and diagnose malfunctions, and make repairs and adjustments to correct observed or reported deficiencies. Repairs requiring shutdown of any system shall be approved by the ACO at least 48 hours in advance of planned work. In the event of inability to perform timely repairs on equipment items, provide a written explanation of the problem and recommended solutions to the ACO by close of business the next work day. Routine maintenance includes, but is not limited to:

- Inspecting equipment to ensure proper operations

- Lubricating motors and fans

- Cleaning and wiping equipment and components such as sight glasses and gauges

- Maintaining appropriate oil and refrigerant levels and recording the amounts of additions

- Testing controls

- Checking for leaks and making appropriate repairs

- Repairing motors, fans, compressors, belts, pulleys, relays, switches, condensers, controls, evaporators, thermostats, valves, etc.

## 3.8.2	Minor Installations and Modifications

Contractor is responsible for minor installations of new, replacement, or moved refrigeration equipment. Ensure that the installation is done correctly and the equipment is functioning properly.

## 3.8.3	Maintenance of Environmental Rooms

Maintain the environmental rooms listed in Exhibit 3.8.3. Develop, maintain and monitor a system to add or delete an environmental room during the term of this contract. The number and location of units may increase or decrease as research program requirements warrant.

## 3.8.4	Service and Preventive Maintenance

Include all refrigeration equipment and systems in the preventive maintenance program and schedules. Develop and implement a leak detection plan in compliance with all applicable regulations for all liquid and gaseous materials in use to prevent environmental contamination. Refrigerant handling shall be carried out by qualified mechanics so not to cause the release of any gaseous refrigerant or similar material to the atmosphere. Recycling/reclaimant equipment shall be utilized and recycling and/or disposal plans shall be implemented. Properly dispose of any liquid materials, refrigerants, cooling agents, oils, etc. in accordance with current OSHA, EPA, USDA, and local regulations.

## 3.8.5	Maintenance and Repair of Scientific Equipment

Install, maintain, modify, adjust, and/or repair scientific equipment in accordance with manufacturers' specifications, and Federal, state, and local regulations. Equipment repairs shall not interfere with laboratory operations and all safety precautions shall be observed when working in laboratories or other restricted areas. Equipment shall not be removed from its location unless approved by the scientific requestor and ACO. If the equipment is not serviceable, provide the ACO a written explanation of the problem and recommended solutions by close of business the next work day. Such equipment could include, but is not limited to:

- Incubators

- Shakers

- Water baths

- Refrigerators, freezers (specialty)

- Special controlled temperature rooms (excluding those in Exhibit 3.1.9)

- Growth chambers

- Environmental chambers

Exhibit 3.8.3

COLD BOX REPORT

NAME:  _____________________________	DATE:  _____________________________

| LOCATION | TEMP | READING #1 | READING #2 | READING #3 | RESPONSIBLE SCIENTIST | PHONE EXT | HOME PHONE |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Time |  |  |  |  |  |  |  |
| 3107-Cold Room | 38-42 |  |  |  |  |  |  |
| MSB Vista A | 5C-11C |  |  |  |  |  |  |
| MSB Vista B | 40F-45F |  |  |  |  |  |  |
| MSB 227A | 1C-7C |  |  |  |  |  |  |
| MSB 228A | 4C-10C |  |  |  |  |  |  |
| MSB Mush. Box 1 | Variable (Off) |  |  |  |  |  |  |
| MSB Mush. Box 2 | Variable (Off) |  |  |  |  |  |  |
| MSB 231D | Out of Service |  |  |  |  |  |  |
| MSB 227B | Out of Service |  |  |  |  |  |  |
| 0129A Growth | Variable |  |  |  |  |  |  |
| 0129B Growth | Variable |  |  |  |  |  |  |
| Path 1 | 35-39C |  |  |  |  |  |  |
| Path 2 | 8-12C |  |  |  |  |  |  |
| Path 3 | 10-20F |  |  |  |  |  |  |
| Path 4 | 37-40F |  |  |  |  |  |  |
| 0213A | -24C to -16C |  |  |  |  |  |  |
| 0213B | -24C to 16C |  |  |  |  |  |  |
| 0213C | 1C-7C |  |  |  |  |  |  |
| 0213D | 38F |  |  |  |  |  |  |
| 0213E | 0F1 |  |  |  |  |  |  |
| 1207 | 1C-7C |  |  |  |  |  |  |
| 2121A | 1C-7C |  |  |  |  |  |  |
| 2121B | 33C-40C |  |  |  |  |  |  |

# 4.0	General Maintenance

Performance of services, as defined in the specific requirements, includes grounds maintenance, pest control, general moving, and housekeeping services. Government Furnished Equipment/Material for all services is listed in Attachment IX.

## 4.1	Grounds Maintenance Services

Submit a Grounds Maintenance Plan and Schedule to the ACO for approval within 30 days after contract award and update it by November 1 of each succeeding year. The information furnished shall include: fertilizer application plan, weed control plan and schedule, trimming and pruning schedule, seasonal planting plan, and snow and ice removal plans.

## 4.1.1	Lawn Care

There are 16 acres of grounds to be maintained.

### 4.1.1.1	Mowing, trimming and edging. Mow, trim, and edge all lawns to maintain the grass at least 1-1/2 inches but no greater than 3 inches in height. Wind rows caused by improper mowing shall be recut. Debris, including grass clippings, shall be removed from the facility or properly composted. Grass clippings shall be removed from all walkways concurrently with mowing and trimming. Handwork, including trimming around buildings, trees, shrubs, parking signs, fire hydrants, and other obstructions, is considered part of the mowing task and shall be performed concurrently with mowing. Grass or other vegetation encroaching on hedge rows or flower beds shall be neatly cut and removed in such a manner as to leave a well-defined edge between the lawn area and the hedge rows or flower beds.

### 4.1.1.2	Weed control. Chemicals used for weed control for all grounds must comply with state and EPA regulations. Application of such chemicals shall be in accordance with the manufacturer's recommendations and applicable regulations. All MSDS sheets for these chemicals shall be maintained.

### 4.1.1.3	Seeding. Seed or recondition the lawns, when required for uniform growth of grass. The current mixture of grass seed used is 50% Kentucky Blue, 30% Penn. Lawn Fescue, and 20% Manhattan.

### 4.1.1.4	Fertilizing. Conduct a soil test each year to determine the need for fertilizing the grounds. The test results will determine the type of fertilizer, the application rate, area to be fertilized, the approximate date of application and quality control procedures to be used. Fertilizer currently used for the lawn is 10-6-4, slow release granular organic. Any and all fertilizers proposed for use must be approved before application by the Center’s Safety Officer to assure the fertilizer will not harm or interfere with the research work at the facility. This approval does not constitute agreement that the fertilizer is the most suitable for the conditions.

## 4.1.2	Plant, Scrub and Tree Maintenance

Plant, weed, trim, prune, water, mulch, and fertilize flower beds, shrubs, and trees to obtain shape, size, and growth characteristics that meet professional standards. Trimming and pruning shall be accomplished regularly and in accordance with standard horticultural practices. Care shall be exercised not to damage any existing vegetation or structures. All clippings and debris are to be collected and removed from the facility or properly composted. The maintenance area consists of 20,000 square feet.

## 4.1.3	Removal of Stumps, Excess Vegetation, Leaves & Trash

Remove all unwanted and inappropriate vegetation, wood, trash and debris from the grounds giving special attention to areas of high sensitivity and visibility. Remove all leaves and excess vegetation from the grounds, including lawns, parking areas, culverts, and rain gutters. Leaves shall be removed as they accumulate, and not less than weekly during the fall season. This material shall be composted. Maintain the compost area by keeping the area free of debris to provide easy access to the area. All composted materials are to be placed in flower beds annually. Arrange for trash, paper, wood refuse, etc., (which may include branches and leaves) to be removed from the grounds and buildings for disposal according to local regulations. Remove trees and tree stumps as required. Stumps shall be ground down to a minimum of 12 inches below the existing grade level. All resulting debris shall be removed and the affected area graded and seeded/sodded to match the surrounding area. All areas near intakes for air handlers shall be cleaned monthly except during the fall leaf season and then they shall be cleaned weekly.

## 4.1.4	Disease and Insect Protection

Provide services to preventing disease and insect infestation of the vegetation at the facility. Identify the problem and recommend a solution to the QAS, and when necessary request the services or advice of USDA Extension agents or other recognized experts. A copy of the expert recommendation shall accompany any reports or requests for approval. Dispose of disease and insect-infested vegetation off-site and in accordance with state and local regulations. Maintain a record of chemicals (with MSDS sheets) used. Suitable disease preventive(s) and/or insecticide(s) shall be applied to the vegetation as necessary to maintain acceptable conditions. Prior to any chemical application, each such preventive application and insecticide application shall be reviewed by the Safety Office for concurrence.

## 4.1.5	Storm Damage

Inspect the grounds for storm damage on the first work day after each major storm. The results of these inspections shall be documented in incident reports. Tree branches that have been damaged and/or pose a safety hazard will be removed and properly disposed of immediately. All roadways and walkways shall be cleared immediately of any obstructions, such as tree limbs and other debris. Damage to lawns, bushes, trees and flower beds shall be reported to the ACO and repaired in accordance with the applicable sections noted throughout section 4.1.

## 4.1.6	Picnic Tables

Shall be set up during the period of April through November and cleaned weekly. Trash cans in the area of the picnic tables shall be emptied weekly. From December through March, picnic tables are to be stored in the Vehicle Storage Building, 2nd floor.

## 4.1.7	Snow and Ice Removal

Install blunt-end resilient curb and culvert markers at appropriate spots before the first snow fall. Each marker shall be removed in the spring. Ensure no damage is done to existing roadways, curbs and equipment during snow and ice removal. Fire hydrants, oil fill valve stations and culverts must remain accessibility after plowing the area. Special care must be taken not to dump snow on the fuel oil inlet, or in such locations which will impede Government operations or the removal of succeeding snowfalls. There are 16,322 square yards of roadway and parking areas and 888 square yards of walkways to be maintained.

### 4.1.7.1	Removal. Remove snow and ice from walkways, entrances, parking lots, and roadways so that these areas are clean and safe for pedestrian and vehicular traffic at the start, during, and at the end of the facility's workday. Snow removal on facility roadways shall start automatically when the snow level reaches two (2) inches in depth. All snow shall be removed from roadways, walks, etc., regardless of depth at the end of a snow. Snow removal is to be initiated within two (2) hours after automatic response requirements are met or notification by the ACO or other authorized Government representative.

### 4.1.7.2	Deicing. Spread sand and/or salt or other deicing materials on walkways, around entrances, and on parking lots and roadways during snow and/or icy conditions as soon as these conditions develop during working and nonworking hours. Deicing material shall not damage vegetation or other surfaces such as concrete, tile, etc.

### 4.1.7.3	Priority of snow clearing and deicing. Snow clearing shall proceed according to the following priorities:

- Main Building - Front Entrance. Remove snow/ice from all sidewalks, front and lower steps, and walkways. Avoid excess salt around the holly trees.

- Main Building - All Rear Entrances. Remove all snow/ice from the sidewalk, crosswalks, and entranceway.

- Out Buildings - Remove snow/ice around the HazOps, LRB, MPL, MSB, and boiler house including steps from the parking lot.

- Roadways/Parking lots - Remove snow/ice from all roadways and parking areas.

# 4.2	Pest Control Services

Provide pest control services for entry prevention and eradication of mice, rats, and vermin, eradication of roaches and treatment and eradication of termites. Federally approved pesticides or other non-pesticide methods that are proven to be effective for the specific coverage shall be used. A list of proposed pesticides for use shall be reviewed for concurrence by the Center’s safety office prior to beginning any work. Pest control services are to be performed so as to cause the least practical disturbances to Government employees, activities, and research. Emergency pest control situations shall be responded to within 8 hours of notification. Precautions are to be taken to prevent injury to humans, domestic animals, and property as a result of treatment. All work shall be performed in accordance with Federal, State, and local regulations, using procedures recommended by the National Pest Control Association. Special care is to be used when applying liquid insecticides on asphalt, mastic, or linoleum surface areas and premises shall be cleaned following productive treatment. Pesticides shall not stain or discolor walls, ceilings, floor coverings, or baseboards. Maintain MSDS information for any and all chemicals used to perform the services in this section. Maintain a continuing program of inspection and treatment to prevent infestations of pests. Whenever conditions conducive to breeding or harborage of pests are noted, a report noting such conditions and the recommended correction action shall be submitted to the QAS for concurrence.

## 4.2.1	Pest Control Preventive Maintenance

Provide a schedule of pest and insect control for both exterior and interior of the buildings within 30 days after contract award and updated by November 1 annually.

# 4.3	Routine Moving Services

Move furniture, equipment, and supplies among rooms, buildings, and to and from the loading dock as required. All such activity shall be coordinated with the ACO, QAS, Property Specialist, and Area Engineer.

4.3.1	Modernization

Relocation of scientific staff and equipment will be conducted annually as each phase of the Center’s modernization program is renovated. Moving plans and schedules, which shall include relocation of operational utilities to support both scientists and equipment, are to be submitted to the Area Engineer and ACO 30 days prior to the relocation date established by the ACO. All debris and dirt associated with the performance of these duties shall be removed from the site.

## 4.3.2	Disposal of Excess Property

Disposal services shall be coordinated with the Center’s Property Officer, except for receipt of equipment and materials from commercial sources which will be handled in accordance with the requirements outlined in the Shipping and Receiving section of this PBWS. Removal services will be required for donated excess property within the local Philadelphia and suburban areas.

## 4.3.3	Rigging

Rigging of sensitive equipment and heavy (over 1,000 pounds) or large (over 7'-0" high by 5'-6" wide by 10'-0" long) shall be accomplished by a qualified commercial source to rig into place, off load vehicles or transport such equipment among rooms, buildings, from or to the loading dock or to remote locations. ACO approval is required before scheduling work. These services will be viewed as additional work and will be negotiated when a request is received for action.

## 4.3.4	Government furnished equipment is noted in Attachment IX.

# 4.4	Janitorial/Housekeeping Services

Remove soil from all surfaces including, but not limited to, floors, carpets, stairs, walls, wall hangings, windows, furniture, fixtures, doors, equipment and lamps, and trash removal. Work shall be performed in compliance with applicable Federal, State and local safety regulations, and at a minimum, in the frequencies noted in the Matrix of Services, Exhibit 4.4. Services will be performed during the hours of 7:00 a.m. to 4:30 p.m., Monday through Friday, except Federal holidays and other days designated by Federal Statue, Executive Order, or Presidential Proclamation. Submit a janitorial work management plan to the ACO 30 days after contract award, and annually by October 10. This plan will show completion of services performed by building/area, day, AM/PM shift and frequency as noted in Exhibit 4.4.

## 4.4.1	Trash Removal

All waste baskets (550 each), and other trash containers shall be emptied and returned to their original location. Boxes, cans and papers placed near a trash receptacle and marked trash shall be removed. Soiled or torn plastic trash receptacle liners in such receptacles shall be replaced. Ashes and debris removed from cigarette butt receptacles shall be placed in a nonflammable container. All trash collected shall be deposited in outside trash containers and not stored within any building at the end of the shift in which it was collected. The trash shall be deposited in the nearest outside trash collection point. All sanitary napkin disposal containers (estimated 12 containers), shall be maintained in a manner that leaves a pleasant odor and at a minimum, shall be emptied each day without exception. The containers shall be cleaned, sprayed with a disinfectant spray and replace the receptacle plastic liner. Waste collection containers shall be thoroughly cleaned every two months.

### 4.4.1.1	Recycling. The following waste paper products are to be separated from other paper products for recycling: bond paper, copier paper, tablet paper, envelopes, newspapers, books and magazines. Light bulbs, scrap metal, aluminum cans, printer cartridges, and packing material are recycled materials.

### 4.4.1.2 	Biological waste containers. Remove hazardous waste, carcasses, etc., and place into the designated area on a daily basis. Pickup areas are various locations in the main building and Mechanical Service Building. Annual biological waste removal is approximately 49,000 lbs.

### 4.4.1.3	Ashtrays, smoking stands and sand urns. Nine receptacles shall be cleaned daily. Sand urns shall have the sand changed monthly with commercially available play sand quality.

## 4.4.2	Carpet Vacuuming

There are 41,000 square feet of carpets and rugs to be vacuumed. Carpeted floors shall be free of all visible litter and soil. Any spots shall be removed as soon as noticed using an approved cleaning solution.

4.4.3	Floor areas (89,000 square feet) which include hallways and stair wells, shall be swept and mopped. All floors shall be clean and free of dirt streaks, no dirt shall be left in corners, behind radiators, under furniture, behind doors, on stair landings, or treads. No dirt or trash shall remain on sidewalks, entrances, garages, or other assigned areas.

4.4.4	Floor mat cleaning. Carpet type entrance mats shall be vacuumed to remove soil, grit, and to restore resiliency of the carpet pile. Floor under the mat shall be cleaned as specified in Section 4.10.3, Class D Floor Refinishing, before mats are returned to normal location. A total of 13 mats are located at all exterior entrance doors with corridors located:

- Rear Chemical Wing basement door

- Front Administrative Wing basement door

- Corridor door at Room 0211

- Front Lobby inside entrance door

- Stair Tower Entrances at Rooms 0111, 0213 and 0231

4.4.5	Dusting. Remove all dirt and dust without streaks, smudges, damage and/or discoloration of finished surfaces and materials.

### 4.4.5.1	Low dusting. Low dusting of all rooms is the removal of all dust, lint, litter and dry soil on horizontal and vertical surfaces, such as radiators, desks, file cabinets, glass table tops, brass fixtures, office door panels, louvers, doorways, phone booths, fire extinguishers, sills and window blinds below a 7 feet level. Do not disturb papers, books, and other materials located on desks, tables, cabinets or files. Do not disturb scientific equipment. After low dusting, all dust, lint, litter, and dry soil shall be removed from the horizontal surfaces of desks, chairs, file cabinets, and either type of office furniture and equipment, and from horizontal ledges, window sills, hand rails, etc., to a line of 7 feet floor level. There shall be no dust streaks or marks left by dusting tools.

### 4.4.5.2	High dusting. High dusting of all rooms shall be performed in accordance with the Matrix of Services, Exhibit 4.4. High dusting is the removal of all dust, lint, litter and dry soil from all surfaces above 7 feet from the floor level. It includes but not limited to ledges, shelves, grilles, registers, stairways, and window blinds. Debris and dirt loosened by high dusting shall not fall onto research equipment, research samples, computers, or other laboratory and/or office equipment. After completion, all floor surfaces shall be cleaned according to guidelines noted in section 4.4.10. There shall be no dust streaks or marks left by dusting tools.

## 4.4.6	Drinking Fountains

Clean and disinfect all porcelain and polished metal surfaces, including the orifices and drain for 25 units. All surfaces must be free of streaks, stains, spots, smudges, scale and other obvious soil. Exterior side surfaces shall be clear of dust, dirt and water spots.

## 4.4.7	Chalkboards and White Boards

Clean, remove all writing, dust, streaks, marks, chalk dust, and smudges from the tray for the 10 boards located throughout the facility. Erasers shall be cleaned when they no longer remove markings from the boards. Boards marked Do Not Erase shall not be cleaned.

## 4.4.8	Spot Cleaning

The Contractor shall remove smudges, fingerprints, marks, streaks etc., from washable surfaces of walls, partitions, doors, and fixtures. The surface must be maintained to have an clean, uniform appearance free of streaks, spots, and other evidence of removed soil. Spot cleaning shall be as noted in the Matrix of Services, Exhibit 4.4

## 4.4.9	Restroom Cleaning/Disinfecting

Twenty three (23) restrooms, located throughout the facility, shall be cleaned and disinfected in accordance with the frequencies noted in the Matrix of Services, Exhibit 4.4. All showers, wash basins, partition, walls, mirrors, lights, flush handles, faucets, metal fixtures and plumbing units shall be cleaned so all surfaces are free from streaks, stains, scale, scrum, urine deposits, rust stains and pungent odors.

### 4.4.9.1	Restroom stock supplies. Maintain stock at all times of toilet tissue, paper hand towels, seat covers, liquid hand soap and facial tissues in all restrooms.

## 4.4.10	Floor Refinishing

All floors accessible to floor machines shall be refinished. This includes dry buffing, spray buffing, stripping and waxing according to the following schedule and standards. Floor refinishing shall leave a uniform, glossy appearance, free of scuff marks, heel marks and other stains and discolorations. All floor maintenance solutions shall be removed from baseboards, furniture, trash receptacles, etc. All office furniture or other items moved for floor refinishing shall be replaced in the proper position. Floor covering in rooms 0020, 0022 and 0024 are excluded from this work. Rooms 2112 through 2130 shall be cleaned and sealed only.

### 4.4.10.1	Class B refinishing. Applies to all floors, except those noted in Section 4.4.10, and shall be performed every 6 months. Schedule for this work is to be submitted annually by October 10 to the ACO and show the area, and specific day work is to be started and completed.

### 4.4.10.2	Class C refinishing. Consists of sweeping and damp mopping all floor areas, except those noted in Section 4.4.10, patching the scuffed damaged sealer and wax finish of all worn areas or where the tile has been replaced. Work shall be carried out on a monthly basis except during the period when B refinishing is done in that specific area. Class C refinishing shall be performed within 1 week if a deficiency is noted.

### 4.4.10.3	Class D refinishing. Performed weekly, applies to the floor coverings in the cafeteria, all corridors, stairs and stairwells of Buildings 4 and 6. Consist of sweeping all floors of loose dirt with a treated mop, and damp mopping with a solution of liquid detergent. Areas shall be spray buffed with floor finish which is to be applied so no buildup occurs in non-traffic areas.

## 4.4.11	Internal Window Cleaning

Perform these tasks annually in May during normal working hours. Window surfaces identified as plastic shall be cleaned differently from glass to avoid scratching. Window sills, frames, and casings shall be protected from damage and free of spots, streaks, or runs.

## 4.4.12	Special Cleaning Areas

This includes polishing brass, cleaning windows, removing mud or water from the floors, polishing display cases, changing/cleaning linens, cleaning/sanitizing water closet, lavatory and table services in the following areas:

- Lobby

- Conference Rooms 1025, 2006, 2008, 3008

- Auditorium (Rooms 3012 to 3022 (even numbers)

- Center Directors Office Rooms 1032 to 1036 (even numbers)

- Area Directors Office Rooms 2032 to 2036(even numbers)

- First Aid Room (Room 1029)

## 4.4.13	Pilot Plant Cleaning

Basement: Floor sweeping at a minimum of once per week in the common area from elevator to double doors, corridor from double doors to roll up door, and egress areas into stair tower.

- First Floor: weekly corridor, lab and office cleaning.

- Second Floor: restrooms (2) cleaned daily, sweep and mop once a week in common area (red brick) from elevator to double door.

- Third Floor: sweep and mop once a week common area (red brick) from elevator to double doors.

- Trash shall be emptied 3X per week

## 4.4.14	Miscellaneous Responsibilities

Custodial duties may differ from those regularly scheduled. Such duties could include cleaning up storm damage, setting up the Lobby or conference rooms for special functions and conference based on requesters instructions, and clean up before and after events and return room to its original configuration. When these situations occur, regular scheduled work will not be performed.

## 4.4.15	Cleaning Supplies and Materials Storage

Areas designated for storage of janitorial supplies and equipment shall be kept clean and odor free.

## 4.4.16	Equipment and Tool Standards

All equipment must be suitable to the surfaces to which applied. All cleaning products must meet the requirements established by Federal specifications. All materials used shall be "without ammonia" to avoid the release of fumes in or adjacent to any laboratory as this could affect research. Equipment and tools must meet the following standard requirements:

- Beater bar vacuums

- Bumpers and guards to prevent marking of surfaces

- Electrical equipment meet OSHA safety standards and be UL approved.

## 4.4.17	Government Furnished Equipment/Material is noted in Attachment IX.

Exhibit 4.4

| BiM - BiMonthly 6 - Months 2 - 2 × per week SP - Special 3 - 3 x per week Y - Yearly 4 - 4 × per week M - Monthly D - Daily W - Weekly R - When Requested | Trash | Vac./Clean Spots | Sweep | Wet Mop | Mats | Floor Refinish “B” | Floor Refinish “C” | Floor Refinish “D” | High Speed Buff | Dusting High | Dusting Low | Glass | Spot Clean | Water Fountains | Windows | Chalkboards | Whiteboards | Fixtures | Showers | Sinks | Brass | Clean Tables | Change Linens | Carpet Cleaning | Walls |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Janitorial Matrix |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Lobby | D | D | D | W | 3 | 6 | M | W | M | M | M | W | D |  | Y |  |  |  |  |  |  |  |  | Y |  |  |  |  |  |
| Wells Reading Room | D | D | D | W |  | 6 | M | W | M | M | M | W | D |  | Y |  |  |  |  |  |  | W |  | Y |  |  |  |  |  |
| Library | 3 | W |  |  |  |  |  |  |  | M | M | M | D |  | Y |  |  |  |  |  |  | W |  | Y |  |  |  |  |  |
| Center Director Suite | D | D |  |  |  |  |  |  |  | M | M | W | D |  | Y |  |  |  |  |  |  |  |  | Y |  |  |  |  |  |
| Area Director Suite | D | D |  |  |  |  |  |  |  | M | M | W | D |  | Y |  |  |  |  |  |  |  |  | Y |  |  |  |  |  |
| First Aid Room | D |  | D | D |  | 6 | M | W |  | M | M |  | D |  | Y |  |  | D |  | D |  |  | W |  |  |  |  |  |  |
| Conference Rooms | 3 | W |  |  |  |  |  |  |  | M | M |  | D |  | Y | W | W |  |  |  |  |  |  | Y |  |  |  |  |  |
| Auditorium | 3 | W |  |  |  |  |  |  |  | M | M |  | D |  | Y |  |  |  |  |  |  |  |  | Y |  |  |  |  |  |
| Entrance Ways | 3 |  | 3 | W | 3 | 6 | M | W | M | M | M | W | D |  | Y |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Cafeteria | D |  | D | W |  | 6 | M | W |  | M | M |  | D |  | Y |  |  |  |  |  |  | D |  |  |  |  |  |  |  |
| Smoking Room | D |  | W |  |  |  |  |  |  | M | M |  | W |  |  |  |  |  |  |  |  | D |  |  |  |  |  |  |  |
| Fitness Center | 3 | W | W | W | W |  |  |  |  | M | M | M | W | W | Y |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Hallways | 3 | W | 3 | W | 3 | 6 | M | W | M | M | M |  | D | 3 | Y |  |  |  |  |  | M |  |  | Y |  |  |  |  |  |
| Restrooms | 3 |  | D | 3 |  | 6 | M | W |  | M | M | W | D |  | Y |  |  | D | W | D |  |  |  |  |  |  |  |  |  |
| Men's Locker/Shower | 3 |  | D | W | W | 6 | M | W |  | M | M | M | D |  | Y |  |  |  | W | D |  |  |  |  |  |  |  |  |  |
| Women's Locker/Shower | 3 |  | D | W | W | 6 | M | W |  | M | M | W | D |  | Y |  |  | D | W | D |  |  |  |  |  |  |  |  |  |
| Laboratories | 3 |  | W | W |  | 6 | M | W |  | M | M |  | W |  | Y |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Stairwells |  |  | W | W |  | 6 | M | W |  | M | M |  | W |  | Y |  |  |  |  |  |  |  |  |  | Y |  |  |  |  |
| Elevators |  |  | W | W |  | 6 | M | W |  | M | M |  | W |  | Y |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Attic | M |  | M |  |  |  |  |  |  |  |  |  |  |  | Y |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Offices | 3 | W |  |  |  |  |  |  |  | M | M | M | W |  | Y |  |  |  |  |  |  |  |  | Y |  |  |  |  |  |
| Out Building Restrooms (except 2nd Fl. MSB) | W |  | W | W |  | 6 | M | W |  | M | M | W | W | W | Y |  |  | W |  | W |  |  |  |  |  |  |  |  |  |
| Loading Dock | W |  | W |  |  |  |  |  |  |  |  |  |  |  | Y |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| MSB Lab. Food Safety |  |  | BiM | BiM | W | R |  |  |  |  |  |  |  |  | Y |  |  |  |  |  |  |  |  | Y |  |  |  |  |  |
| Bio Waste Pickup | D |  |  |  |  |  |  |  |  |  |  |  |  |  | Y |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Pilot Plant (PP) Aisles |  |  | W | W | 3 |  |  |  |  |  |  |  |  |  | Y |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| PP Railings & Doors |  |  |  |  |  |  |  |  |  |  |  |  | 6 |  | Y |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 2nd Floor MSB Restrooms (Tuesday and Friday) | 2 |  | 2 | 2 |  | 6 | M | W |  |  |  | 2 | 2 |  |  |  |  | 2 | 2 | 2 |  |  |  |  |  |  |  |  |  |
| MSB Offices Food Safety | 2 | W |  |  |  |  |  |  |  | M | M | M | 2 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

# 5.0		Administrative Support Service Management

Responsible for the efficient operation of administrative services as defined in the specific requirements for word processing, photography, receptionist, mail services, duplication/facsimile requirements, chemical, office support storeroom, shipping, receiving, vehicle dispatching, maintenance, snack room vending machines, and miscellaneous support activities.

## 5.1	Word Processing

Typing support by providing standardization of formats for material, text editing, and efficient word processing services. Responsible for the setup, operations, and formatting of all word processing equipment to produce error free documents in accordance with the requirements set forth in ARS Directives 261.2 (ARS Correspondence Manual) and 431.3 (Position Classification - Research Position Evaluation System), and ARS and ERRC policies. Produce original documents from both draft or final form, as requested, from such material as handwritten and typewritten papers, a combination of handwritten/typewritten papers, floppy disks, CD’s, zip disks, and/or transmissions via E-mail. Documents shall be printed on various types of paper (i.e., letterhead, plain bond, colored bond paper, etc.) and forms (i.e., AD-838 -- USDA Purchase Order). Revise, correct, and update existing documents previously recorded on the word processing system. Produce documents in accordance with manuscript and scientific journal requirements and procedures and individual instructions given on the requestor’s work order request to indicate the proper journal, RPES Case Writeup, Book Chapters, CRIS Project Plan and CRIS Prospectus as well as special projects, i.e. Center Director’s UNJR. Scan approximately 125 reprints per year and convert to PDF files. Conferring and consulting with requestors whenever questions arise on special applications, requirements that are not clear, or requestors' instructions that do not comply with journals’ specifications or ARS Directives, etc. is required. Estimated number of documents edited, scanned, formatted, or typed per year is 450; estimated number of pages per year is 9,300.

## 5.1.1	Archives

Duplicate and retain an archival copy of all work produced. A system shall be maintained to catalog all archival material for future reference. No documents shall be deleted from the system without the approval of the author of the document.

## 5.1.2	Word Processing Scheduling

Backlog of work shall be monitored. Notify the ACO of the potential need for special effort when backlog is over 2 weeks aged. This notification is critical during the peak word processing season which occurs during the 3rd quarter of each year. The requestor shall mutually agree to changes to requested deliver date for completion when problems arise with work, such as the time the work was received, length of time needed to complete, and unusual or critical deadlines.

### 5.1.2.1	Turnaround timeframes for document completion.

Manuscripts:		1 to 5 pages – 1 - 2 work days

6 to 25 pages – 2 - 3 work days

26 pages and greater – 3 - 4 work days, unless otherwise agreed to by the requestor.

Revisions:		Minor Revisions -- 1-2 working day

Moderate Revisions -- 2-3 working days

Major Revisions -- 3-4 working days

Definition of Types of Revisions

Minor Revisions: simple revisions/changes; additions, deletions, transposition of characters, words, sentences, and/or paragraphs.

Moderate Revisions:  additions, deletions, extensive moving, repagination.

Major Revisions: Additional inputting/typing of new material or complex changes to the document, including multilevel equations and tables.

## 5.1.3	Editing

All documents shall be checked for completeness of all work and ensure that current copy is used for all revisions. All work shall be reviewed for conformance/compliance with required specifications, text content, spelling, punctuation, grammar, typographical errors, and general appearance, including layout of tables and equations. Proofreading and formatting turnaround time is 1 - 4 days.

## 5.1.4	Scanning

Documents (reprints, etc.) are submitted in printed or typewritten form. Document pages are scanned as images, modified by removing small sections and adding page numbers, and saved.  Images are pasted into MS Word and converted to PDF files with Adobe Acrobat.  Optical character recognition software is used to scan the page images to text files; these text files for reprints are not proofread or corrected.  There are approximately 125 reprints per year and scientific and administrative work on an as needed basis.  Scanning turnaround time is 2-4 days.

## 5.1.5	Reporting Requirements

Provide a written report log of all tasks performed on a weekly basis to the QAS. This report shall contain at a minimum the name of the requestor, type of document, date received, requested completion date, actual date completed, and number of pages typed. A consolidated or summary report of this data shall be contained in the Contractor's quarterly report.

## 5.1.6	Government Furnished Equipment/Material is noted in Attachment IX.

# 5.2	Photography Services

Scientific experimental results are to be translated into accurate photographic records using various types of cameras, film, digital disks, lighting, and darkroom equipment; selection of proper materials needed to complete the job; and produce clear and legible slides, gels, glossy and digitized computer prints and digitized images for Web pages. Work must be completed within 10 work days from date of receipt and 3 work days before the date required for meetings and/or publication. No slippage of completion dates will be acceptable, unless approved by the requestor and the ACO. Coordinate all photography tasks to produce effective results. Coordinate with Center’s graphic office to meet scheduled completion dates on joint projects. Produce and submit a weekly workload report to the QAS that identifies workload, priorities, and scheduled start and completion dates for all work.

## 5.2.1	Research Photography

Provide photographic services to record research work performed by scientific, engineering, and support personnel at the Center. Items may be perishable in nature and require a short response time. This work may be accomplished in the photography laboratory or on location, and may be used as prints for publications, slides, overheads for presentations, and/or enlargements for poster sessions. These photographs may be black and white or color taken by conventional, instant and/or digital photographic equipment as appropriate. A photographic record of some research work will necessitate a short turnaround time particularly those experiments that are classified as perishable. Requesters will provide advance notification when perishable items will be available for photographing so services can be conducted before the research material is spoiled. An estimated 3,500 photographs are taken annually.

## 5.2.2	Slides

Slides created in black and white or color shall be of appropriate contrast for presentation in large auditoriums. The original of these slides could be camera ready figures, tables, journals, and previously recorded research photographs. Layout, format, and color utilized in the development shall be coordinated with the requester. An estimated 2,100 slides are created annually.

## 5.2.3	Publicity Photographs

Provide photographic services to cover and record award ceremonies, guest speakers, portraits, research seminars and activities by digital slide, photos, and/or video tapes. Advance notification by ERRC or NAA personnel will be given so as not to adversely effect routine services.

## 5.2.4	Employment Identification and Passport Photographs

Photographic services are required for identification badges of all new employees of the Center, NAA Administrative Office, and designated Center and/or NAA contractors, photos for replacement identification badges and passport photos. ID badges will be processed for contractors using the Avery Identification System. Photography sessions for identification badges shall be coordinated with the ERRC/NAA Personnel Office so it can be scheduled for the day new employees report to work. NAA Engineering Office will assign construction contractors designated to have photo identification badges prior to project work commencement. Finger print impressions of new Federal employees are to be taken concurrently with the identification photos. Requests for passport photos shall be given priority to complete due to the potential impact on a scientist's travel/research schedule. Issuing passports is not a daily requirement.

## 5.2.5	Processing

Estimated annual negatives/prints processed is 300 each. Black and white processing is done on site using Government-furnished darkroom facilities and equipment. Color processing is done off site by a commercial firm as color processing equipment is not available from/at ERRC.

## 5.2.6	Prints

Provide photographic services for glossy prints. This may include publication requirements in a variety of sizes and layouts. Sometimes special size reductions (2" × 2") and enlargements (20" × 20") are necessary due to specific journal requirements. Enlargements are also to be supplied for poster sessions and exhibits. Film positives are to be prepared for 35mm slides and overhead projection.

## 5.2.7	Digitized Camera Photography

Furnish digital prints produced from Government furnished hardware and software to digitally enhance photographs. Maintain all digitized photographs on disk, and record and update a recorded index inventory taken of all digitized prints quarterly. An estimated 3,500 digitized photographs are processed annually.

## 5.2.8	Photographic Equipment

Maintain a system for control of portable photographic equipment that Center personnel may use on a temporary loan. The log shall contain the name of the requestor, unit the equipment is signed out to, the date the equipment was lent out and returned, serial number of each piece of equipment, and condition of equipment upon return. Immediately notify the ACO if equipment is damaged.

## 5.2.9	Photographic Consultation Services

### 5.2.9.1	Photographic consultations. Consult with scientists who record routine data by their own photographic systems and identify optimizing conditions necessary for filming data.

### 5.2.9.2	Design and layout consultations. Prepare more useful and understandable photographic layouts to optimize output for the Center's scientific, engineering, and support personnel.

### 5.2.9.3	Design and preparations guidance. Recommend the design and preparation of data for use in publications, presentations, posters, patents, displays, and exhibits, as requested.

### 5.2.9.4	Display material. Recommend the selection of visual materials and the preparation of sketches and selected photographs for effective use as exhibits, displays, and brochures with emphasis on layout, artwork, lettering, and mounting, as requested.

### 5.2.9.5	Poster presentation. Recommend the layout, lettering, sizing, and mounting of figures, text, and photographs enlarged for use in technical poster presentation. Legibility, neatness, color selection, and visual effectiveness are critical. Posters of annual Center events are maintained in the lobby and updated monthly. Approximately 50 requests for photography mounted are initiated annually.

## 5.2.10	Text Preparation

### 5.2.10.1	Specialized typing. Provide specialized typing for technical presentations for photos, slides, glossies, etc. produced in house. This includes, but is not limited to, sequences, flowcharts, chemical formulas and structures, extensive tabular material, often including a combination of several types of materials on one typed sheet, extensive use of Greek and mathematical symbols or super and subscript numbers and letters. Work is done from either rough draft or handwritten copy. Adherence to size specifications is critical.

### 5.2.10.2	Slide material preparation. Provide slide material copy for slides produced in house. Material must be composed and laid out for camera-ready reproduction with emphasis on style and size of lettering, technical proportion, accuracy, legibility, and completeness. Use of Greek and mathematical symbols may be also included in preparation. Capability of variable vertical and horizontal line spacing is critical to the nature of this work.

### 5.2.10.3	Photographic support functions. Provide typing or related services/method to be done as support for photographic function to include large letter size typing capability for displays, label signs, name tags, etc. Typing of narratives for flyers, brochures, reports, memos, and overhead transparencies will be required using above methods with Government-furnished equipment.

## 5.2.11	Photographic File

Maintain a system to catalogue all new material for future reference. This file shall include, but not be limited to, prints, negatives, digitized enhancements, slides, equipment instructions, and log books cross-referencing photographic materials. All existing files and catalogues are to be maintained.

## 5.2.12	Government Furnished Equipment. Appendix VIII.

# 5.3	Reception and Switchboard Services

Maintain reception and telephone switchboard services at the Lobby entrance area between the hours of 7:30 a.m. and 4 p.m., Monday through Friday, except Federal holidays and any other day designated by Federal statute, Executive Order, Presidential Proclamation, or early dismissal by the Office of Personnel Management or the ERRC Center Director. Personnel performing this function shall be able to read, write, speak, and understand the English language so to greet and assist the general public in a courteous and pleasant manner, and maintain poise and self-control under normal and occasionally stressful situations.

## 5.3.1	Reception Services

Operate and enforce a system of personnel identification and control by staffing the station at the main entrance lobby area. Greet all visitors and contact the proper party to meet the visitor(s). Require each visitor to register information into the Avery Identification System and issue a photo identification badge to all visitors, provide instructions on the display of the visitor's badge, verify visitors are met by their party before passing through the interior lobby doors. When directed by the ACO, briefcases, boxes, shopping bags, etc. may be inspected before removed from or taken into the ERRC facility. Verify persons removing Government property/equipment from the facility are in receipt of a properly signed property pass. Be familiar with laboratory scheduled activities, such as scheduled training courses, special meetings, conferences, etc., to inform persons with inquiries regarding same as to scheduled times, dates, etc. The Contractor will be notified by the various designated ERRC and/or NAA officials of these activities, as well as scheduled visits of persons from industry, other Federal agencies, State, and local governments. Services are required to cover after-hour conferences, meetings, etc.

### 5.3.1.1	Secured access. Unauthorized/unescorted personnel shall not be allowed access to the building. Alert the appropriate Government officials as noted in the Facility Self Protection Plan in the event of situations or occurrences, such as internal disorder, attempts to commit espionage, sabotage, or other criminal acts adversely affecting the security and/or safety of the Government and Contractor employees, property, and the general public lawfully in the building or on the grounds. Insure unauthorized persons are not permitted entry into building without proper clearance. Incidents of unauthorized entry should be reported immediately to the Project Manager.

### 5.3.1.2	Emergencies. Notify the Incident Response Team and/or appropriate agency, such as the fire, ambulance, and/or police department, as the situation may warrant as directed in the Facility Self Protection Plan. Immediately notify the ACO or other designated official in the event of an emergency or unusual occurrence adversely affecting the interest of the Government. Be familiar with all areas of the building and surrounding grounds to assure quick response to emergency calls.

## 5.3.2	Telephone Switchboard Services

The Government furnished equipment for performance of this service is a PC-driven, electronic switchboard manufactured by Mitel. Answer all incoming calls within 10 (ten) seconds of ringing and connect the caller with the requested party. Notify the caller if party is unavailable. Be familiar with laboratory programs and personnel to answer telephone inquiries from the general public and to offer assistance to persons requiring or requesting information. Receive, secure, and turn over to appropriate persons, official mail, messages, and/or telegrams received. Receive, log, and make telephone calls in connection with the duties and responsibilities of the assignment. Arrange for overseas calls and/or conference calls as required.

## 5.3.3	Express Mail

Prepare express mail shipment documents and small packages using vendor furnished hardware and software to prepare package labeling, and for tracking shipment costs and delivery status.

## 5.3.4	Lost and Found

Notify of lost items founds via the Center’s E-mail system. Secure articles until they can be turned over to the proper owner.

5.3.5	Type Government purchase orders using Government furnished hardware and software in accordance with established Government procedures and time frames. Approximately 180 purchase orders are prepared annually.

## 5.3.6	Required Instruction and Training

Training shall include: orientation on ERRC's research programs, its organization and tenants; employee and public relations with general orientation on professional dress code, conduct, and attitude on and toward the job; authority of the individual performing security services and functions at the Lobby location such as building entry and exit policies; and operation of the switchboard and other equipment located at the station.

## 5.3.7	Government furnished equipment is noted in Appendix VIII.

# 5.4	Mail Services

The contractor shall provide mail services for ERRC and the North Atlantic Area Administrative Offices located at ERRC include receiving and sorting mail delivered from the U.S. Post Office at Philadelphia (Market East Station) PA each day. Two pickups and two deliveries of mail to the Center Director's office, NAA Administrative Offices and the Research Leaders' suites in the Administration Wing shall be performed daily. Coordinate with the U. S. Post Office for pickup and delivery of mail, once in the morning and once in the afternoon. Mail for personnel whose offices are not in the Administration Wing shall be sorted and posted in the mail room. Center and Area organizational structures are given in Paragraph 5.4 so mail is routed effectively. Maintained and update this information to show individual changes such as  new employees and relocation of employees.

## 5.4.1	Mail Classification and Handling

Typical mail includes, but is not limited to, internal agency mail and distribution, postal service first-class, priority, second-class, third-class, fourth-class (includes library or book rates), nonprofit, and bulk.

- Outgoing. The Contractor shall sort mail into proper classes, weighing, and applying appropriate metered mail postage according to postal procedures and regulations. Put in proper sacks. Wrap and box documents and mail as needed. Tag mail sacks per postal regulations. Maintain an inventory of special handling postal mailing containers and labels. An estimated 9,500 pieces of mail are metered and mailed.

- Incoming package sort. The Contractor shall mark packages, boxes, and oversized items for individuals by building and room numbers. Mail addressed only to the Center or Area without a sufficient address to determine proper delivery shall be forwarded unopened to the ACO for redirection.

- Over Night Mail/Packages. The Contractor shall immediately notify the addressee by telephone when a package or letter is received from Federal Express, DHL, or other overnight carrier. If the addressee is not available, the addressee's Research Leader's secretary or Area Administrative Office Section Head shall be notified. If the addressee does not pick up the package within 2 hours of notification, the Contractor shall deliver it to the addressee. No package shall remain undelivered for more than 2 hours.

## 5.4.2	Handling of Special USPS Mail

The Contractor shall maintain a daily log of incoming registered, certified, insured, express, and special delivery mail. Obtain the appropriate signatures for postal receipts. Prepare outgoing registered, certified, express, customs documents following proper postal regulations and forms. A daily log of outgoing registered, certified, insured, express, and special delivery mail shall be maintained.

## 5.4.3	Metered Mail Procedures

Approximate yearly postage is $7,000. Quarterly, the Contractor shall set meters which are done at the time of postage purchase at the USPS Glenside Office. The postage meter shall be kept locked when not in use and the key maintained in a locked/secure place. Spoiled meter stamps and tapes should be used on other large mailings. If necessary, a second meter tape can be printed to total the required postage. Spoiled postage must be used on the date shown on the meter stamp. Appropriate care should be taken when metering and the USPS does not issue credits for spoiled tapes.

## 5.4.4	Express Mail

All Express Mail sent by the Post Office shall be metered and the "customer" copy of USPS Form shall be maintained in a file, unless otherwise requested by the sender.

## 5.4.5	Preparation of Mail for Courier Service

Approximate yearly postage is $30,000. The Contractor shall prepare the appropriate forms/air bills for overnight delivery of packages. The GSA schedule source contract will be used for delivery requiring overnight service from ERRC and the NAA. Other overnight services not on GSA schedule, such as USPS, Purolator, DHL, etc., may be used only in an emergency. Forms/Air bills will be prepared with address, date, description of contents, and accounting code of the sender.

## 5.4.6	Reporting

The Contractor shall track the number of items mailed and all mail costs incurred by: ERRC, Office of the Area Director [NAA], and NAA Area Administrative Offices. Costs and pieces of mail for each entity shall be tallied at the end of each month and the results/totals included in the Contractor's quarterly report.

## 5.4.7	Government Furnished Property/Material

The Government shall furnish, without cost to the Contractor, the following property and services:

- Space now located in Room 0209 and equipment and supplies associated with the mail function. Space is subject to change at the convenience of the Government.

- Postage, purchased from the U.S. Postal Service, used in applying metered postage to official mail.

- Pitney Bowes Postage Machine

- Government-owned vehicle will be used when the pick up and delivery of mail to and from the U.S. Post office is required.

# 5.5	Duplicating/Facsimile Services

Services are required during normal work hours, Monday through Friday, from 7:30 a.m. to 4:00 p.m., except Federal holidays and any other day designated by Federal statute, Executive Order, Presidential Proclamation, or early dismissal by the Office of Personnel Management or the ERRC Center Director.

## 5.5.1.	Duplicating

Services include collate, staple, and bind work as requested in the number of copies as specified by the requestor. To gather historical data a work request form will be developed for requesters to receive these services. This form must include at a minimum the requestor's name, date work was received, date work was completed, number of document pages, number of copies requested/made, type of document, and any special requirements (i.e., stapled, binding, single or double-sided, hole-punched paper, etc.). Duplicating work shall be returned, with the original document, to the requestor within 2 work days after receipt of a work request, unless otherwise stated by the requestor. The exception to this is a voluminous job which must be done manually. The requestor shall be notified of the additional time needed. Approximately 300,000 pages are copied annually.

The ERRC and NAA personnel perform approximately 75% of their own duplicating except for complex, bulk copy work as noted below.

- Jobs with more than 10 originals or jobs needing 5 or more sets.

- Complex jobs involving more than five back-to-back originals requiring make-ready copies.

- Jobs of more than five originals in which some are of different sizes.

- Jobs that require the insertion of separation sheets (such as section guides).

- Binding jobs of more than one copy.

- Manual collating jobs of material of different sizes.

Samples of jobs to be performed include, but are not limited to:

- Contract solicitations (20 to 40 per year; 50 copies; 50 to 70 pages, single-sided)

- Contracts (20 to 40 per year; 10 copies; 40 to 50 pages, single-sided)

- Notices to all employees with several attachments

- Facilities Self-Protection Plan

- Manuals

- Specifications

- ERRC Telephone Directory

## 5.5.2	Setup and Maintenance of Duplicating Equipment

Setup, operate, and perform operator level maintenance of all Government-owned and -leased duplicating equipment. The duplicating equipment currently onsite consists of various models and types, such as Xerox, Konica, Canon, Sharp, and Panasonic. See Exhibit 5.5.2 for current list of owned and leased equipment and its location. Trained operators will function as key personnel for correcting malfunctions and perform routine maintenance (i.e., correct paper jams, install toner and developer, etc.).

## 5.5.3	Supplies and Materials

Supplies include dry ink, toner, developer, paper (white and colored), heavy cover paper, transparencies, labels, and binding material, etc. Maintain adequate supplies and materials for the main duplicating equipment and the stations located throughout the Center. Stations throughout the Center shall be checked daily and restocked to maintain an adequate supply of copy paper. A log shall be kept to record usage.

## 5.5.4	Facsimile Operations

Responsible for the use, maintenance, and ordering of supplies for the facsimile equipment  identified in Exhibit 5.5.4. For the machine in room 0209 a log of all incoming and outgoing messages shall be maintained. All incoming messages shall be delivered to the addressee or contact person within 1 hour of receipt and place facsimile in receivers’ mailbox. An estimated 825 incoming messages are received. All outgoing messages shall be processed within 1 hour of receipt. If unable to process the message within 1 hour, the operator shall notify the requestor of the delay or problem and request further instructions. All outgoing messages must be confirmed by calling the confirmation number. Facsimile original messages shall be noted that they have been sent, the time sent, the operator's initials, and the name of the person who confirmed receipt. This shall be returned to the sender. Approximately 300 messages are sent annually.

### 5.5.4.1	Facsimile maintenance. Provide the maintenance and supplies for the facsimile equipment listed in Exhibit 5.5.4. Trained operators will act as the personnel for correcting malfunctions, perform routine maintenance (i.e., correct paper jams, install toner and developer, etc.), and maintain an appropriate amount of supplies at all facsimile stations. Perform adjustments and minor repairs to all facsimile equipment.

## 5.5.4.2.	Government furnished equipment is noted in Appendix VIII.

Exhibit 5.5.2

COPIER INVENTORY

| Company | Qty. | Model No. |  | Serial No. |  | Location |
| --- | --- | --- | --- | --- | --- | --- |
| Mita |  |  |  |  |  |  |
|  | 1 | KM5035 |  |  |  | 0209 |
| Canon |  |  |  |  |  |  |
|  | 1 | NP3050 |  | NBX19149/ID #76257 |  | Library |
|  | 1 | NP3050 |  | NBZ37908/ID #ZV273 |  | 2 FL/FT |
|  | 1 | NP4050 |  | NAG13646/ID #P5387 |  | 3032 Tomasula |
|  | 1 | IR330S |  | NNY13550/7C857 |  | 1032 Dr. Cherry |
|  | 1 | GP30F |  | NHX03311 |  | Library (Wells) |
|  | 1 | 3300G |  | MPD00195/ID #9K195 |  | 2032 Martinez |
|  | 1 | 3300G |  | MPD00205/ID #9K112 |  | 2028 Madden |
|  | 1 | C330S |  | NQJ35179/ID #8F463 |  | 2004 McCullom |
|  | 1 | PC1080F |  | ZTR28531 |  | MSB Cube |
|  | 1 | PC745 |  | ZTC15531 |  | 1116 |
|  | 1 | D860 |  | 2TF46173 |  | 1022 |
|  |  | 3 Year Warranty on the D860 |  |  |  |  |
|  | 1 | PC795 |  | ZTF46177 |  | Boiler |
|  | 1 | PC795 |  | ZTF56142 |  | 2FL/PP |
|  | 1 | PC795 |  | ZTF50293 |  | 0101/ Computer Room |
|  | 1 | PC795 |  | ZTF54920 |  | 3209 N. Parris |
|  | 1 | PC980 |  | TVH13883 |  | 0105 (Shipping) |
|  | 1 | D660 |  | ZTS04606 |  | 3rd FL/FT |
|  | 1 | D660 |  | ZTS15337 |  | 0008 |
|  |  | 3 Year Warranty on the D660 |  |  |  |  |
| Konica |  |  |  |  |  |  |
|  | 1 | 3135 |  | 25KE11285 |  | 1st FL/FT |
|  | 1 | 2223 |  | 35EW02256 |  | 2012 J. Rogers |
|  | 1 |  | 3135 | 25KE12687 | 2023 Helen |  |
|  | 1 |  | 2223 | 35EW02449 | 2024 Eileen |  |
|  | 1 |  | 2028 | 576216782/(ID #50405) | 2018 John Kelly |  |
| Sharp |  |  |  |  |  |  |
|  | 1 |  | SF2025 | 76605469/(ID #8469) | 2116 Bhaduri |  |
|  | 1 |  | D1866 | 96600948/ID #1866 | 3002 Hicks |  |
|  | 1 |  | AL1451 | 16737859 | MSB Boyd |  |
|  | 1 |  | AL1551 | 35025607 | 1214 Onwulata |  |
| Panasonic | 10/03 (Warranty) |  |  |  |  |  |
|  | 1 |  | DP6010 | GCG2KNOO151/ID #B5431 | 1026 S. I. Tu |  |

Exhibit 5.5.4

FACSIMILE EQUIPMENT

| Room | Model |
| --- | --- |
| 1032 | Panafax UF-8000 |
| 1026 | Panafax DX-2000 |
| 3004 | Canon CFX-L4000 |
| 0008 | HP 1230 |
| 2023 | Panafax UF-885 |
| 2004 | Panafax UF-595 |
| LRB | Panasonic UF-790 |
| 3032 | Panasonic UF-790 |
| 3036 | Panafax UF-790 |
| 3002 | Canon CFX-L4000 |
| 2029 | Panafax UF-885 |
| 1015 | Panafax UF-790 |
| 2012 | Panafax UF-790 |
| 0209 | Brother 4750-E |

# 5.6		Chemical and Stationery Storerooms

Provide for the operation of the Chemical and Stationery storerooms. Maintain an inventory of all supplies, chemicals, gas cylinders and tanks, and comply with all Federal, state, and local laws and regulations. The storage and distribution activities include: receiving, checking, storing, shelving, physical inventories, and related activities. These functions shall operate from 7:30 a.m. to 4:00 and issue supplies on a first in/first out request basis. Frequency of issue and end users shall be monitored on all stock using a bar code type computerized system to be furnished by the government. On an average, approximately 340 items are dispersed monthly.

## 5.6.1	Stationery Storeroom

Stock and maintain the ERRC Stationery Storeroom which includes the purchase of supplies (i.e., pencils, paper [letter head, lined and unlined tablets, colored, and plain]), laser printer toner cartridges, storage disks (CD’s, zip disks, etc.), envelopes, binders, laboratory notebooks, and all other stationery supplies needed by the ERRC and the NAA Administrative Office. Supplies to be ordered through the U.S. Government Printing Office schedules and General Service Administration (GSA)/Federal Supply Schedule (FSS) will be forwarded to the Center LAO office for procurement. Records of orders and receipts shall be maintained onsite for appropriate review by Government personnel. The supplies shall be stocked on shelves that are clearly labeled.

### 5.6.1.1	Stationery storeroom inventory. Develop and maintain a current inventory list using the inventory module of the Government-furnished automatic work order system (Maximo) or equal or a bar code type system presently located in the Storeroom area. The inventory system shall include information on inventory, material to be ordered, material on order and awaiting delivery, and delivered material not yet on inventory. There are approximately 173 items stocked in the Stationery Storeroom.

### 5.6.1.2	Stationery storeroom catalog. Publish a catalog of stationery storeroom items for distribution to all personnel within 60 days after contract award. The catalog shall be updated annually by March 1 and shall include, but not be limited to, the following information: supply category, item number, item description, and unit of issue. The QAS and storeroom supervisor shall recommend to the ACO additional items that had not been previously stocked and deletion of any current items.

## 5.6.2	Chemical Storeroom

Maintain and replenish ERRC's Chemical Storeroom. There are approximately 301 items stocked. Such items and materials include hazardous chemicals, solvents, and reagents. Authorization will be given to order supplies through the use of available General Service Administration (GSA)/Federal Supply Schedule (FSS) contracts. Supplies to be ordered through the U.S. Government Printing Office schedules and General Service Administration (GSA)/Federal Supply Schedule (FSS) will be forwarded to the Center LAO office for procurement. Records of orders and receipts shall be maintained onsite for appropriate review by Government personnel. The storage and distribution activities include receiving, checking, storing, surveillance, physical inventories, and related activities. Ensure all chemicals coming into the Center have MSDS sheets, a copy is given to the user, and a copy is maintained in the Centers Safety Office. Requests for supplies shall be processed on a first in/first out basis.

### 5.6.2.1	Chemical storeroom inventory. Develop and maintain a current inventory list using the inventory module in the Government-furnished automatic work order system (Maximo) or equal or a bar code type system presently located in Storeroom area. Inventory system shall include information on inventory, material to be ordered, material on order and awaiting delivery, and delivered material not yet on inventory. Implement procedures for controlling the inventory so that items are withdrawn through established procedures.

### 5.6.2.2	Chemical storeroom catalog. Publish a catalog of chemicals available for distribution to ERRC personnel within 60 days after contract award. The catalog shall be updated annually and shall include, but not be limited to, the following information: supply category, item number, item description, and unit of issue. The ERRC Chemical Storeroom Committee shall recommend additional items that had not been previously stocked and deletion of current items. After the Committee's approval, the items shall be stocked or deleted and the inventory and catalog listing shall be updated.

### 5.6.2.3	Solvent storage locker. Solvent Storage Locker shall be used for long term storage. The locker shall be kept in a neat and orderly manner and in compliance with all Federal, state, and local laws and regulations. All shelves shall be properly labeled and solvents stored on designated shelves. Disposal of empty drums shall be made in accordance with all Federal, state, and local laws and regulations.

## 5.6.3	Dry Ice

Dry ice shall be available at all times for laboratory use. Ordered from the federal supply schedule, receive and store dry ice in the appropriate container(s) in a designated area outside of the storeroom. The Center receives, on average, one delivery of approximately 1,000 pounds per week.

## 5.6.4	Compressed Gases

Procure compressed gases, specialty and non-specialty through the federal supply schedule. Order, receive, store, issue, and deliver gas cylinders in accordance with all Federal, state, and local laws and regulations. Approximately 10-12 gas cylinders are used per week. Services required for compressed gases include, but are not limited to, the following:

- Ordering, receiving, and storing compressed gas cylinders

- Retrieving empty cylinders for refilling

- Inspecting cylinders for leaks and malfunctions

- Repairing fittings, valves, hoses, and gauges

- Procuring new or replacement fittings, valves, hoses, and gauges

- Advising and consulting ERRC staff on proper handling of compressed gases

- Returning cylinders and tanks to the company

- Maintaining an inventory of all cylinders and tanks onsite

- Monitoring and recording any and all demurrage charges

- Ensuring that the cylinders display evidence of having been properly hydrostatically tested

- Refusing to accept cylinders without evidence of hydrostatic testing and caps

## 5.6.5	Cryogenic Liquids

Procure cryogenic liquids from a federal supply schedule source except liquid nitrogen, an open market commodity. Order, receive, and deliver containers of cryogenic liquids, such as liquid helium, liquid nitrogen, argon, etc., in accordance with Federal, state, and local laws and regulations. Monitor the supply of such materials and reorder/refill as required. The Center, through the GSA contract, rents a 6,000 gallon tank for liquid nitrogen which is refilled at least once per week on an average with approximately 2,500 gallons.

## 5.6.6	Documentation and Records

Maintain records of all transactions on compressed gas cylinders and cryogenic liquids delivered and received at the Center. Such documentation shall contain, at a minimum, the following information:

- Inspection dates of cylinders and tanks

- Maintenance performed

- Hydrostatic test results

- Date of refill

- Type of material received

- Date received from company and date issued to scientist

- Location of cylinder or tank

- Date returned from scientist and returned to company

# 5.7	Shipping and Receiving Operations

Provide services for the shipping and receiving materials, supplies, and equipment for ERRC. Activities associated with this function include, but are not limited to the following:

- Selecting containers appropriate for the material

- Packing, marking, and labeling packages in accordance with transporters' requirements

- Weighing prepared shipments and completing weigh bills

- Issuing bills of lading

- Delivery of shipments to depot, UPS, etc., as necessary

## 5.7.1	Receiving Operations

Approximately 6,400 freight items are received annually. Copies of all Government purchase orders and credit card purchase logs are furnished to identify materials to be received. Each shipment shall be verified within 2 hours of receipt against the appropriate order documentation to verify quantity, accuracy of shipment, etc. If the shipment is accurate, the recipient is to be notified to pick up the received materials within 1 working day of receipt of routine items. Items marked perishable, refrigerate, or requiring other special handling conditions shall be placed in the hands of recipients within 1 hour of receipt. The recipient shall sign the green copy of the purchase order for the shipment. If unable to contact the recipient of such critical items, the items are to be placed in the appropriate refrigerator, freezer, etc., and contact the recipient's Research Leader for guidance. Approximately 390 items are received annually that require refrigeration.

Materials and/or supplies that weigh up to an estimated 20 pounds to be received by ERRC employees shall be placed on the shelves. The green copy of purchase order shall be placed on the package for signature. MSDS sheets are to be attached to packages of chemicals that ERRC personnel ordered through the Government (A copy of the MSDS sheet shall be filed with the Center Safety Office). The green copies of the Government purchase orders are to be forwarded to the USDA, National Finance Center on a daily basis. If the green copy does not require a signature (order was less than $1,000), return the unsigned copy to the Center’s Location Administrative Officer. Material estimated to be 20 pounds or over shall be delivered to the appropriate office or laboratory.

## 5.7.2	Shipping Operations

Responsible for shipping/transporting packages from ERRC to appropriate destination in accordance with transporter's, state(s), and U.S. Department of Transportation's regulations. Approximately 230 items are shipped annually. Select and prepare appropriate containers, pack, mark, and label all items to be shipped. An adequate inventory of supplies to perform this service shall be maintained. Ship all items within 2 working days of receipt, except perishable items which are to be shipped the same day received. Biological materials are to be secured until pickup by an express courier. The Center averages approximately 10 outgoing shipments per week. Postage for shipped items averages approximately $6,000.00 per year.

## 5.7.3	Forklift/Equipment Operation and Maintenance

Government-furnished forklift and other equipment such as hand trucks, pallet trucks, etc. will be provided to perform these duties. Only authorized and designated employees properly trained will be permitted to operate forklift equipment. The forklift shall be used to load and unload and move heavy equipment and supplies only. Operators shall also be trained in the use of power winches, hoists, cranes, positioning of loads, fastening chains and ropes in the performance of loading, unloading, and setting up of equipment, without damaging equipment or property.

## 5.7.4	Warranty Tracking System

Establish a computerized system (i.e. bar code) to track all equipment and software under warranty acquired for maintenance services, research, or administration. The process shall include but not limited to warranty registration, equipment tagging, and email notification one month prior to warranty expiration.

## 5.7.5	Government furnished equipment is noted in Appendix VIII.

# 5.8	Vehicle Dispatch and Scheduling

Responsible for scheduling, dispatching and maintaining Government-owned and leased vehicles during regular working hours, Monday through Friday, from 7:00 a.m. to 4:30 p.m. The vehicles used by the Center and the NAA Administrative Office are listed in Exhibit 5.8. Vehicles shall be scheduled for individuals or groups on official Government business. NOTE: Operators shall have a valid state driver's license. Prior to giving out the vehicle keys, verify if personnel possess a current valid state driver's license to operate a Government motor vehicle. Vehicle keys, U.S. Government motor vehicle credit card, and dispatch ticket shall be given to the requestor at the time the vehicle is picked up. Requests for vehicle scheduling will be received from the RL secretary by telephone or other authorized Government personnel. The availability and scheduling logs of each vehicle shall be maintained on a daily basis and a copy of this log shall be kept and made available for review upon request. Maintain vehicle keys and credit cards in a secured location when not in use. Vehicles shall be locked when not in use and kept clean and well maintained for safety purposes. All Government vehicles shall be parked in the court yard to the extent that there are adequate spaces available. Drivers will be required to return cars to the court yard. If there are no spaces available, they will be parked in Parking Lot #1. Approximately 360 requests are received annually for vehicle dispatching.

## 5.8.1	Vehicle Maintenance

Perform routine vehicle maintenance for all Government-furnished vehicles prior to dispatching and inspect vehicles weekly to assure maintenance is completed. Maintain a log to record and track maintenance which includes, but is not limited to:

- Ensuring the fuel tank is at least 3/4 full before assigning the vehicle to another operator

- Checking and adding fluids (gas; oil; water; windshield washer, transmission, brake, and power steering fluids; etc.)

- Maintaining proper tire pressure and inspecting for tire tread condition and wear

- Cleaning the inside and outside of all Government-furnished vehicles. This includes, but is not limited to, washing the exterior (including wheel covers), cleaning and vacuuming the interior (dashboard, consoles, carpeting/mats, ashtrays, windshields, windows, etc.), ensuring that spills, stains, dirt, trash, papers, debris, etc., are removed, inspecting for potential problems/defects, charging batteries and maintaining safety/emergency equipment and supplies kit in each vehicle.

- Schedule all maintenance to be performed as recommended by the manufacture and to keep the warranty in effect.

## 5.8.2	State Regulated Safety Compliance and Emission Inspections

Pennsylvania Department of Transportation, Bureau of Motor Vehicles, requires all motor vehicles be inspected for safety compliance and emissions on an annual basis. Fines and/or any associated costs that are assessed by any police department due to failure or negligence to comply with the annual Pennsylvania-required inspections shall be borne by the Contractor. These inspections shall be performed by certified/authorized Pennsylvania state inspection stations. Vehicles which do not pass inspection shall be removed from service and all deficiencies corrected. Upon passing inspection, the vehicles shall clearly and properly display all decals, stickers, tags, etc., in accordance with Federal and state laws.

## 5.8.3	Repair and Overhaul of Vehicles and Equipment

Make arrangements for repairs when notified on the following workday. Repairs shall include, but not be limited to:

- Repairing brakes and brake systems

- Adjusting and repairing the steering system

- Repairing the transmission system

- Performing tune-ups

- Repairing/replacing the air conditioning and heating systems

- Repairing/replacing the suspension system

- Repairing/replacing the exhaust system

- Repairing/replacing tires

- Winterizing the vehicles

- Repairing/replacing the engine cooling system

- Performing miscellaneous repairs on lights, doors, locks, batteries, etc.

- Performing minor body work

When the necessary repairs are corrected, return the vehicle to service within five (5) working days. Extensions of this service time shall be requested of and approved by the ACO. In the event the vehicle cannot be repaired, a written explanation of the problem and recommended solution is to be submitted to the ACO not later than the next work day. All repairs are to be performed by qualified automotive service centers/dealers/companies and in compliance with all Federal and state laws.

## 5.8.5	Placing Vehicles in and out of Service

Place new vehicles into service for the Center and the NAA Administrative Office as requested by the ACO or the Area Property Management Officer. Perform an inspection of all incoming vehicles and report deficiencies, damage, missing, or malfunctioning parts to the Area Property Management Officer. Vehicles passing inspection shall display all appropriate decals according to State laws.

Surplus vehicles shall be removed from service when requested by the ACO. Such vehicles shall be cleaned (interior and exterior), repaired, and inspected, removing all Government markings and decals. Tool bins, radios, and other Government-owned equipment shall also be removed and disposed of in accordance with the directions of the Area Property Management Officer. Surplus vehicles shall be delivered to the location specified by the Area Property Management Officer.

Exhibit 5.8

GOVERNMENT VEHICLES AT ERRC

| Year | Make | Model | Color | Tag Number |
| --- | --- | --- | --- | --- |
| 2005 | Dodge | Caravan | Blue | A319382 |
| 2002 | Dodge | Caravan | Silver | A311531 |
| 2002 | Dodge | Caravan | Gold | A311532 |
| 1999 | Dodge | Caravan | White | A311535 |
| 2000 | Ford | Taurus | Silver | A293035 |
| 2001 | Chrysler | Concorde | Silver | A293079 |
| 1995 | Chevrolet | Cheyenne | Red/gold | A264044 |

# 5.9	Snack Room Vending Machines Services and Maintenance

5.9.1	Vending machine equipment shall be installed and maintained as approved by the Area Property Management Office. Any additional and/or replacement of equipment will also be approved by the ACO and APMO before the installation.

5.9.2	Wholesome, fresh and clean quality products consisting primarily of sandwiches, soups, hot and cold drinks, snacks, fruits, and salads will be stocked and sold at prices comparable with products of similar quality attainable from other vending sources. Supplies that have exceeded their expiration date will be immediately replaced with fresh products.

5.9.3	Cost of installation, maintenance in good repair and condition, and removal or relocation of all equipment installed is the responsibility of the vending contractor.

5.9.4	Compliance with applicable state codes governing foods sales and services is required and documentation to show compliance is to be submitted to the ACO 30 days after contract award.

5.9.5	If the above conditions are not met, the ACO will provide notification in writing of the deficiencies. If deficiencies are not corrected within 3 working days after receipt of notification, action will be taken to remove such equipment and its stock from the site.

5.9.5	Government Furnished Equipment. Two bays of space with utilities will be provided for vending machines on the basement floor in the snack room area.

# 5.10	Miscellaneous Administrative Support

## 5.10.1	ERRC Telephone Directory

The contractor shall prepare and issue ERRC telephone directory two (2) times per year, not later than January 31 and July 31. This directory shall list, at a minimum, each employee by name and job title, their room number, telephone number, management unit and E-Mail address. It shall also indicate titles such as Dr., Mrs., Ms., Miss, or Mr. A classified section containing, at a minimum, the Area Director's office, Area Administrative Management offices, Laboratory offices, Facilities Contractor staff, etc., shall also be included. Emergency and first aid procedures shall be prominently listed. The directory shall be bound with a graphic scientific related cover approved by the ACO.

Approximately 300 copies shall be duplicated, distributed, and each employee shall receive one copy. The Contractor shall provide an addendum to the telephone directory two (2) times per year, not later than March 31 and September 30, listing the changes of personnel (addition, deletions) and any changes in room numbers, emergency procedures, etc. Information for changes shall be actively obtained by the Contractor via phone request or a written memo to Management Unit (MU) secretaries, the Safety Officer, Personnel, the AFGE Union, the Credit Union, etc.

## 5.10.2	Bell Telephone Directories

Bell Telephone directories shall be placed on the automatic order system for all NAA Administration and Center offices. Philadelphia White Pages directory, Philadelphia Consumer/Business Yellow Pages, and Montgomery County White/Yellow Pages directory shall be provided for each administrative office at the Center. This will require approximately 100 copies of each directory. These directories shall be distributed within 2 weeks of receipt.

## 5.10.3	Reprints

About 160 sets of reprints are received each year which are recorded, stamped with a number, and distributed to the applicable laboratory secretary. A record copy shall be placed in numerical sequence in the reprint file room and a file log is to be maintained to show document file number and title. Upon request, an average of 30 reprints per week, are mailed out to individual addresses. These requests (letters, post cards, or lists from the List of Publications and Patents) shall be logged in the same day as they are received, a copy forwarded to the senior author and responded to within 2 days of receipt of the request. A log of all reprints mailed shall be maintained which shows the date reprint was received, date sent, and the initials of the sender.

## 5.10.4	Conference Room Scheduling

The Contractor shall maintain a schedule of three conference rooms (Rooms 2006, 2008, and 3008) and the 3rd floor Auditorium (Rooms 3012 through 3022 [even-numbered rooms]). Furnish and test for good operation of requested equipment. Resolve any conflicts in schedules and those that cannot be resolved shall be referred to the ACO. Approximately 500 requests are received annually for conference room reservations and setups.

## 5.10.5	Distribution of Circulars, Directives, Memoranda

Distribute all circulars, directives, and memoranda received from USDA, ARS, and other Agency offices and from NAA and ERRC authorized personnel. The distribution shall be made in accordance with lists provided at contract award. The Contractor shall provide for updating these lists from information furnished from ACO. A file is to be maintained to include one copy of each item distributed, date of distribution, and the name of the distributor. Distribution of these documents shall be made within 2 working days of receipt.

## 5.10.6	Laboratory Notebooks

Laboratory research notebooks and accompanying material shall be packaged and shipped to the Federal Records Center (FRC) in Philadelphia, Pennsylvania in accordance with FRC guidelines. This material shall be stored in a secure location and shipped on a monthly basis or when 10 notebooks have accumulated. Stored research notebooks and/or materials from the FRC are to be retrieved within 5 working days after receiving a request from the Area Property Management Office.

## 6.0	Security Protection Services

Provide security protection services 24 hours per day 7 days a week including all Federal holidays and any other days designated by Federal statute, Executive Order, or Presidential Proclamation to protect the building structures, property in the buildings, its occupants, and visitors.

## 6.1.1	Entry Control System

Operate and enforce a personnel identification control entry system for persons to enter and exit at various locations at the site during Government duty and non-duty hours. Unauthorized persons shall be prohibited from entering the buildings. The opening of locked or entrance to a restricted area by unauthorized personnel is prohibited. Persons not escorted by a Center or Contractor employee shall be prohibited from entering the building at all times. When directed by the ACO, inspect packages and parcels being carried out of the building by employees and visitors when a problem is suspected; however, inspection of employees and visitors is not to be a frequent occurrence. After normal working hours, all persons entering the building must log in and out. Maintain log books in the Service Building and the Main Building at the rear entrance of the Chemical Wing. When filled, the log book shall be transferred to the ACO and a new book installed.

6.1.2	The facility is equipped with a Northern Computer WinPac 2.0 system. All Government and operations and maintenance contractor employees shall be issued access cards for entrances authorized. Approximately 200 card access cards are issued annually. Monitor all card reader equipment and repair malfunctions. Monitor access control printout and renew the printing tape. Report to the ACO any improper use or any alarm condition experienced with the access system. An access control print out report will be furnished to the ACO upon request. Outside contractor employees needing access are to be issued access cards so that they can perform their assigned work.

## 6.1.3 	Key Control

Maintain/support the key and key card systems for the facilities. Provide door keys for use during emergencies and/or power failures. Ensure all keys and key cards are controlled and accounted for and are not lost, misplaced, or used by unauthorized personnel. Lost keys and key cards shall be reported to the ACO within 1 day of discovery and no keys or key cards are to be duplicated and issued without the written approval of the ACO. Strict control of key blanks, cut keys, the computer system for key cards, inventory and register of all keys and key cards shall be maintained at all times. Keys and key cards issued for contractor employee inventories shall be submitted annually by October 31 to the QAS. Procedures for requesting and disbursing keys and key cards, changing locks, and systems maintenance, etc. shall be submitted as a Key Control Plan to the ACO for approval within 30 days after contract award and updated annually not later than May 31. Note: In the event a master key is lost, all locks and keys for that system shall be replaced by the Contractor. The cost for re-keying the system(s) shall be borne by the Contractor (no reimbursement by the Government) if such loss is due to negligence on the part of the Contractor.

## 6.1.4	Facility System(s) Monitoring

Monitor and maintain an equipment reading log for the fire, security and building systems monitoring equipment located in room 0019, the Service Building (Boiler House) and the front lobby reception area. Monitoring is also required for the:

- Air supply units

- Steam boiler systems

- Controlled temperature rooms

- Cold rooms and freezer rooms

- Fire alarm system

- Security alarm system

## 6.1.5	Research Equipment Monitoring

Monitor identified research equipment following the instructions of the requestor as required. Monitoring may involve recording and reporting data from meter or gauge readings or observing setups labeled "continuous operation" for obvious malfunctions. In the event of a malfunction, follow the instructions as provided by the researcher or indicated on forms attached to the equipment and report the malfunction to the requestor immediately. In the event of a safety hazard, take appropriate action and notify the on-call supervisor immediately and inform the ACO of malfunction(s) or safety hazards as soon as possible following the incident.

## 6.1.6	Patrols

Conduct patrols (rounds) to maintain surveillance of site conditions. Patrols shall include, but not be limited to, monitoring equipment, checking to ensure that doors and windows are closed and/or locked, turning lights off, monitoring fire alarm, closed circuit TV monitoring security system, security devices, and general condition of facilities. The daytime watchperson shall remain stationed in and around the Security Station with the exception of making two outside tours during the day. The afternoon watchperson shall remain in and around the Security Station until 6 PM to check badges and assist visitors and employees. After 6 PM, 3 inside and 3 outside tours must be completed. During the rounds, cold box readings will be recorded and exceptions reported. The nighttime watchperson shall remain in and around the Security Station after 6 AM to check badges and assist visitors. Beginning at the start of the shift and before 6 AM, 3 inside and 3 outside tours must be completed. During the rounds, cold box readings will be recorded and exceptions reported. Remaining in and around the Security Station at certain times is not a requirement on weekends and holidays for any shift. The watchperson will issue parking tickets to illegally parked vehicles during business hours. While making rounds, the guard key stations shall be used to assure all areas of the facilities have been secured. These stations are located throughout the entire premises of the ERRC and are annotated on the maps in Exhibit 6.1.6. Unusual conditions or incidents shall be reported to the immediate or on-call supervisor immediately and a written report is to be submitted to the ACO within 24 hours of the occurrence.

## 6.1.7	Emergencies

The risk of fire, explosion, or similar incidents shall be minimized and such potentially hazardous conditions that could result in such an incident shall be promptly reported to the Project Manager, Area Engineer, and the Center’s Safety & Health Manager. Monitor security and systems monitoring equipment that are located in room 0019, the Service Building (Boiler House) and the front lobby reception area. Investigation of malfunctions is the responsibility of the person on watch at the time of the malfunction. All malfunctions shall be reported to the immediate supervisor or on-call supervisor immediately and a written report shall be submitted to the ACO within 24 hours after the occurrence. If a spill or flood occurs in the building after normal working hours because of broken pipes or other difficulties encountered, the staff on duty will immediately notify the on-call supervisor and endeavor to clean the area of spill water and/or slippery floors. Floods shall be reported immediately to the on-call supervisor so corrective action can be taken. If an acid and/or caustic spill control occurs, apply control measures such as spill pads, dike snakes, etc. and notify supervisor. Call 911 if out of scope of control. Assist government personnel in containment and/or neutralization. The On-call supervisor shall be notified when icing conditions occur at night or over weekends so a remedial response can be put into affect to deice walks and parking areas. A written report summarizing emergency responses are to be submitted to the ACO within 24 hours of occurrence.

## 6.1.8	Security Personnel Qualifications

Staff shall be able to read, write, speak, and understand the English language; meet and deal with the general public; understand and apply various rules and regulations; and maintain poise and self-control under stress. Physical fitness, including vision and hearing, shall be evidenced by a report of medical examination which is certified by a licensed physician and submitted to the ACO prior to reporting for duty. Newly hired personnel are required to pass a federal and state background check.

## 6.1.9	Training Requirements

To protect the research mission of the Center, a security training program shall be developed to include, but not be limited to, basic training on the protection of personnel and property; building entry and exit control procedures; fire prevention; safety indoctrination; first aid; patrol methods; fundamental rules and practices governing search and seizure; responding to the scene of an accident or disturbance; and telephone and radio communications.

## 6.1.10	Flag Duties

Government flags and pennants shall remain at full staff at all times since night time lighting is provided. If there is a malfunction with the evening lighting system the flags and pennants shall be lowered at dusk and raised at 7:00 am each day in accordance with the guidelines of USDA Departmental Regulation No. 5160-4 until the lighting system is placed back in service. Notification will be furnished by the North Atlantic Area Property Manager when flags are to be lowered to half staff position as well as length of time before flags are raised to the full staff position.

## 6.1.11	Vehicle Registration and Driver Licenses

Compile and maintain a listing of vehicle registration for all Contractor, ERRC, and NAA employees for notification of necessity to move the vehicle to another area for safety purposes, improper parking, etc. Compile and maintain a list of all drivers licenses for all Contractor, ERRC, and NAA employees for use of Government vehicles. Maintain a log to register Government subcontractor vehicles which is to include the following: employee name and employer, a drivers license number, vehicle registration number, and make, model, and year of vehicle.

## 6.1.12	Logs, Reports and Documentation

### 6.1.12.1	Daily logs. The Contractor shall maintain daily logs and records in a bound-book or binder at in the security office which shall include the following:

- Date

- Shift times

- Name of personnel on watch

- Building/Equipment conditions viewed on patrols

- Malfunctions and unusual events

- Data observed during rounds

- Signature of Supervisor

### 6.1.12.2	Incident reports. Reports of medical emergencies, hazardous conditions discovered, traffic accidents, security breaches, and any other unusual occurrences shall be made to the appropriate local authorities, Project Manager for action, and to the ACO for information within 24 hours of the occurrence.

### 6.1.12.3	Entry control report. Printout card access recorder shall be submitted to the ACO or his/her designee upon request.

## 6.1.13	Government-Furnished Property to be supplied for use in operation of these services:

- Space to serve as a security office/area, including office furniture

- Security system for exterior doors and windows

- Closed circuit television camera system

- Fire alarm system for the entire facilities

- Equipment such as base radio station, portable radio units, keys, flashlights, cellular telephone, etc.

- Guard Key station system

# 6.2	Asbestos Abatement

Asbestos containing material (ACM) or suspected ACM may be discovered during the course of routine maintenance or this service may be requested for the removal of such material from old equipment. This work shall be performed by an EPA certified contractor and the certification shall be numbered by EPA. Air sampling shall be performed by an independent 3rd party industrial hygienist. Material sampling will be performed by a National Institute of Standards and Technology Program certified lab using EPA testing methods. Work is to be scheduled during normal working hours unless otherwise directed by the ACO. If this work will have an impact on research or normal operations at the Center, sufficient advance notification to those affected is required. Government notification is required at the start of the abatement or testing work to allow for real time inspection and evaluation of work performance.

## 6.2.1	Asbestos Abatement Reports

Contractors must submit copies of insurance, workers and supervisors state certifications, removal and monitoring plans, re-occupancy air sampling results, and the waste manifests for shipping and final waste site for review and approval by the ACO with the request for additional funds. This information shall also be sent to the QAS and the ERRC Safety Officer. Final waste manifest will be sent to the ERRC’s Safety Officer so information is available to satisfy regulatory reporting requirements.

## 6.2.2 Training

The contractor shall provide training to all maintenance personnel to properly recognize potential ACM.

# 7.0	Modernization Support

With the Area Engineer, or his/her designated representative, the Contractor shall coordinate services required to support renovation activities performed throughout the Center. Modernization support activities that exceed an estimated cost of $2,500 will be separately priced.

## 7.1	Utility Outage Support. The Contractor shall coordinate and schedule outage support for utilities upon notification of the Area Engineer or his/her designated representative. Utility shutdowns include, but not limited to, water, gas, nitrogen, vacuum, chilled water, hot water, compressed air, steam, electricity, telephone and computer (local area network) as required. Outage support includes:

Advance notification shall be provided to all Center personnel as to what utilities will be disconnected and the duration of the shut down period.

Provide temporary services when disconnection of required service would disrupt research during the utility shutdown period.

Terminate utility services following logout/tagout procedures to assure safety. Restore utility services when construction work is completed.

## 7.2.	Relocation Support

The Contractor shall provide services required to relocate office and scientific equipment to swing space, designated place of storage and/or renovated spaces. Salvage equipment as noted by the resident scientists and general office equipment such as blinds, door hardware, fire extinguishers, cabinets and biological safety cabinetry.

## 7.3	Swing Space Renovations

The Contractor shall prepare space for interim use during modernization as directed by the Area Engineer. Preparations may include cleaning, painting and installation of required utilities for relocated scientific equipment, computers and telephones.