control joints in concrete floor slabs

ISSUE:

Improve the quality of floor slabs by properly specifying control joints.

background:

ProCATS (Proactive Claims Analysis and Tracking System) data indicates that extensive cracking may occur in a floor slab when control joints are not properly specified.

discussion:

Industry standards require control joints every 400 square feet. Control joints every 20 feet in both directions work well for large slabs. However, for narrow slabs, such as in corridors or lobbies, specifying control joints every 400 square feet would result in poor quality slabs. In a recent situation, the control joints were placed every 50 feet,  for an 8 feet wide corridor,  which met the industry standard and contract requirement, but resulted in numerous cracks.

recommendations:

1. Distance between control joints must not exceed the spacing between 	columns or 24 feet, whichever is smaller.

2. Provide diamond shaped isolation joints at columns.

3. Control joints should be carefully detailed at floor depressions.

for additional information:

Contact Krishna Banga at 202-565-9370 in the Standards Service (187C), or Dan Edwards, SRE, Marion, IN., at 317-677-3159.

12 JULY 1996
								         FM-187C-DA56