DEPARTMENT OF VETERANS AFFAIRS

DESIGN INSTRUCTIONS TO ARCHITECTS AND ENGINEERS

LOCATION	:

PROJECT TITLE	:

PROJECT NO.	:

[ ]	SCHEMATICS	[ ]	DESIGN	[ ]	CONSTRUCTION

DEVELOPMENT		DOCUMENTS

_____________________________________________________________________

AUTOMATIC TRANSPORT

TRANSPORT SYSTEMS DESIGN MANUAL FOR HOSPITAL PROJECTS

(February 2000)

[ ]	AMBULATORY CARE

[ ]	DOMICILIARY

[ ]	NURSING HOME

[ ]	SATELLITE OUTPATIENT CLINIC

[ ]	TUBERCULOSIS

[ ]	PATIENT ROOMS & RELATED AREAS

[ ]	VETERINARY MEDICAL UNIT

FROM:		DATE:

Package Preparer:

Telephone Number:

DEPARTMENT OF VETERANS AFFAIRS

TRANSPORT SYSTEMS DESIGN MANUAL

TABLE-OF-CONTENTS

1.	Criteria Unique to VA

2.	General

3.	Elevators

4.	Size and Number of Elevators

5.	Guidelines

6.	Power Door Operation

7.	Handicapped Provisions

8.	Elevator Hoistways

9.	Elevator Pits

10.	Elevator Machine Rooms

11.	Basic Electrical Notes

12.	Venting and Automatic Damper of Hoistway Venting

13.	Drawings

14.	Design Criteria

15.	Applicable Design and Construction Procedure

16.	Transport Systems Standard Details Index

17.	Applicable Transport Systems Master Specifications Index

TRANSPORT SYSTEMS DESIGN MANUAL

DEPARTMENT OF VETERANS AFFAIRS

February 2000

1.	CRITERIA UNIQUE TO VA:

1.1 	Curved Hoistway Door Jamb

1.2	Solid Grouting of Door Jambs

1.3	Intercom System (No Telephones) located in auxiliary car station, elevator machine room, and station designated 24 hour occupied area.

1.4	Hydraulic Elevator

A.	Automatic Shut-off Valve located in pit, in oil line, next to piston jackhead.

B.	Oil Line Gate Shut-off Valve located in pit.

C.	Oil Return Scavenger Pump located in pit.

1.5	Hoistway Lighting

1.6	Motorized Hoistway Louvered Venting Activated by Top of Hoistway Smoke Detector.

1.7	Provide smoke detectors at top of the hoistways.  The detectors shall operate hoistway venting and alarms as per Hoistway Venting System Design Criteria.

2.	GENERAL:

2.1	The transportation equipment in new facilities shall be included in the general contract with specification sections prepared for the transport systems as required.  These specification sections are included in the 01001 series through 14582 portions of the master specifications.

2.2	The requirements of the latest edition of the ASME A17.1 Safety Code for Elevators, and Escalators (herein referred to as the ASME A17.1 Code) must constitute the minimum requirements of all transportation systems, including methods of construction, manner of installation, design and tests.  All electrical work shall meet the latest requirements of the "National Electrical Code (NEC)", and all equipment will meet the requirements of the Uniform Federal Accessibility Standards (UFAS), American Disabilities Act, for architectural barrier free requirements.

3.	ELEVATORS:

3.1	Passenger type elevators are used to transport the public, hospital staff, and ambulatory patients (wheelchairs).

3.2	Hospital service type elevators are used to transport employees, patients, and equipment or carts.  Patients may be on foot, in wheelchairs, on gurneys or beds.

3.3	Combination passenger and service type elevators are installed where combined use is possible without interfering with normal activities, i.e., outpatient, domiciliary, and nursing home care facilities.

3.4	Elevators shall be provided in all facilities having two or more floors and shall be of a design to provide the functional link for the type of traffic anticipated.  Passenger and service elevators shall be of a size to accommodate handicapped persons.

3.5	Elevators for limited special use, such as those for private passengers, are economically undesirable.  They shall not be installed unless they can be fully justified.  The use of slow speed elevators shall be considered and separated from other traffic if required for mortuary use or the transport of animals.

3.6	When planning the location of elevators, the following principles shall be observed:

A.	Elevators shall be located so that the building entrances with the heaviest traffic will have adequate elevator service.  Elevators shall be as near to the center of the building area served as practicable, taking into consideration the distance from the elevator bank or banks to the most distant functional areas.

B.	Elevators shall be located so that they will serve all floors that require service.  This includes the basement, sub-basement, as well as all of the typical floors of the office building.  Avoid placing elevators or dumbwaiters over occupied spaces as this will require counterweight safeties and reinforced pits.

C.	Elevators shall be grouped in banks of adjacent cars or banks of adjacent cars or banks of cars facing each other.  It is desirable to have not over four service cars in a bank or three passenger cars in a bank, and not over six cars in a group of two facing banks.

D.	Consideration shall be given to the maximum walking distance from the vertical transportation service to the most distant function.  This factor shall be weighed along with the advantages of locating elevators near the center of the building and the advantage of elevator clustering.  In general, the maximum walking distance to elevators should not exceed 60 m (200 feet).  Any decentralized banks and/or clustering of elevators should be planned to include at least two cars to maintain an acceptable dispatch interval between cars and insure continuity of service.

E.	The lobby width between two banks of passenger elevators shall be not less than 3.6 m (12 feet).  Service elevators lobby shall be no less than 4.2 m (14 feet).

4.	SIZE AND NUMBER OF ELEVATORS:

4.1	Size and number of elevators required for a given building depends upon the size and function of the building, allocation of activities in it, density of population, the physical location and grouping of elevators, etc.  The elevator installation needed for a given facility shall be estimated on the basis of anticipated local condition, quality of service, and the overall annual cost of the installation.  The overall annual cost of the transport systems, including amortized costs of the original investment, cost of maintenance, material, and consumed power shall be considered.

4.2	The following primary functions shall be used for the purpose of estimating the elevator requirements:

A.	The anticipated population density figures shall be provided by the Department of Veterans Affairs to assist in the system design.  However, in all cases, the vertical transportation requirements shall be planned for the total population that the facility could reasonably house, rather than a forecast of initial occupancy.

B.	Maximum traffic peak.  This is the maximum percentage of the total population on the floors served by the elevators that must be handled during any 5 minute period.  This maximum traffic peak will vary with the type of functional areas and special conditions applicable to the facility. In general, the maximum traffic peak shall be considered as being up peak by the 24 hourly summaries, i.e., based on elevator loading at the lower main terminal, or terminals, local discharge of passengers on the up trip and express runback to the lowest main terminal.

C.	The computations for vertical transportation equipment shall be based on transporting 10 to 14 percent of those persons who move between floors during periods of maximum demand in five minutes.  The peak values, together with the population density factor should provide a reserve capacity adequate to maintain reasonable satisfactory service during periods when one elevator is shut down for repairs.

D.	The possibility of changes in the type of occupancy and reassignment of building areas that would result in a greater volume of traffic shall be investigated.  When such possibilities exist, the building framing shall be arranged to permit future installation of such additional elevator equipment as will be required to handle future possible increase in traffic volume.

E.	Special conditions which must receive consideration in estimating elevator requirements include cafeteria traffic, canteen store traffic, dietary distribution and retrieval, transient traffic, visitor traffic, outpatient traffic, pharmacy, building management, SPD, surgery warehousing, spinal cord injury, grouping of elevators, external transport facilities, building entrances at more than one level, basement facilities, unusual interfloor traffic requirements, and trash removal if chutes are not used.

F.	Where groups of elevators serving identical floors are required to be furnished in two or more locations for the purpose of providing reasonable convenience of use, the elevators shall provide a minimum carrying capacity of not less than 120 percent of the maximum traffic peak.  This factor provides the elimination of unequal distribution of traffic.

G.	Passenger and service elevators shall have the capability to handle their maximum peak loads while providing a satisfactory interval.  Consider the following:

1.	A capacity and speed shall be selected that will require the least number of elevators to handle the peak loads with an acceptable interval.  Where four or more passenger elevators are in a group, the interval shall be no greater that 45 seconds.  Service elevators in a group shall have an interval of 60 seconds maximum.  Where there are fewer than four elevators in a group, the interval shall be no greater than 45 seconds maximum.  For passenger elevators, except special outpatient elevators or other special purpose elevators, the most suitable car capacities are 1815 kg (4000 lbs).  When separate service elevators are provided, they shall be 2270 kg (5000 lb). capacity.

2.	Where one elevator would normally meet the requirements in the facility where patient elevator service is essential (such as facilities over 2 stories high), two elevators shall be installed to insure continuity of service.  If there are financial restrictions during construction, install one elevator now and provide a future elevator hoistway.

5.	GUIDELINES:

5.1	The equipment specified shall depend upon the service demand and the equipment commercially available to meet those demands.  Care shall be exercised to avoid specifying non-competitive methods in features of elevator.

A.	Geared hoisting machines shall be used for elevators in buildings of eight stories or less.  Gearless machines shall be used for elevators in all buildings nine floors or more.  The placing of hoisting machines in basement machine rooms, or in machine rooms adjacent to the hoistway, shall be limited to special cases where conditions do not permit the installation of overhead machines.

B.	Limited rise:  Oil hydraulic direct plunger elevator equipment shall be considered for limited rise (four stops, approximately 14.5 m (48 foot) rise) slow speed elevators.  The machine room and pump unit shall be located adjacent to the hoistway at the lowest landing.

C.	SCR control shall be used where elevators will be in relatively intense service.  Use of SCR control is appropriate for unlimited applications.

1.	Single wrap geared traction configuration shall be used for speeds up to 1.75 m/s (350 FPM).

2.	Double wrap gearless traction configuration shall be used with speeds of 2.5 m/s (500 FPM) and greater.  Roping shall be 2:1.  Secondary sheaves shall be used.

D.	Operations:  In general, the following systems of operation shall be provided for elevators:

1.	Single car selective collective operation.

2.	A two car bank of elevators shall have duplex selective collective automatic operation.

3.	A bank of three or more elevators shall have group automatic operation with automatic selection of method of dispatching.

(a)	For a group of three or more elevators include zone dispatching system.

(b)	Dispatching of systems shall be tailored to building configuration and general precepts of a fully zoned system.

E.	Special circuits, special control and emergency requirements should be anticipated.  Possible areas for such consideration are surgery, intensive care, cardiac emergency, emergency receiving and dietary usage.  Medical emergency service may be required.

F.	Elevator capacity and platform design:  Passenger elevators 1815 kg (4,000 lb.) capacity, 2400 mm (8'0") wide by 1850 mm (6'2") deep platform.  Service elevators up to 1815 kg (4,000 lb.) capacity, 1800 mm (6’0”) wide by 2600 mm (8'8") deep platform.  Service elevators up to 2270 kg (5,000 lbs.), 2000 mm (6'8") wide by 2600 mm (8'8") deep platform.

G.	Maximum size of vehicles or other loads, and maximum weight of portable medical or X-ray equipment should be determined before setting elevator size and capacities.  Maximum area allowed by the ASME A17.1 Code shall be used to develop inside dimensions of car enclosure.

H.	Elevator cars:  Car enclosures shall be of a single entrance or front and rear type and shall be of standard design unless modifications are dictated due to special project conditions.  Cab designs shall be detailed on the architectural drawings.  Materials for elevator cabs shall be selected so the car enclosure conforms to ASME A17.1 and the specifications.

I.	Entrances - Passenger and Service Hoistway and Elevator Entrances:

1.	Doors shall be single speed center opening or two speed side slide.  Do not use two speed center opening doors.

2.	Passenger elevator entrance width:  1200 mm (4'0") standard.

3.	Service elevators entrance width:  1200 mm (4'0") standard - 1500 mm (5'0") optional if required by facilities function.

4.	Door opening height:  2100 mm (7'0").

5.	Freight elevators:  Hoistway and car bi-parting doors shall be power operated.  Openings to be determined by facilities function.

6.	POWER DOOR OPERATION:  Power door operation shall be provided for all elevators and the following door opening speed is required:

6.1	Door operator shall be capable of opening doors at the rate of 0.6 m/s (two feet per second).  This is a capability speed, with actual speed being adjusted to meet requirements of the specific installation.

6.2	Closing speed shall be a maximum 0.3 m/s (one foot per second).  All power operated doors shall be equipped with an automatic reopen device, for passenger protection.

7.	HANDICAPPED PROVISIONS:  Provide as per the requirements of ASME A17.1 and The Americans With Disabilities Act of 1990 (ADA).

8.	ELEVATOR HOISTWAYS:

8.1	All hoistways shall comply with ASME A17.1.  Structural supports shall be provided at each floor and where conditions require it, between floors for securing guide rail brackets.  Provide either intermediate supports between floors or general brackets where the distance between floors or structural supports exceed 4.2 m (14 feet) or as needed by seismic requirements.  All additional supports for guide rails shall be shown on structural drawings and shall be included as part of the structural framing of the hospital.

8.2	The interior face of the hoistway walls shall have a smooth, flush, light colored surface.  Exposed spray-on fire proofing shall not be used in the elevator hoistway.

8.3	Hoistway sizes of elevators with their overhead and pit clearances are shown on VA's construction details sheets.  These clearances are based on probable car structures, heights and maximum heights of commercially obtainable equipment together with runby and clearance requirements of ASME A17.1.

9.  ELEVATOR PITS:

9.1	Pit depths shall meet the ASME A17.1 Code requirements.

9.2	Pits shall be provided with a fixed vertical steel access ladder for each elevator.  The ladder shall be located within reach of the elevator hoistway entrance at the bottom landing and clear all elevator equipment.

9.3	Pits 2400 mm (8 feet, 0 inches) deep and over should be provided with a permanent means of external access.  Where external access is impractical, a permanent ladder, accessible from the bottom hoistway entrance door, shall be provided in each pit.  The external access shall be carefully studied before it is declared impractical.

9.4	Door to pit space shall be of fire resistant construction and shall be provided with self closing, self locking hardware, and arranged so that a key is required for entry.  Indicate sign on door as per ASME A17.1.

9.5	Sump pits shall be avoided unless a water problem exists.  If sump pits are required provide a pit with a removable grate.  A portable sump pump shall be used to pump pits.  No sump pump shall be connected to a sewer.

10.	ELEVATOR MACHINE ROOMS:

10.1	Elevator machine rooms shall be large enough to install the elevator equipment, including space for controllers.  Clearances for control equipment shall be not less than that required by the National Electrical Code, and with enough working space between the various items of equipment for maintenance purposes.  It must be possible to remove major equipment components of each elevator for repair without dismantling components of an adjacent elevator. Minimum headroom shall be 2300 mm (7'6").

10.2	Elevator machine rooms shall be of fire resistant construction equivalent to hoistway construction and the machine room side of floors, ceilings, and walls shall have a smooth surface equivalent to a well pointed smooth face tile or brick or smooth concrete.  Exposed spray on fireproofing shall not be used in elevator machine room.  Walls, ceilings and floor should be painted a light color.  Floors shall be sealed to eliminate concrete dust.

10.3	All openings in the floor for passage of hoist ropes, etc. shall have a 50 mm (2 inch) high concrete curb or 50 mm (2 inch) high metal sleeves.

10.4	Elevator machine rooms access doors shall conform to ASME A17.1 Code.

10.5	Industrial stairs shall be provided for convenient access to machine room.  Access to machine room should preferably not require passage across a roof or similar exposed area.  Provide clear access to machine rooms and overhead sheave areas through interstitial space.

10.6	Geared machines shall be mounted on vibration and sound isolating devices.  These isolating devices, when required, shall be of design to conform with seismic design requirements.

10.7	Skylights shall not be installed in elevator machine rooms.

10.8	Provide adequate air conditioning, heating, and ventilation in machine rooms.

10.9	Adequate lighting shall be provided to insure proper illumination in the front and rear of all controllers, supervisory and selector panels and over each hoisting machine.  Convenience outlets shall be provided for each elevator area within the machine room.

11.	BASIC ELECTRICAL NOTES:

11.1	POWER:

A.	Main Power:

1.	Each elevator shall be provided with a separate three phase supply through a circuit breaker located in the respective machine room, adjacent to the entry and with clear access.  The supply should terminate at the respective elevator controller.  Indicate the design electrical loads, (horsepower, voltage, amperage etc.) switch sizes, breaker settings, wire sizes and conduit sizes.

2.	The elevator supply shall be dedicated main feeder utilizing the shortest practical run and continuous ground conductor.

B.	Auxiliary Power:

1.	The elevators shall be arranged to have auxiliary power available with the capacity to operate one elevator at a time.

2.	If emergency generator is not available, then hydraulic elevators shall be provided with energizing to the down valve to bring the elevator to the bottom floor and maintain an energized door open button.

C.	Receptacle Outlets:

1.	Each elevator machine room shall be provided with a minimum of one ground type duplex receptacle outlet per elevator, and one receptacle for the master intercom panel.

2.	Each elevator pit shall be provided with one ground type duplex receptacle outlet per elevator.

3.	Provide for hydraulic elevators, a ground type duplex receptacle in the pit, mounted on the starting channel of each elevator at a point near the buffer springs preferably 450 mm (18 inches) above the pit floor.

11.2	COMMUNICATION:

A.	Each elevator will have an intercom system in place of a telephone.

B.	Conduit must be provided from the elevator machine room to a 24 hour monitoring location.

11.3	DETECTORS:  Smoke detectors shall be installed in the elevator lobbies at all floors, front and rear openings if applicable.  These smoke detectors plus the detectors at the top of the hoistway and machine room will be connected in common zone terminating in the machine room.  The smoke detector at the main floor lobby will form a second zone and terminate in the machine room.

11.4	HEAT DETECTORS FOR SPRINKLER HEADS:  See Supplment.

11.5	MACHINE ROOM AND HOISTWAY LIGHTING AND APPLIANCE PANEL:

A.	Provide and indicate a circuit breaker panel capable of locking the disconnecting means in the off position in each machine room.  The panel shall contain:

1.	A separate circuit to supply 120 V to each elevator for fan, lights and alarm.

2.	A separate circuit for the machine room lights.

3.	A separate circuit for the machine room receptacles.

4.	A separate circuit for the hoistway lights.

5.	A separate circuit for hoistway receptacles.

6.	Each hydraulic elevator shall be provided with a separate circuit for the scavenger pump in the pit.

7.	Provide 1200 mm (four foot) length fluorescent lighting fixtures in the elevator hoistway.  The lights are to be stacked vertically in a back corner wall for a single elevator or on the back wall between the divider beams of a duplex or triplex installation.  The extreme top and bottom fluorescents are to be mounted horizontally to illuminate the pit area when the car is at the bottom landing and the car top when the car is at the top landing.  A three way light switch is to be provided at the top of the pit ladder and five foot above the top terminal landing at the inside front wall near the hall button box.

12.  HOISTWAY VENTING FOR ALL V.A. ELEVATORS

12.1	The VA and National Building Codes requires that all elevator hoistways be vented to prevent accumulation of hot gases and smoke inside the hoistway.  This requirement includes non-personnel elevators if equipped with the means for top of car operation by service personnel.

12.2	The required vent shall be controlled by a motorized louver that is powered closed.  This louver shall open upon loss of electrical power or by a signal from either a smoke detector or activation of the Fire Emergency Service in any other manner.  See Supplement, Article, 1.A.

13.  DRAWINGS:

13.1	Separate architectural drawings shall be prepared for the transport systems.  Elevator drawings shall show electrical services, materials, sizes, details, space conditions, etc., of hoistway enclosures, pits, cabs, entrances, machine rooms, and other features.  These elevator drawings shall be coordinated with the other architectural, structural, mechanical and electrical drawings to insure that proper space conditions and other requirements have been provided.

13.2	The automatic guided vehicle systems tracking layout, warning lights, control room electrical conduit runs, floor, and wall mounted control boxes or panels shall also be indicated on the architectural and electrical drawings.

13.3	The spaces shall be designed so that they will accommodate the largest elevator equipment.  The transport system drawings shall be prepared and designed so that no manufacturer is prevented from bidding on the work.

13.4	Architectural drawings shall show reactions at point of elevator machine beams, and car and counterweights buffer supports.  Indicate impact loads.

13.5	Architectural drawings shall show elevator rail bracket spacing and maximum horizontal and vertical forces on guide rails.

13.6	Dumbwaiter hoistway entrance details shall be shown complete with doors.  The top and bottom entrances of shaft equipment shall include access doors.  Provide permanent access to overhead machine spaces.  Provide an access door and industrial stair into machine space or room.

14.	DESIGN CRITERIA:

14.1	Overhead Traction Machines:  See Supplement, Article 1.B.1.

14.2	Motor Sizes for Geared Elevators:  See Supplement, Article 1.B.2.

14.3	Do's and Don'ts of Elevators:  See Supplement, Article 1.B.3.

14.4	Guide Rail Bracket Inserts:  See Supplement, Article 1.B.4.

14.5	Sprinklers in Machine Rooms and Hoistways:  See Supplement, Article 1.B.5.

15.	APPLICABLE DESIGN AND CONSTRUCTION PROCEDURE:  Drawings

16.	TRANSPORT SYSTEMS STANDARD DETAILS INDEX:  Details not provided as a hard copy with this A/E Package, or of a later edition, may be obtained at the first review.  Details are provided in VA Program Guide PG-08-4, Volume I, ARCHITECTURAL STANDARD DETAILS.

DETAIL	DATE	TITLE

29	1969	Elevator, Passenger Two Speed Sliding Doors

29A	1992	Elevator, Passenger - Entrance Details Two Speed Sliding Doors

29B	1992	Elevator, Service Horizontal Sliding Center Opening Doors

29C	1992	Elevator, Service and Passenger Entrance Detail (Horizontal Sliding Center Opening Doors)

29D	1992	Vertical Sliding Bi-parting Type Freight Elevator Doors

29E	1992	Elevator, Hydraulic Plan and Section

29F	1976	Elevator Hoistways (Passenger) Vertical Dimensions

29G	1992	Elevator Hoistway (Service) Vertical Dimensions

29H	1992	Elevator, Passenger, Horizontal Sliding Center Opening Doors

29J	1992	Elevator, Service and Passenger Entrance Details

33	1992	Elevator Pit Ladder

17.	APPLICABLE TRANSPORT SYSTEMS MASTER SPECIFICATIONS INDEX: Use latest edition.

SECTION		TITLE	COMMENTS

11161		Dock Levelers

11162		Dock Lifts

14120		Dumbwaiters - Drum Type

14121		Dumbwaiters - Geared Traction

14125		ATS Cart Elevator

14210		Traction Elevators

14225		Elevator Modernization

14240		Hydraulic Elevators

14310		Escalators

14420		Wheel Chair Lift

14510		Tote Box Conveyer Electric Track

14511		Automatic Transport Guided Vehicle System (Basic Requirements)

14560		Gravity Trash Chute

14561		Gravity Linen Chute

14580		Pneumatic Tube System

14581		Pneumatic Trash System

14582		Pneumatic Soiled Linen System

14450		Motor Vehicle Lifts

--End--

DO

DO

DO NOT

DO NOT

DO NOT

DO NOT

MOTOR SIZES FOR GEARED ELEVATORS

Values given in table are maximum rated loads of elevators and are based on the assumption that counterbalance will be provided to equal the cage plus 40% of rated load.  In other words, net loads will be 60% of elevator ratings.

|  |  | ELEVATOR CAR SPEED IN FEET PER MINUTE |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Elevator | M-G | 25 | 50 | 75 | 100 | 125 | 150 | 200 | 250 | 300 | 350 | 400 |
| Hoisting | Set | ASSUMED OVERALL MECHANICAL EFFICIENCY - GEARLESS EFFICIENCY - 90% |  |  |  |  |  |  |  |  |  |  |
| Motor | If V. V. | 40 | 46 | 48 | 51 | 53 | 53 | 55 | 58 | 59 | 60 | 61 |
| HP | KW | MAXIMUM ELEVATOR CAPACITY - LB. |  |  |  |  |  |  |  |  |  |  |
| 3 5 7.5 10 12.5 | - - 5 7.5 7.5 | 2640 4400 6600 8800 11000 | 1500 2500 3800 5000 6300 | 1050 1750 2650 3500 4400 | 840 1400 2100 2800 3500 | 700 1150 1750 2300 2900 | 580 970 1450 1950 2400 | 450 760 1150 1500 1900 | - 630 950 1250 1600 | - 540 810 1080 1350 | - 470 700 940 1175 | - - 625 840 1050 |
| 15 20 25 30 40 | 10 15 15 20 25 | 13200 17600 22000 26400 35200 | 7600 10100 12600 15200 20200 | 5300 7000 8800 10500 14000 | 4200 5600 7000 8400 11200 | 3500 4650 5800 7000 9300 | 2900 3850 4850 5800 7750 | 2250 3050 3800 4550 6100 | 1900 2550 3200 3800 5100 | 1600 2150 2700 3250 4300 | 1400 1850 2350 2800 3750 | 1250 1675 2100 2500 3350 |
| 50 60 75 100 125 150 | 30 40 50 60 75 100 | 44000 53000 66000 88000 110000 132000 | 25300 30300 38000 50600 63200 75900 | 17600 21100 26400 35200 44000 52800 | 14000 16800 21000 28000 35000 42000 | 11600 14000 17500 23300 29100 35000 | 9700 11600 14500 19400 24300 29000 | 7600 9150 10600 15200 19000 22800 | 6350 7650 8900 12750 16000 19000 | 5400 6500 8100 10800 13500 16000 | 4700 5650 7050 9400 11800 14150 | 4200 5000 6300 8400 10500 12600 |

The efficiencies listed may be considered as normal for first class overhead installations; if they are not correct for the equipment to be used, corrections to correspond to actual available efficiencies must be made in figures tabulated above.

This page does not apply to basement type installations because of poorer mechanical efficiency.

KW ratings of M-G sets are given to be used for variable voltage, geared equipment, but sizes of motors listed may, of course, be used for speeds and load ratings shown for other types of elevator equipment.

For sizes of motors to apply on elevators where ratings are not in the above table, use the following formula:

HP = Elev. Capac. (lb.) x F.P.M.

550 x % Eff.

KW Factor for Gearless:	KW = K x T x H

T = Rated Cap. in Thousand

H = FPM in Hundred

K = 	1.5 above 3700 Cap.

=	1.77 - 2500 - 3700

=	1.90 - 2000 - 2400

Running Time

Gearless	Geared

Start - Stop 	3.6 sec.	4.4 sec.

Run:	FL x 60 sec.   =   Total R.T. in sec.

FPM

Example:	12.5 x 60 sec.   =   1.5 sec.	12.5 x 60 sec.   =   2.4 sec

500	      350

S - S	3.6 sec.	S - S 	4.4 sec.

Total R.T.	5.1 sec.	Total R. T.	6.8 sec.