## Table4_7A_AO_Causes_Cnt
Electric Power Annual 2010
Released: March 2012
Next Update: November 2012
Table 4.7.A. U.S. Transmission Circuit Automatic Outage Counts by Cause Code and by NERC Region, 2010
| FRCC | MRO | NPCC | RFC | SERC | SPP | TRE | WECC | Contigious U.S. | FRCC | MRO | NPCC | RFC | SERC | SPP | TRE | WECC | Contigious U.S.
| AC & DC Circuit Outage Counts | [8 empty] | Percent
Momentary Outage Causes
Weather, excluding lightning | 0 | 55 | 0 | 32 | 22 | 27 | 1 | 47 | 184 | 0 | 39.5683 | 0 | 13.8528 | 7.8292 | 23.4783 | 0.82645 | 10.2397 | 12.4577
Lightning | 14 | 32 | 4 | 85 | 99 | 42 | 22 | 81 | 379 | 14.5833 | 23.0216 | 11.4286 | 36.7965 | 35.2313 | 36.5217 | 18.1818 | 17.6471 | 25.6601
Environmental | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Contamination | 5 | 0 | 1 | 4 | 24 | 1 | 36 | 11 | 82 | 5.2083 | 0 | 2.8571 | 1.7316 | 8.5409 | 0.86957 | 29.7521 | 2.3965 | 5.5518
Foreign Interference | 21 | 1 | 0 | 4 | 18 | 1 | 25 | 22 | 92 | 21.875 | 0.71942 | 0 | 1.7316 | 6.4057 | 0.86957 | 20.6612 | 4.793 | 6.2288
Fire | 0 | 0 | 1 | 1 | 1 | 0 | 1 | 1 | 5 | 0 | 0 | 2.8571 | 0.4329 | 0.35587 | 0 | 0.82645 | 0.21786 | 0.33852
Vandalism, Terrorism, or Malicious Acts | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2 | 0 | 0 | 0 | 0.4329 | 0 | 0 | 0 | 0.21786 | 0.13541
Failed AC Substation Equipment | 2 | 1 | 2 | 8 | 11 | 3 | 4 | 25 | 56 | 2.0833 | 0.71942 | 5.7143 | 3.4632 | 3.9146 | 2.6087 | 3.3058 | 5.4466 | 3.7915
Failed AC/DC Terminal Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Failed Protection System Equipment | 5 | 7 | 7 | 32 | 26 | 2 | 2 | 1 | 82 | 5.2083 | 5.036 | 20 | 13.8528 | 9.2527 | 1.7391 | 1.6529 | 0.21786 | 5.5518
Failed AC Circuit Equipment | 7 | 1 | 4 | 18 | 7 | 4 | 2 | 10 | 53 | 7.2917 | 0.71942 | 11.4286 | 7.7922 | 2.4911 | 3.4783 | 1.6529 | 2.1786 | 3.5884
Failed DC Circuit Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.21786 | 0.067705
Vegetation | 0 | 0 | 1 | 0 | 2 | 0 | 0 | 0 | 3 | 0 | 0 | 2.8571 | 0 | 0.71174 | 0 | 0 | 0 | 0.20311
Power System Condition | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 3 | 5 | 0 | 0 | 0 | 0.8658 | 0 | 0 | 0 | 0.65359 | 0.33852
Human Error | 3 | 2 | 3 | 16 | 22 | 2 | 0 | 8 | 56 | 3.125 | 1.4388 | 8.5714 | 6.9264 | 7.8292 | 1.7391 | 0 | 1.7429 | 3.7915
Unknown | 38 | 38 | 12 | 28 | 48 | 31 | 28 | 239 | 462 | 39.5833 | 27.3381 | 34.2857 | 12.1212 | 17.0819 | 26.9565 | 23.1405 | 52.0697 | 31.2796
Other | 1 | 2 | 0 | 0 | 1 | 2 | 0 | 9 | 15 | 1.0417 | 1.4388 | 0 | 0 | 0.35587 | 1.7391 | 0 | 1.9608 | 1.0156
TOTAL | 96 | 139 | 35 | 231 | 281 | 115 | 121 | 459 | 1477 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
Sustained Outage Causes
Weather, excluding lightning | 0 | 83 | 2 | 23 | 18 | 40 | 4 | 142 | 312 | 0 | 34.5833 | 2.7778 | 8.3636 | 5.625 | 31.25 | 5.6338 | 16.4542 | 14.8219
Lightning | 8 | 24 | 1 | 10 | 65 | 18 | 14 | 94 | 234 | 5.8824 | 10 | 1.3889 | 3.6364 | 20.3125 | 14.0625 | 19.7183 | 10.8922 | 11.1164
Environmental | 0 | 1 | 0 | 2 | 1 | 0 | 0 | 4 | 8 | 0 | 0.41667 | 0 | 0.72727 | 0.3125 | 0 | 0 | 0.4635 | 0.38005
Contamination | 3 | 5 | 1 | 0 | 30 | 7 | 2 | 20 | 68 | 2.2059 | 2.0833 | 1.3889 | 0 | 9.375 | 5.4688 | 2.8169 | 2.3175 | 3.2304
Foreign Interference | 27 | 1 | 2 | 9 | 20 | 0 | 6 | 15 | 80 | 19.8529 | 0.41667 | 2.7778 | 3.2727 | 6.25 | 0 | 8.4507 | 1.7381 | 3.8005
Fire | 2 | 0 | 4 | 1 | 4 | 2 | 1 | 55 | 69 | 1.4706 | 0 | 5.5556 | 0.36364 | 1.25 | 1.5625 | 1.4085 | 6.3731 | 3.2779
Vandalism, Terrorism, or Malicious Acts | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.34762 | 0.14252
Failed AC Substation Equipment | 17 | 15 | 20 | 71 | 18 | 9 | 19 | 54 | 223 | 12.5 | 6.25 | 27.7778 | 25.8182 | 5.625 | 7.0312 | 26.7606 | 6.2572 | 10.5938
Failed AC/DC Terminal Equipment | 0 | 4 | 0 | 11 | 0 | 0 | 0 | 3 | 18 | 0 | 1.6667 | 0 | 4 | 0 | 0 | 0 | 0.34762 | 0.85511
Failed Protection System Equipment | 8 | 13 | 9 | 28 | 33 | 6 | 10 | 40 | 147 | 5.8824 | 5.4167 | 12.5 | 10.1818 | 10.3125 | 4.6875 | 14.0845 | 4.635 | 6.9834
Failed AC Circuit Equipment | 32 | 22 | 4 | 31 | 43 | 12 | 6 | 57 | 207 | 23.5294 | 9.1667 | 5.5556 | 11.2727 | 13.4375 | 9.375 | 8.4507 | 6.6049 | 9.8337
Failed DC Circuit Equipment | 0 | 2 | 1 | 0 | 0 | 0 | 0 | 3 | 6 | 0 | 0.83333 | 1.3889 | 0 | 0 | 0 | 0 | 0.34762 | 0.28504
Vegetation | 0 | 0 | 2 | 1 | 9 | 1 | 0 | 8 | 21 | 0 | 0 | 2.7778 | 0.36364 | 2.8125 | 0.78125 | 0 | 0.927 | 0.99762
Power System Condition | 2 | 7 | 3 | 11 | 0 | 0 | 0 | 29 | 52 | 1.4706 | 2.9167 | 4.1667 | 4 | 0 | 0 | 0 | 3.3604 | 2.4703
Human Error | 9 | 35 | 17 | 35 | 37 | 4 | 4 | 103 | 244 | 6.6176 | 14.5833 | 23.6111 | 12.7273 | 11.5625 | 3.125 | 5.6338 | 11.9351 | 11.5914
Unknown | 24 | 23 | 1 | 28 | 32 | 24 | 4 | 197 | 333 | 17.6471 | 9.5833 | 1.3889 | 10.1818 | 10 | 18.75 | 5.6338 | 22.8273 | 15.8195
Other | 4 | 5 | 5 | 14 | 10 | 5 | 1 | 36 | 80 | 2.9412 | 2.0833 | 6.9444 | 5.0909 | 3.125 | 3.9062 | 1.4085 | 4.1715 | 3.8005
TOTAL | 136 | 240 | 72 | 275 | 320 | 128 | 71 | 863 | 2105 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
Notes:
• Detailed information on the Transmission Availability Data System outage causes is available at:
http://www.nerc.com/docs/pc/tadswg/Appendix%207%2020101202a%20clean.pdf
Source: U.S. Energy Information Administration, Form EIA-411, "Coordinated Bulk Power Supply Program Report."