$$721.00A

**Section 721.—ELECTRICAL AND ILLUMINATION MATERIAL**

Revised 10 July 2014

*INCLUDE THE FOLLOWING FOR LIGHTING*

$$721.01A

721.01(c). Add the following:

Furnish either ozone resistant cross-linked polyethylene (XLP) or polyvinyl chloride (PVC) insulated cable, with or without a nylon jacket, as applicable, conforming to the following:

**(8) XLP.** IPCEA S-66-524 and NEMA WC-7 (code type XHHW);

**(9) PVC.** UL 83, ANSI C33.80-1971, and Federal Specification J-C-304 (code types THWN or THW).

*INCLUDE THE FOLLOWING FOR ELECTRICAL WORK*

$$721.01B

721.01(c). Add the following:

Furnish soft drawn or annealed copper conductors conforming to ASTM B3, and stranding conforming to ASTM B8. Furnish 7 strand for #10 AWG through #2 AWG, and 17 strand for #1 AWG through #4/0 AWG. Furnish #6 AWG minimum solid copper ground wires.